## README
OSTRAM — OSeMOSYS for Transmission
South Asia Power System Connectivity Model
Version: | 1.1
Last Updated: | 2026-04-16
Prepared for: | UN ESCAP
═══ WHAT IS THIS TEMPLATE ══════════════════════════════════════════════
This workbook collects the South Asia power-system data needed to run OSTRAM,
an OSeMOSYS-based connectivity model covering BD, BT, IN (×5), NP, LK, MV over 2023–2050.
The study is centred on cross-border interconnection — the orange tabs carry that focus;
the blue, red, and green tabs supply the surrounding system context the interconnector
question has to be answered within.
═══ HOW THE COLOURS WORK ══════════════════════════════════════════════
Each tab is colour-coded by its role in the pipeline:
BLUE — Model inputs. The A3 step reads these directly to populate OSeMOSYS.
7 sheets covering fixed parameters, per-tech trajectories, demand,
transmission, variable cost, and emissions.
RED — Timeslice-dependent sheets. The OSTRAM timeslice Python will rewrite
these whenever the temporal resolution changes (4 seasons × 3 bands today,
but not a hard assumption). Everything indexed by S_D_ lives here.
ORANGE — Interconnectors. The study focus: project inventory and the corresponding
TRNCBD_* tech parameters that encode cross-border corridors in OSeMOSYS.
GREEN — Provenance / nice-to-have. Country-lead inventories and cost-source tables
that explain (or will explain) where the numbers in the blue sheets come from.
Not read by A3 — these are the audit trail.
═══ SHEET INDEX ═══════════════════════════════════════════════════════
Sheet | Colour | What it contains
README | Gray | This sheet.
Fixed_Horizon_Parameters | Blue | Time-invariant per-tech parameters: CapacityToActivityUnit, OperationalLife, Input/OutputActivityRatio. Long-form: one row per (Tech × Parameter).
Primary_Techs | Blue | Fuel-supply / mining techs (MIN*). CapitalCost, FixedCost, ResidualCapacity, TotalAnnualMaxCapacity by year 2023–2050 in wide format.
Secondary_Techs | Blue | Power generation techs (PWR*). Same parameter set as Primary_Techs plus additional fields; the heart of the technology database.
Capacities_CF | Red | CapacityFactor (fraction) per (Timeslice × Tech) by year. 12 timeslices × all generation techs.
VariableCost | Blue | VariableCost (USD/GJ) by Mode.Operation × Tech × year. Primary-tech fuels only.
Demand_Projection | Blue | Annual electricity demand per node-ELC fuel (PJ/yr), 2023–2050. One row per node.
Demand_Profiles | Red | Demand fractions per (Timeslice × node-ELC) by year. Must sum to 1.0 across the 12 timeslices for each node-year.
Demand_Techs | Blue | Transmission tech parameters (PWRTRN, RNWTRN, TRNNLI, TRNRPO) — internal transmission layer, not cross-border.
Emissions | Blue | EmissionActivityRatio (tCO2/PJ) for emitting PWR techs by year. Currently IPCC 2006 defaults; to be replaced with country-specific NC values.
Yearsplit_Template | Red | YearSplit fractions per timeslice (must sum to 1.0 per year). Template form — timeslice Python regenerates this when resolution changes.
DaySplit | Red | DaySplit fractions per daily time bracket. Same rewrite rule as Yearsplit.
Interconnectors | Orange | Project inventory of cross-border corridors: 51 rows with from/to node, circuits, COD year, affiliated power, MW capacity, voltage, AC/DC, status. Pre-populated from Zixuan v3.
Interconnector_Params | Orange | OSeMOSYS parameters for TRNCBD_* techs (cross-border interconnectors). CapitalCost, FixedCost, ResidualCapacity, TotalAnnualMaxCapacity by year — the blue-equivalent of the inventory sheet.
Existing_Generation | Green | Plant-level inventory: ~2,112 plants with capacity MW, commissioning year, expected retirement, annual CF, status, source. Provenance for ResidualCapacity in Secondary_Techs.
Planned_Generation | Green | Project pipeline: ~541 committed/announced projects with expected COD, developer, source. Provenance for TotalAnnualMinCapacity / MaxCapacity in Secondary_Techs.
Technology_Costs | Green | Tech-level CAPEX / Fixed O&M / Variable O&M / Heat Rate trajectories 2023→2050, with source. Provenance for CapitalCost, FixedCost in Secondary_Techs.
RE_Targets_Policies | Green | National RE targets and NDC commitments per country-node: target type (Capacity_GW or RE_share), target year, mandate vs aspirational, source.
═══ HOW TO FILL IT IN ═════════════════════════════════════════════════
Step 1 — Send the green sheets to each country lead
They populate: existing plants, planned projects, cost assumptions, RE targets.
Pre-filled headers and dropdowns; only the empty yellow cells need values.
Step 2 — Transfer green-sheet data into the blue sheets
Existing plants → ResidualCapacity in Secondary_Techs
Planned projects → TotalAnnualMinCapacity (committed) and TotalAnnualMaxCapacity
Cost data → CapitalCost and FixedCost in Secondary_Techs and Primary_Techs
Hourly load data → Demand_Projection (annual) and Demand_Profiles (shapes)
Renewable resource data → Capacities_CF
Step 3 — Update the orange sheets if interconnector plans change
Corridor inventory changes in Interconnectors must be mirrored in Interconnector_Params.
Step 4 — Check before running
Every yellow cell with blue text is a flagged gap — it still needs a value.
Demand profile fractions must sum to 1.0 across the 12 timeslices per node-year.
YearSplit fractions must also sum to 1.0.
ResidualCapacity should decline over time as plants retire.
Step 5 — Run the pipeline
A3 reads the blue + orange sheets. The timeslice Python handles the red sheets.
The otoole-based pipeline produces the OSeMOSYS .txt data file.
═══ RULES — DO NOT BREAK THESE ═══════════════════════════════════════
1. Do not rename or reorder columns in the blue sheets. The pipeline reads exact column names.
2. Do not merge cells. The Python reader cannot handle them.
3. Do not delete rows. If a technology is not available at a node, set TotalAnnualMaxCapacity = 0.
4. Projection.Mode = "User defined" and Projection.Parameter = 0 means year-column values are used as-is.
5. CapacityToActivityUnit = 31.536 converts GW → PJ/yr. Do not change this.
6. All costs in USD 2023. Capacity in GW. Energy in PJ. Fractions as decimals (0.0–1.0).
7. Every VRE technology needs capacity factor values for all 12 timeslices.
8. Backstop (PWRBCK) is a safety valve at every node. Give it a very high cost (~99999 USD/kW).
═══ NAMING CONVENTIONS ════════════════════════════════════════════════
Technologies:
PWR + tech code + node code + XX + 01
PWRSPVBDXX01 = Solar PV, Bangladesh
PWRHDRBTXX01 = Hydro Reservoir, Bhutan
PWRCOASCPCIN_NXX01 = Coal Supercritical, India North
Demand fuels:
ELC + node code + XX02
ELCBDXX02 = Electricity demand, Bangladesh
Cross-border interconnectors:
TRNCBD_ + from_node + _ + to_node
TRNCBD_BD_IN_E = Bangladesh ↔ India East
═══ NODE CODES ════════════════════════════════════════════════════════
BD | Bangladesh
BT | Bhutan
IN_N | India – North
IN_S | India – South
IN_E | India – East
IN_W | India – West
IN_NE | India – Northeast
NP | Nepal
LK | Sri Lanka
MV | Maldives
═══ TIMESLICES ════════════════════════════════════════════════════════
Code | Season | Daily Band
S1D1 | Summer (Apr–May) | Night/Off-peak (22:00–06:00)
S1D2 | Summer (Apr–May) | Day/Shoulder (06:00–17:00)
S1D3 | Summer (Apr–May) | Evening/Peak (17:00–22:00)
S2D1 | Monsoon (Jun–Sep) | Night/Off-peak (22:00–06:00)
S2D2 | Monsoon (Jun–Sep) | Day/Shoulder (06:00–17:00)
S2D3 | Monsoon (Jun–Sep) | Evening/Peak (17:00–22:00)
S3D1 | Post-Monsoon (Oct–Nov) | Night/Off-peak (22:00–06:00)
S3D2 | Post-Monsoon (Oct–Nov) | Day/Shoulder (06:00–17:00)
S3D3 | Post-Monsoon (Oct–Nov) | Evening/Peak (17:00–22:00)
S4D1 | Winter (Dec–Mar) | Night/Off-peak (22:00–06:00)
S4D2 | Winter (Dec–Mar) | Day/Shoulder (06:00–17:00)
S4D3 | Winter (Dec–Mar) | Evening/Peak (17:00–22:00)
═══ UNITS ═════════════════════════════════════════════════════════════
Quantity | Unit
Capacity | GW
Energy | PJ
CAPEX | USD2023/kW
Fixed O&M | USD2023/kW/yr
Variable O&M / Fuel | USD/GJ
Demand | PJ/yr
CapacityToActivityUnit | 31.536 (GW → PJ/yr)
Emissions | tCO₂/PJ
Capacity factors | fraction (0.0–1.0)
Demand profiles | fraction (sum to 1.0 per node-year)
═══ TECHNOLOGY CODES ══════════════════════════════════════════════════
Code | Technology | Eligible Nodes
PWRSPV | Solar PV (utility-scale) | All nodes
PWRSPR | Solar PV (rooftop) | All nodes
PWRCSP | Concentrated Solar Power | IN_N/S/E/W/NE, LK
PWRWON | Onshore Wind | All nodes
PWRWOF | Offshore Wind | IN_S/W/E, BD, LK, MV
PWRHDR | Hydro – Reservoir | NP, BT, IN_N/NE/E, LK
PWRHRO | Hydro – Run-of-River | NP, BT, IN_N/NE
PWRHPS | Hydro – Pumped Storage | IN_S/W/N, NP, LK
PWRCOASCPC | Coal – Supercritical | BD, IN_N/S/E/W, LK
PWRCOAUSC | Coal – Ultra-supercritical | IN_N/S/E/W
PWRCCG | CCGT | BD, IN nodes, MV, LK
PWROCG | OCGT | BD, IN nodes, MV, LK
PWROIL | Oil/Diesel | MV, BD, LK
PWRBIO | Biomass/Bagasse | BD, IN nodes, NP, LK
PWRWTE | Waste-to-Energy | IN nodes, BD, LK
PWRURN | Nuclear | IN nodes, BD
PWRGEO | Geothermal | IN_N
PWRSDS | Short-duration storage (Li-ion 4h) | All nodes
PWRLDS | Long-duration storage (8h+) | All nodes
PWRFPV | Floating Solar PV | IN_S/E, BD, LK, MV
PWRH2G | Green Hydrogen Fuel Cell | IN nodes
PWRTDL | Tidal / Marine | IN_S, LK
PWRBCK | Backstop (penalty generator) | All nodes
MINCOA | Coal mining/import | All nodes
MINGAS | Natural Gas supply | All nodes
MINOIL | Oil supply | All nodes
MINURN | Uranium supply | All nodes
MINBIO | Biomass supply | All nodes
MINH2G | Green hydrogen production | All nodes
PWRTRN | Existing transmission (non-RE) | All nodes
RNWTRN | Existing transmission (RE) | All nodes
TRNNLI | New transmission line | All nodes
TRNRPO | Repower/upgrade transmission | All nodes
TRNCBD | Cross-border interconnector | Per corridor

## Fixed_Horizon_Parameters
Tech.Type | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Value
Secondary | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 33 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 33 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 33 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.25
Secondary | 33 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 34 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 34 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 34 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.25
Secondary | 34 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
Secondary | 36 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 36 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 36 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.4726
Secondary | 36 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 36 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 91300
Secondary | 37 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 37 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 37 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.4726
Secondary | 37 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 37 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 91300
Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.4726
Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 91300
Secondary | 39 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 39 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 39 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.4726
Secondary | 39 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 39 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 91300
Secondary | 40 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 40 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 40 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
Secondary | 40 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 40 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 27.5
Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 42 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 42 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 2 | OperationalLife | years | 27.5
Secondary | 42 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
Secondary | 42 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 42 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 43 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 43 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 2 | OperationalLife | years | 27.5
Secondary | 43 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
Secondary | 43 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 43 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 2 | OperationalLife | years | 27.5
Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 45 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 45 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 2 | OperationalLife | years | 27.5
Secondary | 45 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
Secondary | 45 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 45 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 46 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 46 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 27.5
Secondary | 46 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
Secondary | 46 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 46 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 47 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 47 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 2 | OperationalLife | years | 27.5
Secondary | 47 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
Secondary | 47 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 47 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 48 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 48 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 27.5
Secondary | 48 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
Secondary | 48 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 48 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 49 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 49 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 49 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 49 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 49 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 73300
Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 73300
Secondary | 51 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 51 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 51 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 51 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 51 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 73300
Secondary | 52 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 52 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 52 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 52 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 53 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 53 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 53 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 53 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 54 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 54 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 54 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 54 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 55 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 55 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 55 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 55 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 56 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 56 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 56 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 56 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 57 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 57 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 57 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 57 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 58 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 58 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 58 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 58 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 59 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 59 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 59 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 59 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 60 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 60 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 60 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 60 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 60 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 61 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 61 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 61 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 61 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 61 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 63 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 63 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 63 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 63 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 63 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 64 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 64 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 64 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 64 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 64 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 66 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 66 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 66 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 66 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 66 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 67 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 67 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 67 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 67 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 68 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 68 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 68 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 68 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 69 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 69 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 69 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 69 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 70 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 70 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 70 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 70 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 71 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 71 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 71 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 71 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 72 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 72 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 72 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 72 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 73 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 73 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 73 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 73 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 74 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 74 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 74 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 74 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 75 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 75 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 75 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 75 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 76 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 76 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 76 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 76 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 77 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 77 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 77 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 77 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 78 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 78 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 78 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 78 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 79 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 79 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 79 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 79 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 80 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 80 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 80 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 80 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 81 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 81 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 81 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 81 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 82 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 82 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 82 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 82 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 83 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 83 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 83 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 83 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 84 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 84 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 84 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 84 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 85 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 85 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 85 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 85 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 86 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 86 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 86 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 86 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 87 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 87 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 87 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 87 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 88 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 88 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 88 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 88 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 89 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 89 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 89 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 89 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 90 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 90 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 90 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 90 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 91 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 91 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 91 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 91 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 92 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 92 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 92 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 92 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 93 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 93 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 93 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 93 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 94 | MINCOABGD | Coal mining/import, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 94 | MINCOABGD | Coal mining/import, Bangladesh | 2 | OperationalLife | years | 99
Primary | 94 | MINCOABGD | Coal mining/import, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 94 | MINCOABGD | Coal mining/import, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 95 | MINCOABTN | Coal mining/import, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 95 | MINCOABTN | Coal mining/import, Bhutan | 2 | OperationalLife | years | 99
Primary | 95 | MINCOABTN | Coal mining/import, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 95 | MINCOABTN | Coal mining/import, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 96 | MINCOAIND | Coal mining/import, India | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 96 | MINCOAIND | Coal mining/import, India | 2 | OperationalLife | years | 99
Primary | 96 | MINCOAIND | Coal mining/import, India | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 96 | MINCOAIND | Coal mining/import, India | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 97 | MINCOANPL | Coal mining/import, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 97 | MINCOANPL | Coal mining/import, Nepal | 2 | OperationalLife | years | 99
Primary | 97 | MINCOANPL | Coal mining/import, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 97 | MINCOANPL | Coal mining/import, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 98 | MINCOALKA | Coal mining/import, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 98 | MINCOALKA | Coal mining/import, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 98 | MINCOALKA | Coal mining/import, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 98 | MINCOALKA | Coal mining/import, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 99 | MINCOAMDV | Coal mining/import, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 99 | MINCOAMDV | Coal mining/import, Maldives | 2 | OperationalLife | years | 99
Primary | 99 | MINCOAMDV | Coal mining/import, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 99 | MINCOAMDV | Coal mining/import, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 100 | MINGASBGD | Natural Gas supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 100 | MINGASBGD | Natural Gas supply, Bangladesh | 2 | OperationalLife | years | 99
Primary | 100 | MINGASBGD | Natural Gas supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 100 | MINGASBGD | Natural Gas supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 101 | MINGASBTN | Natural Gas supply, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 101 | MINGASBTN | Natural Gas supply, Bhutan | 2 | OperationalLife | years | 99
Primary | 101 | MINGASBTN | Natural Gas supply, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 101 | MINGASBTN | Natural Gas supply, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 102 | MINGASIND | Natural Gas supply, India | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 102 | MINGASIND | Natural Gas supply, India | 2 | OperationalLife | years | 99
Primary | 102 | MINGASIND | Natural Gas supply, India | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 102 | MINGASIND | Natural Gas supply, India | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 103 | MINGASNPL | Natural Gas supply, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 103 | MINGASNPL | Natural Gas supply, Nepal | 2 | OperationalLife | years | 99
Primary | 103 | MINGASNPL | Natural Gas supply, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 103 | MINGASNPL | Natural Gas supply, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 104 | MINGASLKA | Natural Gas supply, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 104 | MINGASLKA | Natural Gas supply, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 104 | MINGASLKA | Natural Gas supply, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 104 | MINGASLKA | Natural Gas supply, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 105 | MINGASMDV | Natural Gas supply, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 105 | MINGASMDV | Natural Gas supply, Maldives | 2 | OperationalLife | years | 99
Primary | 105 | MINGASMDV | Natural Gas supply, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 105 | MINGASMDV | Natural Gas supply, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 106 | MINOILBGD | Oil supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 106 | MINOILBGD | Oil supply, Bangladesh | 2 | OperationalLife | years | 99
Primary | 106 | MINOILBGD | Oil supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 106 | MINOILBGD | Oil supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 107 | MINOILBTN | Oil supply, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 107 | MINOILBTN | Oil supply, Bhutan | 2 | OperationalLife | years | 99
Primary | 107 | MINOILBTN | Oil supply, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 107 | MINOILBTN | Oil supply, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 108 | MINOILIND | Oil supply, India | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 108 | MINOILIND | Oil supply, India | 2 | OperationalLife | years | 99
Primary | 108 | MINOILIND | Oil supply, India | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 108 | MINOILIND | Oil supply, India | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 109 | MINOILNPL | Oil supply, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 109 | MINOILNPL | Oil supply, Nepal | 2 | OperationalLife | years | 99
Primary | 109 | MINOILNPL | Oil supply, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 109 | MINOILNPL | Oil supply, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 110 | MINOILLKA | Oil supply, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 110 | MINOILLKA | Oil supply, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 110 | MINOILLKA | Oil supply, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 110 | MINOILLKA | Oil supply, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 111 | MINOILMDV | Oil supply, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 111 | MINOILMDV | Oil supply, Maldives | 2 | OperationalLife | years | 99
Primary | 111 | MINOILMDV | Oil supply, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 111 | MINOILMDV | Oil supply, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 112 | MINURNBGD | Uranium supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 112 | MINURNBGD | Uranium supply, Bangladesh | 2 | OperationalLife | years | 99
Primary | 112 | MINURNBGD | Uranium supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 112 | MINURNBGD | Uranium supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 113 | MINURNBTN | Uranium supply, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 113 | MINURNBTN | Uranium supply, Bhutan | 2 | OperationalLife | years | 99
Primary | 113 | MINURNBTN | Uranium supply, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 113 | MINURNBTN | Uranium supply, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 114 | MINURNIND | Uranium supply, India | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 114 | MINURNIND | Uranium supply, India | 2 | OperationalLife | years | 99
Primary | 114 | MINURNIND | Uranium supply, India | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 114 | MINURNIND | Uranium supply, India | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 115 | MINURNNPL | Uranium supply, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 115 | MINURNNPL | Uranium supply, Nepal | 2 | OperationalLife | years | 99
Primary | 115 | MINURNNPL | Uranium supply, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 115 | MINURNNPL | Uranium supply, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 116 | MINURNLKA | Uranium supply, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 116 | MINURNLKA | Uranium supply, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 116 | MINURNLKA | Uranium supply, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 116 | MINURNLKA | Uranium supply, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 117 | MINURNMDV | Uranium supply, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 117 | MINURNMDV | Uranium supply, Maldives | 2 | OperationalLife | years | 99
Primary | 117 | MINURNMDV | Uranium supply, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 117 | MINURNMDV | Uranium supply, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 118 | RNWBIOBGDXX | Biomass supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 118 | RNWBIOBGDXX | Biomass supply, Bangladesh | 2 | OperationalLife | years | 99
Primary | 118 | RNWBIOBGDXX | Biomass supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 118 | RNWBIOBGDXX | Biomass supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 119 | RNWBIOBTNXX | Biomass supply, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 119 | RNWBIOBTNXX | Biomass supply, Bhutan | 2 | OperationalLife | years | 99
Primary | 119 | RNWBIOBTNXX | Biomass supply, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 119 | RNWBIOBTNXX | Biomass supply, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 120 | RNWBIOINDNO | Biomass supply, India – North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 120 | RNWBIOINDNO | Biomass supply, India – North | 2 | OperationalLife | years | 99
Primary | 120 | RNWBIOINDNO | Biomass supply, India – North | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 120 | RNWBIOINDNO | Biomass supply, India – North | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 121 | RNWBIOINDSO | Biomass supply, India – South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 121 | RNWBIOINDSO | Biomass supply, India – South | 2 | OperationalLife | years | 99
Primary | 121 | RNWBIOINDSO | Biomass supply, India – South | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 121 | RNWBIOINDSO | Biomass supply, India – South | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 122 | RNWBIOINDEA | Biomass supply, India – East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 122 | RNWBIOINDEA | Biomass supply, India – East | 2 | OperationalLife | years | 99
Primary | 122 | RNWBIOINDEA | Biomass supply, India – East | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 122 | RNWBIOINDEA | Biomass supply, India – East | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 123 | RNWBIOINDWE | Biomass supply, India – West | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 123 | RNWBIOINDWE | Biomass supply, India – West | 2 | OperationalLife | years | 99
Primary | 123 | RNWBIOINDWE | Biomass supply, India – West | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 123 | RNWBIOINDWE | Biomass supply, India – West | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 124 | RNWBIOINDNE | Biomass supply, India – Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 124 | RNWBIOINDNE | Biomass supply, India – Northeast | 2 | OperationalLife | years | 99
Primary | 124 | RNWBIOINDNE | Biomass supply, India – Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 124 | RNWBIOINDNE | Biomass supply, India – Northeast | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 125 | RNWBIONPLXX | Biomass supply, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 125 | RNWBIONPLXX | Biomass supply, Nepal | 2 | OperationalLife | years | 99
Primary | 125 | RNWBIONPLXX | Biomass supply, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 125 | RNWBIONPLXX | Biomass supply, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 126 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 126 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 126 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 126 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 127 | RNWBIOMDVXX | Biomass supply, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 127 | RNWBIOMDVXX | Biomass supply, Maldives | 2 | OperationalLife | years | 99
Primary | 127 | RNWBIOMDVXX | Biomass supply, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 127 | RNWBIOMDVXX | Biomass supply, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Demand | 128 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 128 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 2 | OperationalLife | years | 50
Demand | 128 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 128 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 129 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 129 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 2 | OperationalLife | years | 50
Demand | 129 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 129 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 130 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 130 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 2 | OperationalLife | years | 50
Demand | 130 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 130 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 131 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 131 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 2 | OperationalLife | years | 50
Demand | 131 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 131 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 132 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 132 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 2 | OperationalLife | years | 50
Demand | 132 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 132 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 133 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 133 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 2 | OperationalLife | years | 50
Demand | 133 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 133 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 134 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 134 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 2 | OperationalLife | years | 50
Demand | 134 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 134 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 135 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 135 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 2 | OperationalLife | years | 50
Demand | 135 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 135 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 136 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 136 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 2 | OperationalLife | years | 50
Demand | 136 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 136 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 137 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 137 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 2 | OperationalLife | years | 50
Demand | 137 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 137 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 138 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 138 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 2 | OperationalLife | years | 50
Demand | 138 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 138 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 139 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 139 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 2 | OperationalLife | years | 50
Demand | 139 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 139 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 140 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 140 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 2 | OperationalLife | years | 50
Demand | 140 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 140 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 141 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 141 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 2 | OperationalLife | years | 50
Demand | 141 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 141 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 142 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 142 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 2 | OperationalLife | years | 50
Demand | 142 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 142 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 143 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 143 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 2 | OperationalLife | years | 50
Demand | 143 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 143 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 144 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 144 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 2 | OperationalLife | years | 50
Demand | 144 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 144 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 145 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 145 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 2 | OperationalLife | years | 50
Demand | 145 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 145 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 146 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 146 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 2 | OperationalLife | years | 50
Demand | 146 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 146 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 147 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 147 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 2 | OperationalLife | years | 50
Demand | 147 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 147 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 148 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 148 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 2 | OperationalLife | years | 50
Demand | 148 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 148 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 149 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 149 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 2 | OperationalLife | years | 50
Demand | 149 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 149 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 150 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 150 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 2 | OperationalLife | years | 50
Demand | 150 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 150 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 151 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 151 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 2 | OperationalLife | years | 50
Demand | 151 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 151 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 152 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 152 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 2 | OperationalLife | years | 50
Demand | 152 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 152 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 153 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 153 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 2 | OperationalLife | years | 50
Demand | 153 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 153 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 154 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 154 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 2 | OperationalLife | years | 50
Demand | 154 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 154 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 155 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 155 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 2 | OperationalLife | years | 50
Demand | 155 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 155 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 156 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 156 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 2 | OperationalLife | years | 50
Demand | 156 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 156 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 157 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 157 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 2 | OperationalLife | years | 50
Demand | 157 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 157 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 158 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 158 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 2 | OperationalLife | years | 50
Demand | 158 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 158 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 159 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 159 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 2 | OperationalLife | years | 50
Demand | 159 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 159 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 160 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 160 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 2 | OperationalLife | years | 50
Demand | 160 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 160 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 161 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 161 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 2 | OperationalLife | years | 50
Demand | 161 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 161 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 162 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 162 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 2 | OperationalLife | years | 50
Demand | 162 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 162 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 163 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 163 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 2 | OperationalLife | years | 50
Demand | 163 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 163 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 164 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 164 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 2 | OperationalLife | years | 50
Demand | 164 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 164 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 165 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 165 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 2 | OperationalLife | years | 50
Demand | 165 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 165 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 166 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 166 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 2 | OperationalLife | years | 50
Demand | 166 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 166 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 167 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 167 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 2 | OperationalLife | years | 50
Demand | 167 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 167 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 168 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 168 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 2 | OperationalLife | years | 50
Demand | 168 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 168 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 169 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 169 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 2 | OperationalLife | years | 50
Demand | 169 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 169 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 170 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 170 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 2 | OperationalLife | years | 50
Demand | 170 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 170 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 171 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 171 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 2 | OperationalLife | years | 50
Demand | 171 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 171 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 172 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 172 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 2 | OperationalLife | years | 50
Demand | 172 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 172 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 173 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 173 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 2 | OperationalLife | years | 50
Demand | 173 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 173 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 174 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 174 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 2 | OperationalLife | years | 50
Demand | 174 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 174 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 175 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 175 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 2 | OperationalLife | years | 50
Demand | 175 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 175 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 176 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 176 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 2 | OperationalLife | years | 50
Demand | 176 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 176 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 177 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 177 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 2 | OperationalLife | years | 50
Demand | 177 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 177 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 178 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 178 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 2 | OperationalLife | years | 50
Demand | 178 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 178 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 179 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 179 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 2 | OperationalLife | years | 50
Demand | 179 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 179 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 180 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 180 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 2 | OperationalLife | years | 50
Demand | 180 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 180 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Secondary | 27 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 27 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 27 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 27 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 27 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 27 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 27 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 27 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 27 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 27 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 27 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1

## Primary_Techs
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | MINCOABGD | Coal mining/import, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
1 | MINCOABGD | Coal mining/import, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
1 | MINCOABGD | Coal mining/import, Bangladesh | 3 | ResidualCapacity | GW |  | 0
1 | MINCOABGD | Coal mining/import, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
1 | MINCOABGD | Coal mining/import, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
2 | MINCOABTN | Coal mining/import, Bhutan | 1 | CapitalCost | USD/kW |  | 0
2 | MINCOABTN | Coal mining/import, Bhutan | 2 | FixedCost | USD/kW/yr |  | 0
2 | MINCOABTN | Coal mining/import, Bhutan | 3 | ResidualCapacity | GW |  | 0
2 | MINCOABTN | Coal mining/import, Bhutan | 4 | TotalAnnualMaxCapacity | GW |  | 0
2 | MINCOABTN | Coal mining/import, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
3 | MINCOAIND | Coal mining/import, India | 1 | CapitalCost | USD/kW |  | 0
3 | MINCOAIND | Coal mining/import, India | 2 | FixedCost | USD/kW/yr |  | 0
3 | MINCOAIND | Coal mining/import, India | 3 | ResidualCapacity | GW |  | 0
3 | MINCOAIND | Coal mining/import, India | 4 | TotalAnnualMaxCapacity | GW |  | 0
3 | MINCOAIND | Coal mining/import, India | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
4 | MINCOANPL | Coal mining/import, Nepal | 1 | CapitalCost | USD/kW |  | 0
4 | MINCOANPL | Coal mining/import, Nepal | 2 | FixedCost | USD/kW/yr |  | 0
4 | MINCOANPL | Coal mining/import, Nepal | 3 | ResidualCapacity | GW |  | 0
4 | MINCOANPL | Coal mining/import, Nepal | 4 | TotalAnnualMaxCapacity | GW |  | 0
4 | MINCOANPL | Coal mining/import, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
5 | MINCOALKA | Coal mining/import, Sri Lanka | 1 | CapitalCost | USD/kW |  | 0
5 | MINCOALKA | Coal mining/import, Sri Lanka | 2 | FixedCost | USD/kW/yr |  | 0
5 | MINCOALKA | Coal mining/import, Sri Lanka | 3 | ResidualCapacity | GW |  | 0
5 | MINCOALKA | Coal mining/import, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW |  | 0
5 | MINCOALKA | Coal mining/import, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
6 | MINCOAMDV | Coal mining/import, Maldives | 1 | CapitalCost | USD/kW |  | 0
6 | MINCOAMDV | Coal mining/import, Maldives | 2 | FixedCost | USD/kW/yr |  | 0
6 | MINCOAMDV | Coal mining/import, Maldives | 3 | ResidualCapacity | GW |  | 0
6 | MINCOAMDV | Coal mining/import, Maldives | 4 | TotalAnnualMaxCapacity | GW |  | 0
6 | MINCOAMDV | Coal mining/import, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
7 | MINGASBGD | Natural Gas supply, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
7 | MINGASBGD | Natural Gas supply, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
7 | MINGASBGD | Natural Gas supply, Bangladesh | 3 | ResidualCapacity | GW |  | 0
7 | MINGASBGD | Natural Gas supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
7 | MINGASBGD | Natural Gas supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
8 | MINGASBTN | Natural Gas supply, Bhutan | 1 | CapitalCost | USD/kW |  | 0
8 | MINGASBTN | Natural Gas supply, Bhutan | 2 | FixedCost | USD/kW/yr |  | 0
8 | MINGASBTN | Natural Gas supply, Bhutan | 3 | ResidualCapacity | GW |  | 0
8 | MINGASBTN | Natural Gas supply, Bhutan | 4 | TotalAnnualMaxCapacity | GW |  | 0
8 | MINGASBTN | Natural Gas supply, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
9 | MINGASIND | Natural Gas supply, India | 1 | CapitalCost | USD/kW |  | 0
9 | MINGASIND | Natural Gas supply, India | 2 | FixedCost | USD/kW/yr |  | 0
9 | MINGASIND | Natural Gas supply, India | 3 | ResidualCapacity | GW |  | 0
9 | MINGASIND | Natural Gas supply, India | 4 | TotalAnnualMaxCapacity | GW |  | 0
9 | MINGASIND | Natural Gas supply, India | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
10 | MINGASNPL | Natural Gas supply, Nepal | 1 | CapitalCost | USD/kW |  | 0
10 | MINGASNPL | Natural Gas supply, Nepal | 2 | FixedCost | USD/kW/yr |  | 0
10 | MINGASNPL | Natural Gas supply, Nepal | 3 | ResidualCapacity | GW |  | 0
10 | MINGASNPL | Natural Gas supply, Nepal | 4 | TotalAnnualMaxCapacity | GW |  | 0
10 | MINGASNPL | Natural Gas supply, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
11 | MINGASLKA | Natural Gas supply, Sri Lanka | 1 | CapitalCost | USD/kW |  | 0
11 | MINGASLKA | Natural Gas supply, Sri Lanka | 2 | FixedCost | USD/kW/yr |  | 0
11 | MINGASLKA | Natural Gas supply, Sri Lanka | 3 | ResidualCapacity | GW |  | 0
11 | MINGASLKA | Natural Gas supply, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW |  | 0
11 | MINGASLKA | Natural Gas supply, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
12 | MINGASMDV | Natural Gas supply, Maldives | 1 | CapitalCost | USD/kW |  | 0
12 | MINGASMDV | Natural Gas supply, Maldives | 2 | FixedCost | USD/kW/yr |  | 0
12 | MINGASMDV | Natural Gas supply, Maldives | 3 | ResidualCapacity | GW |  | 0
12 | MINGASMDV | Natural Gas supply, Maldives | 4 | TotalAnnualMaxCapacity | GW |  | 0
12 | MINGASMDV | Natural Gas supply, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
13 | MINOILBGD | Oil supply, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
13 | MINOILBGD | Oil supply, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
13 | MINOILBGD | Oil supply, Bangladesh | 3 | ResidualCapacity | GW |  | 0
13 | MINOILBGD | Oil supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
13 | MINOILBGD | Oil supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
14 | MINOILBTN | Oil supply, Bhutan | 1 | CapitalCost | USD/kW |  | 0
14 | MINOILBTN | Oil supply, Bhutan | 2 | FixedCost | USD/kW/yr |  | 0
14 | MINOILBTN | Oil supply, Bhutan | 3 | ResidualCapacity | GW |  | 0
14 | MINOILBTN | Oil supply, Bhutan | 4 | TotalAnnualMaxCapacity | GW |  | 0
14 | MINOILBTN | Oil supply, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
15 | MINOILIND | Oil supply, India | 1 | CapitalCost | USD/kW |  | 0
15 | MINOILIND | Oil supply, India | 2 | FixedCost | USD/kW/yr |  | 0
15 | MINOILIND | Oil supply, India | 3 | ResidualCapacity | GW |  | 0
15 | MINOILIND | Oil supply, India | 4 | TotalAnnualMaxCapacity | GW |  | 0
15 | MINOILIND | Oil supply, India | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
16 | MINOILNPL | Oil supply, Nepal | 1 | CapitalCost | USD/kW |  | 0
16 | MINOILNPL | Oil supply, Nepal | 2 | FixedCost | USD/kW/yr |  | 0
16 | MINOILNPL | Oil supply, Nepal | 3 | ResidualCapacity | GW |  | 0
16 | MINOILNPL | Oil supply, Nepal | 4 | TotalAnnualMaxCapacity | GW |  | 0
16 | MINOILNPL | Oil supply, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
17 | MINOILLKA | Oil supply, Sri Lanka | 1 | CapitalCost | USD/kW |  | 0
17 | MINOILLKA | Oil supply, Sri Lanka | 2 | FixedCost | USD/kW/yr |  | 0
17 | MINOILLKA | Oil supply, Sri Lanka | 3 | ResidualCapacity | GW |  | 0
17 | MINOILLKA | Oil supply, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW |  | 0
17 | MINOILLKA | Oil supply, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
18 | MINOILMDV | Oil supply, Maldives | 1 | CapitalCost | USD/kW |  | 0
18 | MINOILMDV | Oil supply, Maldives | 2 | FixedCost | USD/kW/yr |  | 0
18 | MINOILMDV | Oil supply, Maldives | 3 | ResidualCapacity | GW |  | 0
18 | MINOILMDV | Oil supply, Maldives | 4 | TotalAnnualMaxCapacity | GW |  | 0
18 | MINOILMDV | Oil supply, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
19 | MINURNBGD | Uranium supply, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
19 | MINURNBGD | Uranium supply, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
19 | MINURNBGD | Uranium supply, Bangladesh | 3 | ResidualCapacity | GW |  | 0
19 | MINURNBGD | Uranium supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
19 | MINURNBGD | Uranium supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
20 | MINURNBTN | Uranium supply, Bhutan | 1 | CapitalCost | USD/kW |  | 0
20 | MINURNBTN | Uranium supply, Bhutan | 2 | FixedCost | USD/kW/yr |  | 0
20 | MINURNBTN | Uranium supply, Bhutan | 3 | ResidualCapacity | GW |  | 0
20 | MINURNBTN | Uranium supply, Bhutan | 4 | TotalAnnualMaxCapacity | GW |  | 0
20 | MINURNBTN | Uranium supply, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
21 | MINURNIND | Uranium supply, India | 1 | CapitalCost | USD/kW |  | 0
21 | MINURNIND | Uranium supply, India | 2 | FixedCost | USD/kW/yr |  | 0
21 | MINURNIND | Uranium supply, India | 3 | ResidualCapacity | GW |  | 0
21 | MINURNIND | Uranium supply, India | 4 | TotalAnnualMaxCapacity | GW |  | 0
21 | MINURNIND | Uranium supply, India | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
22 | MINURNNPL | Uranium supply, Nepal | 1 | CapitalCost | USD/kW |  | 0
22 | MINURNNPL | Uranium supply, Nepal | 2 | FixedCost | USD/kW/yr |  | 0
22 | MINURNNPL | Uranium supply, Nepal | 3 | ResidualCapacity | GW |  | 0
22 | MINURNNPL | Uranium supply, Nepal | 4 | TotalAnnualMaxCapacity | GW |  | 0
22 | MINURNNPL | Uranium supply, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
23 | MINURNLKA | Uranium supply, Sri Lanka | 1 | CapitalCost | USD/kW |  | 0
23 | MINURNLKA | Uranium supply, Sri Lanka | 2 | FixedCost | USD/kW/yr |  | 0
23 | MINURNLKA | Uranium supply, Sri Lanka | 3 | ResidualCapacity | GW |  | 0
23 | MINURNLKA | Uranium supply, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW |  | 0
23 | MINURNLKA | Uranium supply, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
24 | MINURNMDV | Uranium supply, Maldives | 1 | CapitalCost | USD/kW |  | 0
24 | MINURNMDV | Uranium supply, Maldives | 2 | FixedCost | USD/kW/yr |  | 0
24 | MINURNMDV | Uranium supply, Maldives | 3 | ResidualCapacity | GW |  | 0
24 | MINURNMDV | Uranium supply, Maldives | 4 | TotalAnnualMaxCapacity | GW |  | 0
24 | MINURNMDV | Uranium supply, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 3 | ResidualCapacity | GW |  | 0
25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
26 | RNWBIOBTNXX | Biomass supply, Bhutan | 1 | CapitalCost | USD/kW |  | 0
26 | RNWBIOBTNXX | Biomass supply, Bhutan | 2 | FixedCost | USD/kW/yr |  | 0
26 | RNWBIOBTNXX | Biomass supply, Bhutan | 3 | ResidualCapacity | GW |  | 0
26 | RNWBIOBTNXX | Biomass supply, Bhutan | 4 | TotalAnnualMaxCapacity | GW |  | 0
26 | RNWBIOBTNXX | Biomass supply, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
27 | RNWBIOINDNO | Biomass supply, India – North | 1 | CapitalCost | USD/kW |  | 0
27 | RNWBIOINDNO | Biomass supply, India – North | 2 | FixedCost | USD/kW/yr |  | 0
27 | RNWBIOINDNO | Biomass supply, India – North | 3 | ResidualCapacity | GW |  | 0
27 | RNWBIOINDNO | Biomass supply, India – North | 4 | TotalAnnualMaxCapacity | GW |  | 0
27 | RNWBIOINDNO | Biomass supply, India – North | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
28 | RNWBIOINDSO | Biomass supply, India – South | 1 | CapitalCost | USD/kW |  | 0
28 | RNWBIOINDSO | Biomass supply, India – South | 2 | FixedCost | USD/kW/yr |  | 0
28 | RNWBIOINDSO | Biomass supply, India – South | 3 | ResidualCapacity | GW |  | 0
28 | RNWBIOINDSO | Biomass supply, India – South | 4 | TotalAnnualMaxCapacity | GW |  | 0
28 | RNWBIOINDSO | Biomass supply, India – South | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
29 | RNWBIOINDEA | Biomass supply, India – East | 1 | CapitalCost | USD/kW |  | 0
29 | RNWBIOINDEA | Biomass supply, India – East | 2 | FixedCost | USD/kW/yr |  | 0
29 | RNWBIOINDEA | Biomass supply, India – East | 3 | ResidualCapacity | GW |  | 0
29 | RNWBIOINDEA | Biomass supply, India – East | 4 | TotalAnnualMaxCapacity | GW |  | 0
29 | RNWBIOINDEA | Biomass supply, India – East | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
30 | RNWBIOINDWE | Biomass supply, India – West | 1 | CapitalCost | USD/kW |  | 0
30 | RNWBIOINDWE | Biomass supply, India – West | 2 | FixedCost | USD/kW/yr |  | 0
30 | RNWBIOINDWE | Biomass supply, India – West | 3 | ResidualCapacity | GW |  | 0
30 | RNWBIOINDWE | Biomass supply, India – West | 4 | TotalAnnualMaxCapacity | GW |  | 0
30 | RNWBIOINDWE | Biomass supply, India – West | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
31 | RNWBIOINDNE | Biomass supply, India – Northeast | 1 | CapitalCost | USD/kW |  | 0
31 | RNWBIOINDNE | Biomass supply, India – Northeast | 2 | FixedCost | USD/kW/yr |  | 0
31 | RNWBIOINDNE | Biomass supply, India – Northeast | 3 | ResidualCapacity | GW |  | 0
31 | RNWBIOINDNE | Biomass supply, India – Northeast | 4 | TotalAnnualMaxCapacity | GW |  | 0
31 | RNWBIOINDNE | Biomass supply, India – Northeast | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
32 | RNWBIONPLXX | Biomass supply, Nepal | 1 | CapitalCost | USD/kW |  | 0
32 | RNWBIONPLXX | Biomass supply, Nepal | 2 | FixedCost | USD/kW/yr |  | 0
32 | RNWBIONPLXX | Biomass supply, Nepal | 3 | ResidualCapacity | GW |  | 0
32 | RNWBIONPLXX | Biomass supply, Nepal | 4 | TotalAnnualMaxCapacity | GW |  | 0
32 | RNWBIONPLXX | Biomass supply, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
33 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 1 | CapitalCost | USD/kW |  | 0
33 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 2 | FixedCost | USD/kW/yr |  | 0
33 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 3 | ResidualCapacity | GW |  | 0
33 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW |  | 0
33 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
34 | RNWBIOMDVXX | Biomass supply, Maldives | 1 | CapitalCost | USD/kW |  | 0
34 | RNWBIOMDVXX | Biomass supply, Maldives | 2 | FixedCost | USD/kW/yr |  | 0
34 | RNWBIOMDVXX | Biomass supply, Maldives | 3 | ResidualCapacity | GW |  | 0
34 | RNWBIOMDVXX | Biomass supply, Maldives | 4 | TotalAnnualMaxCapacity | GW |  | 0
34 | RNWBIOMDVXX | Biomass supply, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0

## Secondary_Techs
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 840 | 822 | 804 | 785.4 | 766.8 | 748.2 | 729.6 | 711 | 692.7 | 674.4 | 656.1 | 637.8 | 619.5 | 609.3 | 599.1 | 588.9 | 578.7 | 568.5 | 558.3 | 548.1 | 537.9 | 527.7 | 517.5 | 507.3 | 497.1 | 486.9 | 476.7 | 466.5
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 12 | 12 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 10.5 | 10.2 | 9.9 | 9.6 | 9.3 | 9 | 9 | 9 | 9 | 9 | 9 | 8.7 | 8.4 | 8.1 | 7.8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 3.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1008 | 986.4 | 964.8 | 942.48 | 920.16 | 897.84 | 875.52 | 853.2 | 831.24 | 809.28 | 787.32 | 765.36 | 743.4 | 731.16 | 718.92 | 706.68 | 694.44 | 682.2 | 669.96 | 657.72 | 645.48 | 633.24 | 621 | 608.76 | 596.52 | 584.28 | 572.04 | 559.8
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 14.4 | 14.4 | 14.4 | 14.04 | 13.68 | 13.32 | 12.96 | 12.6 | 12.24 | 11.88 | 11.52 | 11.16 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.44 | 10.08 | 9.72 | 9.36 | 9 | 9 | 9 | 9 | 9 | 9
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645 | 22.7645
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0.19286 | 1.295 | 9.3391 | 18.421 | 11.144 | 1.35 | 1.517 | 7.729 | 0 | 0 | 0 | 0 | 7.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035 | 25.035
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0.1 | 0.17 | 1.2035 | 1.9 | 0.83 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0.075 | 0.024 | 0.358 | 0.01 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014 | 17.8014
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0.158 | 4.191 | 5.363 | 9.753 | 5.42 | 2.55 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464 | 0.22464
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 896 | 876.8 | 857.6 | 837.76 | 817.92 | 798.08 | 778.24 | 758.4 | 738.88 | 719.36 | 699.84 | 680.32 | 660.8 | 649.92 | 639.04 | 628.16 | 617.28 | 606.4 | 595.52 | 584.64 | 573.76 | 562.88 | 552 | 541.12 | 530.24 | 519.36 | 508.48 | 497.6
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 12.8 | 12.8 | 12.8 | 12.48 | 12.16 | 11.84 | 11.52 | 11.2 | 10.88 | 10.56 | 10.24 | 9.92 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.28 | 8.96 | 8.64 | 8.32 | 8 | 8 | 8 | 8 | 8 | 8
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 849 | 830.81 | 812.61 | 793.82 | 775.02 | 756.22 | 737.42 | 718.62 | 700.12 | 681.63 | 663.13 | 644.63 | 626.14 | 615.83 | 605.52 | 595.21 | 584.9 | 574.59 | 564.28 | 553.97 | 543.66 | 533.35 | 523.04 | 512.74 | 502.43 | 492.12 | 481.81 | 471.5
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 12 | 12 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 10.5 | 10.2 | 9.9 | 9.6 | 9.3 | 9 | 9 | 9 | 9 | 9 | 9 | 8.7 | 8.4 | 8.1 | 7.8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947 | 0.947
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.2 | 0.47 | 0.5 | 0.5 | 0.87 | 0.45 | 0.45 | 0.35 | 0 | 0.35 | 0.35 | 0.35 | 0 | 0.4 | 0.4 | 0 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1680 | 1644 | 1608 | 1570.8 | 1533.6 | 1496.4 | 1459.2 | 1422 | 1385.4 | 1348.8 | 1312.2 | 1275.6 | 1239 | 1218.6 | 1198.2 | 1177.8 | 1157.4 | 1137 | 1116.6 | 1096.2 | 1075.8 | 1055.4 | 1035 | 1014.6 | 994.2 | 973.8 | 953.4 | 933
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 24 | 24 | 24 | 23.4 | 22.8 | 22.2 | 21.6 | 21 | 20.4 | 19.8 | 19.2 | 18.6 | 18 | 18 | 18 | 18 | 18 | 18 | 17.4 | 16.8 | 16.2 | 15.6 | 15 | 15 | 15 | 15 | 15 | 15
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0.0071 | 0.032 | 0.036 | 0 | 0.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1218 | 1158.78 | 1099.56 | 1091.88 | 1084.2 | 1076.51 | 1068.83 | 1061.15 | 1053.79 | 1046.42 | 1039.06 | 1031.7 | 1024.34 | 1016.97 | 1009.61 | 1002.25 | 994.89 | 987.52 | 980.16 | 972.8 | 965.44 | 958.07 | 950.71 | 943.03 | 935.35 | 927.66 | 919.98 | 912.3
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 35.2 | 35.2 | 35.2 | 34.88 | 34.56 | 34.24 | 33.92 | 33.6 | 33.28 | 32.96 | 32.64 | 32.32 | 32 | 32 | 32 | 32 | 32 | 32 | 31.68 | 31.36 | 31.04 | 30.72 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 837.1 | 786.5 | 735.9 | 720.7 | 705.5 | 690.4 | 675.2 | 660 | 653.2 | 646.4 | 639.5 | 632.7 | 625.9 | 618.9 | 611.8 | 604.8 | 597.7 | 590.7 | 583.9 | 577.1 | 570.2 | 563.4 | 556.6 | 549.8 | 543 | 536.1 | 529.3 | 522.5
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 24.2 | 23.65 | 23.1 | 22.88 | 22.66 | 22.44 | 22.22 | 22 | 21.56 | 21.12 | 20.68 | 20.24 | 19.8 | 19.58 | 19.36 | 19.14 | 18.92 | 18.7 | 18.48 | 18.26 | 18.04 | 17.82 | 17.6 | 17.82 | 18.04 | 18.26 | 18.48 | 18.7
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
12 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157 | 5.157
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
13 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994 | 19.5994
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
14 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836 | 17.836
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
16 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
17 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 989.3 | 929.5 | 869.7 | 851.8 | 833.8 | 815.9 | 797.9 | 780 | 771.9 | 763.9 | 755.8 | 747.8 | 739.7 | 731.4 | 723.1 | 714.7 | 706.4 | 698.1 | 690 | 682 | 673.9 | 665.9 | 657.8 | 649.7 | 641.7 | 633.6 | 625.6 | 617.5
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 28.6 | 27.95 | 27.3 | 27.04 | 26.78 | 26.52 | 26.26 | 26 | 25.48 | 24.96 | 24.44 | 23.92 | 23.4 | 23.14 | 22.88 | 22.62 | 22.36 | 22.1 | 21.84 | 21.58 | 21.32 | 21.06 | 20.8 | 21.06 | 21.32 | 21.58 | 21.84 | 22.1
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
18 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1391 | 1323.37 | 1255.74 | 1246.96 | 1238.19 | 1229.42 | 1220.64 | 1211.87 | 1203.46 | 1195.05 | 1186.65 | 1178.24 | 1169.83 | 1161.42 | 1153.01 | 1144.6 | 1136.2 | 1127.79 | 1119.38 | 1110.97 | 1102.56 | 1094.16 | 1085.75 | 1076.97 | 1068.2 | 1059.43 | 1050.65 | 1041.88
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 39.6 | 39.6 | 39.6 | 39.24 | 38.88 | 38.52 | 38.16 | 37.8 | 37.44 | 37.08 | 36.72 | 36.36 | 36 | 36 | 36 | 36 | 36 | 36 | 35.64 | 35.28 | 34.92 | 34.56 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264 | 0.264
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
19 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.01 | 0.14 | 0.73 | 0.2 | 0.15 | 0.384 | 0.3 | 0.22 | 0 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1522 | 1430 | 1338 | 1310.4 | 1282.8 | 1255.2 | 1227.6 | 1200 | 1187.6 | 1175.2 | 1162.8 | 1150.4 | 1138 | 1125.2 | 1112.4 | 1099.6 | 1086.8 | 1074 | 1061.6 | 1049.2 | 1036.8 | 1024.4 | 1012 | 999.6 | 987.2 | 974.8 | 962.4 | 950
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 44 | 43 | 42 | 41.6 | 41.2 | 40.8 | 40.4 | 40 | 39.2 | 38.4 | 37.6 | 36.8 | 36 | 35.6 | 35.2 | 34.8 | 34.4 | 34 | 33.6 | 33.2 | 32.8 | 32.4 | 32 | 32.4 | 32.8 | 33.2 | 33.6 | 34
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
20 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3800 | 3784 | 3768 | 3702.8 | 3637.6 | 3572.4 | 3507.2 | 3442 | 3156.4 | 2870.8 | 2585.2 | 2299.6 | 2014 | 2003.2 | 1992.4 | 1981.6 | 1970.8 | 1960 | 1951.8 | 1943.6 | 1935.4 | 1927.2 | 1919 | 1912.4 | 1905.8 | 1899.2 | 1892.6 | 1886
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114 | 114 | 114 | 112.2 | 110.4 | 108.6 | 106.8 | 105 | 103.4 | 101.8 | 100.2 | 98.6 | 97 | 95.6 | 94.2 | 92.8 | 91.4 | 90 | 88.8 | 87.6 | 86.4 | 85.2 | 84 | 83.2 | 82.4 | 81.6 | 80.8 | 80
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
21 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3800 | 3784 | 3768 | 3702.8 | 3637.6 | 3572.4 | 3507.2 | 3442 | 3156.4 | 2870.8 | 2585.2 | 2299.6 | 2014 | 2003.2 | 1992.4 | 1981.6 | 1970.8 | 1960 | 1951.8 | 1943.6 | 1935.4 | 1927.2 | 1919 | 1912.4 | 1905.8 | 1899.2 | 1892.6 | 1886
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114 | 114 | 114 | 112.2 | 110.4 | 108.6 | 106.8 | 105 | 103.4 | 101.8 | 100.2 | 98.6 | 97 | 95.6 | 94.2 | 92.8 | 91.4 | 90 | 88.8 | 87.6 | 86.4 | 85.2 | 84 | 83.2 | 82.4 | 81.6 | 80.8 | 80
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
22 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3800 | 3784 | 3768 | 3702.8 | 3637.6 | 3572.4 | 3507.2 | 3442 | 3156.4 | 2870.8 | 2585.2 | 2299.6 | 2014 | 2003.2 | 1992.4 | 1981.6 | 1970.8 | 1960 | 1951.8 | 1943.6 | 1935.4 | 1927.2 | 1919 | 1912.4 | 1905.8 | 1899.2 | 1892.6 | 1886
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114 | 114 | 114 | 112.2 | 110.4 | 108.6 | 106.8 | 105 | 103.4 | 101.8 | 100.2 | 98.6 | 97 | 95.6 | 94.2 | 92.8 | 91.4 | 90 | 88.8 | 87.6 | 86.4 | 85.2 | 84 | 83.2 | 82.4 | 81.6 | 80.8 | 80
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 6650 | 6510 | 6370 | 6060.6 | 5751.2 | 5441.8 | 5132.4 | 4823 | 4602.8 | 4382.7 | 4162.6 | 3942.4 | 3722.2 | 3694.2 | 3666.2 | 3638.2 | 3610.2 | 3582.2 | 3561.2 | 3540.2 | 3519.2 | 3498.2 | 3477.2 | 3460.8 | 3444.3 | 3427.9 | 3411.5 | 3395
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 199.5 | 195.12 | 190.75 | 187.6 | 184.45 | 181.3 | 178.15 | 175 | 172.2 | 169.4 | 166.6 | 163.8 | 161 | 158.9 | 156.8 | 154.7 | 152.6 | 150.5 | 148.4 | 146.3 | 144.2 | 142.1 | 140 | 138.25 | 136.5 | 134.75 | 133 | 131.25
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 6142.71 | 6116.85 | 6090.98 | 5985.59 | 5880.19 | 5774.79 | 5669.4 | 5564 | 5102.33 | 4640.66 | 4178.98 | 3717.31 | 3255.64 | 3238.18 | 3220.72 | 3203.26 | 3185.8 | 3168.35 | 3155.09 | 3141.83 | 3128.58 | 3115.32 | 3102.07 | 3091.4 | 3080.73 | 3070.06 | 3059.39 | 3048.72
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 182.4 | 182.4 | 182.4 | 179.52 | 176.64 | 173.76 | 170.88 | 168 | 165.44 | 162.88 | 160.32 | 157.76 | 155.2 | 152.96 | 150.72 | 148.48 | 146.24 | 144 | 142.08 | 140.16 | 138.24 | 136.32 | 134.4 | 133.12 | 131.84 | 130.56 | 129.28 | 128
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
25 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 7600 | 7440 | 7280 | 6926.4 | 6572.8 | 6219.2 | 5865.6 | 5512 | 5260.4 | 5008.8 | 4757.2 | 4505.6 | 4254 | 4222 | 4190 | 4158 | 4126 | 4094 | 4070 | 4046 | 4022 | 3998 | 3974 | 3955.2 | 3936.4 | 3917.6 | 3898.8 | 3880
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 228 | 223 | 218 | 214.4 | 210.8 | 207.2 | 203.6 | 200 | 196.8 | 193.6 | 190.4 | 187.2 | 184 | 181.6 | 179.2 | 176.8 | 174.4 | 172 | 169.6 | 167.2 | 164.8 | 162.4 | 160 | 158 | 156 | 154 | 152 | 150
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
26 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3377.76 | 3411.53 | 3445.31 | 3469.945 | 3494.585 | 3519.22 | 3543.855 | 3568.49 | 3593.005 | 3617.515 | 3642.03 | 3666.54 | 3691.055 | 3715.69 | 3740.325 | 3764.96 | 3789.595 | 3814.235 | 3838.745 | 3863.26 | 3887.77 | 3912.285 | 3936.795 | 3961.43 | 3986.07 | 4010.705 | 4035.34 | 4059.975
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2 | 55.2
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
27 | PWRHYDNPLXX | Large Hydropower, Nepal, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0.04 | 0.5356 | 0.1204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1740.385 | 1757.79 | 1775.19 | 1788.64 | 1802.085 | 1815.53 | 1828.975 | 1842.425 | 1855.785 | 1869.145 | 1882.51 | 1895.87 | 1909.23 | 1922.675 | 1936.125 | 1949.57 | 1963.015 | 1976.46 | 1989.825 | 2003.185 | 2016.545 | 2029.91 | 2043.27 | 2056.715 | 2070.16 | 2083.61 | 2097.055 | 2110.5
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075 | 30.075
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | 2.33
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
28 | PWRHYDBTNXX | Large Hydropower, Bhutan, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 1.138 | 0 | 0.6 | 0.67 | 0 | 4.145 | 0 | 0 | 0 | 0 | 2.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2500 | 2525 | 2550 | 2565 | 2580 | 2595 | 2610 | 2625 | 2640 | 2655 | 2670 | 2685 | 2700 | 2715 | 2730 | 2745 | 2760 | 2775 | 2790 | 2805 | 2820 | 2835 | 2850 | 2865 | 2880 | 2895 | 2910 | 2925
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756 | 19.756
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
29 | PWRHYDINDNO | Large Hydropower, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 2.024 | 0.8015 | 1.84 | 0.902 | 0.21 | 0.3 | 0 | 0 | 0 | 0.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2500 | 2525 | 2550 | 2565 | 2580 | 2595 | 2610 | 2625 | 2640 | 2655 | 2670 | 2685 | 2700 | 2715 | 2730 | 2745 | 2760 | 2775 | 2790 | 2805 | 2820 | 2835 | 2850 | 2865 | 2880 | 2895 | 2910 | 2925
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027 | 2.027
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
30 | PWRHYDINDNE | Large Hydropower, India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 1.87 | 0 | 0 | 0.426 | 0 | 0 | 2.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2500 | 2525 | 2550 | 2565 | 2580 | 2595 | 2610 | 2625 | 2640 | 2655 | 2670 | 2685 | 2700 | 2715 | 2730 | 2745 | 2760 | 2775 | 2790 | 2805 | 2820 | 2835 | 2850 | 2865 | 2880 | 2895 | 2910 | 2925
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.066 | 0.12 | 0.5 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 4166.67 | 4208.33 | 4250 | 4275 | 4300 | 4325 | 4350 | 4375 | 4400 | 4425 | 4450 | 4475 | 4500 | 4525 | 4550 | 4575 | 4600 | 4625 | 4650 | 4675 | 4700 | 4725 | 4750 | 4775 | 4800 | 4825 | 4850 | 4875
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
32 | PWRHYDLKAXX | Large Hydropower, Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0
33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747 | 11.747
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
34 | PWRHYDINDSO | Large Hydropower, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 1.23 | 1.64 | 0.96 | 4.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392 | 7.392
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
35 | PWRHYDINDWE | Large Hydropower, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 1.92 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 1.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865 | 45.865
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
37 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0.66 | 0 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998 | 44.998
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
38 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 3.2 | 2.64 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.66 | 2.26 | 1.32 | 2.92 | 2.4 | 2.4 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786 | 85.786
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
40 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 1.6 | 3.2 | 1.6 | 3.2 | 4.24 | 0 | 0 | 0 | 0 | 0 | 6.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
41 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995 | 5.995
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
43 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492 | 6.492
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
44 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806 | 10.806
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
46 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
47 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660 | 1660
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
48 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145 | 1351.145
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
49 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.235 | 0.35 | 0.115 | 0.2 | 0 | 0.13 | 0.1 | 0 | 0 | 0 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315 | 0.5315
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
50 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168 | 1.168
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
52 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0
53 | PWROILNPLXX | Oil/Diesel generation, Nepal, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0
54 | PWROILINDNO | Oil/Diesel generation, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366 | 0.43366
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0
55 | PWROILINDSO | Oil/Diesel generation, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0
56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0
57 | PWROILINDWE | Oil/Diesel generation, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0
58 | PWROILINDNE | Oil/Diesel generation, India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157 | 3.1157
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
60 | PWRBIOINDNO | Biomass/Bagasse, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571 | 3.5571
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
61 | PWRBIOINDSO | Biomass/Bagasse, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436 | 3.0436
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
63 | PWRBIOINDWE | Biomass/Bagasse, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158 | 0.0158
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
64 | PWRBIOINDNE | Biomass/Bagasse, India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6 | 2316.6
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69 | 92.69
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
65 | PWRBIONPLXX | Biomass/Bagasse, Nepal, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
66 | PWRBIOLKAXX | Biomass/Bagasse, Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.01 | 0.015 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141 | 0.24141
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
67 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876 | 0.18876
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
68 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806 | 0.11806
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
70 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
71 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
73 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62 | 1.62
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
74 | PWRURNINDNO | Nuclear, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
75 | PWRURNINDSO | Nuclear, India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
77 | PWRURNINDWE | Nuclear, India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
78 | PWRURNINDNE | Nuclear, India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 1.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 4589 | 4566.5 | 4544 | 4522 | 4500 | 4478 | 4456 | 4434 | 4412.6 | 4391.2 | 4369.8 | 4348.4 | 4327 | 4306 | 4285 | 4264 | 4243 | 4222 | 4201.6 | 4181.2 | 4160.8 | 4140.4 | 4120 | 4100 | 4080 | 4060 | 4040 | 4020
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
80 | PWRGEOINDNO | Geothermal, India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1058.4 | 964.8 | 871.2 | 844.6 | 817.9 | 791.3 | 764.6 | 738 | 727.4 | 716.9 | 706.3 | 695.8 | 685.2 | 674.9 | 664.6 | 654.2 | 643.9 | 633.6 | 622.8 | 612 | 601.2 | 590.4 | 579.6 | 569 | 558.5 | 547.9 | 537.4 | 526.8
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 24 | 24.6 | 25.2 | 24.24 | 23.28 | 22.32 | 21.36 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.16 | 19.92 | 19.68 | 19.44 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 18.96 | 18.72 | 18.48 | 18.24 | 18
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 970.2 | 884.4 | 798.6 | 774.2 | 749.8 | 725.3 | 700.9 | 676.5 | 666.8 | 657.1 | 647.5 | 637.8 | 628.1 | 618.6 | 609.2 | 599.7 | 590.3 | 580.8 | 570.9 | 561 | 551.1 | 541.2 | 531.3 | 521.6 | 511.9 | 502.3 | 492.6 | 482.9
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 28 | 28.7 | 29.4 | 28.28 | 27.16 | 26.04 | 24.92 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.52 | 23.24 | 22.96 | 22.68 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.12 | 21.84 | 21.56 | 21.28 | 21
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
82 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 882 | 804 | 726 | 703.8 | 681.6 | 659.4 | 637.2 | 615 | 606.2 | 597.4 | 588.6 | 579.8 | 571 | 562.4 | 553.8 | 545.2 | 536.6 | 528 | 519 | 510 | 501 | 492 | 483 | 474.2 | 465.4 | 456.6 | 447.8 | 439
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
83 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 882 | 804 | 726 | 703.8 | 681.6 | 659.4 | 637.2 | 615 | 606.2 | 597.4 | 588.6 | 579.8 | 571 | 562.4 | 553.8 | 545.2 | 536.6 | 528 | 519 | 510 | 501 | 492 | 483 | 474.2 | 465.4 | 456.6 | 447.8 | 439
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
84 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 882 | 804 | 726 | 703.8 | 681.6 | 659.4 | 637.2 | 615 | 606.2 | 597.4 | 588.6 | 579.8 | 571 | 562.4 | 553.8 | 545.2 | 536.6 | 528 | 519 | 510 | 501 | 492 | 483 | 474.2 | 465.4 | 456.6 | 447.8 | 439
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 882 | 804 | 726 | 703.8 | 681.6 | 659.4 | 637.2 | 615 | 606.2 | 597.4 | 588.6 | 579.8 | 571 | 562.4 | 553.8 | 545.2 | 536.6 | 528 | 519 | 510 | 501 | 492 | 483 | 474.2 | 465.4 | 456.6 | 447.8 | 439
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
86 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 882 | 804 | 726 | 703.8 | 681.6 | 659.4 | 637.2 | 615 | 606.2 | 597.4 | 588.6 | 579.8 | 571 | 562.4 | 553.8 | 545.2 | 536.6 | 528 | 519 | 510 | 501 | 492 | 483 | 474.2 | 465.4 | 456.6 | 447.8 | 439
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
87 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1146.6 | 1045.2 | 943.8 | 914.9 | 886.1 | 857.2 | 828.4 | 799.5 | 788.1 | 776.6 | 765.2 | 753.7 | 742.3 | 731.1 | 719.9 | 708.8 | 697.6 | 686.4 | 674.7 | 663 | 651.3 | 639.6 | 627.9 | 616.5 | 605 | 593.6 | 582.1 | 570.7
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 26 | 26.65 | 27.3 | 26.26 | 25.22 | 24.18 | 23.14 | 22.1 | 22.1 | 22.1 | 22.1 | 22.1 | 22.1 | 21.84 | 21.58 | 21.32 | 21.06 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.54 | 20.28 | 20.02 | 19.76 | 19.5
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
88 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1323 | 1206 | 1089 | 1055.7 | 1022.4 | 989.1 | 955.8 | 922.5 | 909.3 | 896.1 | 882.9 | 869.7 | 856.5 | 843.6 | 830.7 | 817.8 | 804.9 | 792 | 778.5 | 765 | 751.5 | 738 | 724.5 | 711.3 | 698.1 | 684.9 | 671.7 | 658.5
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 30 | 30.75 | 31.5 | 30.3 | 29.1 | 27.9 | 26.7 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.2 | 24.9 | 24.6 | 24.3 | 24 | 24 | 24 | 24 | 24 | 24 | 23.7 | 23.4 | 23.1 | 22.8 | 22.5
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
89 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.005 | 0.1 | 0 | 0.1 | 0.1 | 0.05 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1323 | 1206 | 1089 | 1055.7 | 1022.4 | 989.1 | 955.8 | 922.5 | 909.3 | 896.1 | 882.9 | 869.7 | 856.5 | 843.6 | 830.7 | 817.8 | 804.9 | 792 | 778.5 | 765 | 751.5 | 738 | 724.5 | 711.3 | 698.1 | 684.9 | 671.7 | 658.5
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 30 | 30.75 | 31.5 | 30.3 | 29.1 | 27.9 | 26.7 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.2 | 24.9 | 24.6 | 24.3 | 24 | 24 | 24 | 24 | 24 | 24 | 23.7 | 23.4 | 23.1 | 22.8 | 22.5
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
90 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2160 | 1957.8 | 1755.6 | 1694.2 | 1632.7 | 1571.3 | 1509.8 | 1448.4 | 1425.4 | 1402.3 | 1379.3 | 1356.2 | 1333.2 | 1310.2 | 1287.1 | 1264.1 | 1241 | 1218 | 1195 | 1171.9 | 1148.9 | 1125.8 | 1102.8 | 1080.2 | 1057.7 | 1035.1 | 1012.6 | 990
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1980 | 1794.7 | 1609.3 | 1553 | 1496.7 | 1440.3 | 1384 | 1327.7 | 1306.6 | 1285.5 | 1264.3 | 1243.2 | 1222.1 | 1201 | 1179.9 | 1158.7 | 1137.6 | 1116.5 | 1095.4 | 1074.3 | 1053.1 | 1032 | 1010.9 | 990.2 | 969.5 | 948.9 | 928.2 | 907.5
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
92 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1800 | 1631.5 | 1463 | 1411.8 | 1360.6 | 1309.4 | 1258.2 | 1207 | 1187.8 | 1168.6 | 1149.4 | 1130.2 | 1111 | 1091.8 | 1072.6 | 1053.4 | 1034.2 | 1015 | 995.8 | 976.6 | 957.4 | 938.2 | 919 | 900.2 | 881.4 | 862.6 | 843.8 | 825
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
93 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1800 | 1631.5 | 1463 | 1411.8 | 1360.6 | 1309.4 | 1258.2 | 1207 | 1187.8 | 1168.6 | 1149.4 | 1130.2 | 1111 | 1091.8 | 1072.6 | 1053.4 | 1034.2 | 1015 | 995.8 | 976.6 | 957.4 | 938.2 | 919 | 900.2 | 881.4 | 862.6 | 843.8 | 825
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
94 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1800 | 1631.5 | 1463 | 1411.8 | 1360.6 | 1309.4 | 1258.2 | 1207 | 1187.8 | 1168.6 | 1149.4 | 1130.2 | 1111 | 1091.8 | 1072.6 | 1053.4 | 1034.2 | 1015 | 995.8 | 976.6 | 957.4 | 938.2 | 919 | 900.2 | 881.4 | 862.6 | 843.8 | 825
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1800 | 1631.5 | 1463 | 1411.8 | 1360.6 | 1309.4 | 1258.2 | 1207 | 1187.8 | 1168.6 | 1149.4 | 1130.2 | 1111 | 1091.8 | 1072.6 | 1053.4 | 1034.2 | 1015 | 995.8 | 976.6 | 957.4 | 938.2 | 919 | 900.2 | 881.4 | 862.6 | 843.8 | 825
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
96 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1800 | 1631.5 | 1463 | 1411.8 | 1360.6 | 1309.4 | 1258.2 | 1207 | 1187.8 | 1168.6 | 1149.4 | 1130.2 | 1111 | 1091.8 | 1072.6 | 1053.4 | 1034.2 | 1015 | 995.8 | 976.6 | 957.4 | 938.2 | 919 | 900.2 | 881.4 | 862.6 | 843.8 | 825
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
97 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2340 | 2121 | 1901.9 | 1835.3 | 1768.8 | 1702.2 | 1635.7 | 1569.1 | 1544.1 | 1519.2 | 1494.2 | 1469.3 | 1444.3 | 1419.3 | 1394.4 | 1369.4 | 1344.5 | 1319.5 | 1294.5 | 1269.6 | 1244.6 | 1219.7 | 1194.7 | 1170.3 | 1145.8 | 1121.4 | 1096.9 | 1072.5
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
98 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2700 | 2447.2 | 2194.5 | 2117.7 | 2040.9 | 1964.1 | 1887.3 | 1810.5 | 1781.7 | 1752.9 | 1724.1 | 1695.3 | 1666.5 | 1637.7 | 1608.9 | 1580.1 | 1551.3 | 1522.5 | 1493.7 | 1464.9 | 1436.1 | 1407.3 | 1378.5 | 1350.3 | 1322.1 | 1293.9 | 1265.7 | 1237.5
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
99 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2700 | 2447.2 | 2194.5 | 2117.7 | 2040.9 | 1964.1 | 1887.3 | 1810.5 | 1781.7 | 1752.9 | 1724.1 | 1695.3 | 1666.5 | 1637.7 | 1608.9 | 1580.1 | 1551.3 | 1522.5 | 1493.7 | 1464.9 | 1436.1 | 1407.3 | 1378.5 | 1350.3 | 1322.1 | 1293.9 | 1265.7 | 1237.5
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
100 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | CapitalCost | USD/kW | User defined |  | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | FixedCost | USD/kW/yr | User defined |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | ResidualCapacity | GW | User defined |  | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189 | 1.7189
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | TotalAnnualMaxCapacity | GW | User defined
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | TotalAnnualMinCapacity | GW | User defined
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | AvailabilityFactor | fraction | User defined |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | Efficiency | fraction | User defined | bar: 2023 to 2050
29 | PWRSHPINDNO | Small Hydropower, India – North, region XX (investable) |  | TotalAnnualMinCapacityInvestment | GW | User defined |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | CapitalCost | USD/kW | User defined |  | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | FixedCost | USD/kW/yr | User defined |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | ResidualCapacity | GW | User defined |  | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333 | 1.9333
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | TotalAnnualMaxCapacity | GW | User defined
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | TotalAnnualMinCapacity | GW | User defined
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | AvailabilityFactor | fraction | User defined |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | Efficiency | fraction | User defined | bar: 2023 to 2050
34 | PWRSHPINDSO | Small Hydropower, India – South, region XX (investable) |  | TotalAnnualMinCapacityInvestment | GW | User defined |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | CapitalCost | USD/kW | User defined |  | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | FixedCost | USD/kW/yr | User defined |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | ResidualCapacity | GW | User defined |  | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | TotalAnnualMaxCapacity | GW | User defined
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | TotalAnnualMinCapacity | GW | User defined
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | AvailabilityFactor | fraction | User defined |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | Efficiency | fraction | User defined | bar: 2023 to 2050
31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | TotalAnnualMinCapacityInvestment | GW | User defined |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | CapitalCost | USD/kW | User defined |  | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | FixedCost | USD/kW/yr | User defined |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | ResidualCapacity | GW | User defined |  | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739 | 0.6739
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | TotalAnnualMaxCapacity | GW | User defined
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | TotalAnnualMinCapacity | GW | User defined
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | AvailabilityFactor | fraction | User defined |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | Efficiency | fraction | User defined | bar: 2023 to 2050
35 | PWRSHPINDWE | Small Hydropower, India – West, region XX (investable) |  | TotalAnnualMinCapacityInvestment | GW | User defined |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | CapitalCost | USD/kW | User defined |  | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | FixedCost | USD/kW/yr | User defined |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | ResidualCapacity | GW | User defined |  | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935 | 0.29935
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | TotalAnnualMaxCapacity | GW | User defined
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | TotalAnnualMinCapacity | GW | User defined
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | AvailabilityFactor | fraction | User defined |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | Efficiency | fraction | User defined | bar: 2023 to 2050
30 | PWRSHPINDNE | Small Hydropower, India – Northeast, region XX (investable) |  | TotalAnnualMinCapacityInvestment | GW | User defined |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacities_CF
Timeslices | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
S1D1 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524
S1D3 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06
S2D2 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975
S2D3 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05
S3D2 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906
S3D3 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05
S4D1 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214
S4D3 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867
S1D3 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05
S2D2 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229
S2D3 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05
S3D1 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255
S3D2 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641
S3D3 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219
S4D1 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333
S4D3 | 2 | PWRSPVBTNXX | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739
S1D3 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505
S2D2 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961
S2D3 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06
S3D1 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265
S3D2 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564
S3D3 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05
S4D1 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027
S4D3 | 3 | PWRSPVINDNO | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069
S1D3 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575
S2D3 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231
S3D3 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418
S4D3 | 4 | PWRSPVINDSO | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05
S1D2 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516
S1D3 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502
S2D2 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663
S2D3 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638
S3D2 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446
S3D3 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298
S4D2 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348
S4D3 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004
S1D3 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844
S2D3 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06
S3D1 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349
S3D3 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05
S4D1 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875
S4D3 | 6 | PWRSPVINDWE | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052
S1D2 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035
S1D3 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261
S2D2 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286
S2D3 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121
S3D2 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959
S3D3 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785
S4D2 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601
S4D3 | 7 | PWRSPVINDNE | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06
S1D2 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422
S1D3 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412
S2D2 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512
S2D3 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955
S3D2 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487
S3D3 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05
S4D2 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533
S4D3 | 8 | PWRSPVNPLXX | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578
S1D3 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074
S2D3 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361
S3D3 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418
S4D3 | 9 | PWRSPVLKAXX | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331
S1D3 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719
S2D3 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146
S3D3 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984
S4D3 | 10 | PWRSPVMDVXX | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271
S1D2 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973
S1D3 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761
S2D1 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216
S2D2 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854
S2D3 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451
S3D1 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614
S3D2 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055
S3D3 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914
S4D1 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462
S4D2 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134
S4D3 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855
S1D1 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887
S1D2 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763
S1D3 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784
S2D1 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788
S2D2 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705
S2D3 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576
S3D1 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479
S3D2 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703
S3D3 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201
S4D1 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296
S4D2 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323
S4D3 | 28 | PWRWONBTNXX | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816
S1D1 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525
S1D2 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302
S1D3 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968
S2D1 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756
S2D2 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531
S2D3 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589
S3D1 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612
S3D2 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239
S3D3 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488
S4D1 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002
S4D2 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386
S4D3 | 29 | PWRWONINDNO | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234
S1D1 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063
S1D2 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601
S1D3 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015
S2D1 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216
S2D2 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781
S2D3 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301
S3D1 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136
S3D2 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091
S3D3 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757
S4D1 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011
S4D2 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464
S4D3 | 30 | PWRWONINDSO | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699
S1D1 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451
S1D2 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909
S1D3 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672
S2D1 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438
S2D2 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886
S2D3 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172
S3D1 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549
S3D2 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303
S3D3 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717
S4D1 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851
S4D2 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597
S4D3 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278
S1D1 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383
S1D2 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478
S1D3 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659
S2D1 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236
S2D2 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744
S2D3 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218
S3D1 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917
S3D2 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679
S3D3 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838
S4D1 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023
S4D2 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604
S4D3 | 32 | PWRWONINDWE | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678
S1D1 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174
S1D2 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372
S1D3 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786
S2D1 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554
S2D2 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016
S2D3 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981
S3D1 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423
S3D2 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192
S3D3 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299
S4D1 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868
S4D2 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137
S4D3 | 33 | PWRWONINDNE | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112
S1D1 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158
S1D2 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806
S1D3 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569
S2D1 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244
S2D2 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086
S2D3 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415
S3D1 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318
S3D2 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821
S3D3 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758
S4D1 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716
S4D2 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307
S4D3 | 34 | PWRWONNPLXX | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756
S1D1 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017
S1D2 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575
S1D3 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039
S2D1 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541
S2D2 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144
S2D3 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453
S3D1 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862
S3D2 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108
S3D3 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255
S4D1 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973
S4D2 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404
S4D3 | 35 | PWRWONLKAXX | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799
S1D1 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967
S1D2 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357
S1D3 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032
S2D1 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355
S2D2 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542
S2D3 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464
S3D1 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581
S3D2 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062
S3D3 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914
S4D1 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934
S4D2 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462
S4D3 | 36 | PWRWONMDVXX | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016
S1D1 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195
S1D2 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195
S1D3 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195
S2D1 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
S2D2 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
S2D3 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
S3D1 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429
S3D2 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429
S3D3 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429
S4D1 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S4D2 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S4D3 | 37 | PWRWOFINDSO | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S1D1 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275
S1D2 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275
S1D3 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275
S2D1 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375
S2D2 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375
S2D3 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375
S3D1 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D2 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D3 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S4D1 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S4D2 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S4D3 | 38 | PWRWOFINDWE | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D1 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D2 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D3 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D1 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D2 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D3 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D1 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D2 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D3 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D1 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D2 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D3 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D1 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
S1D2 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
S1D3 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
S2D1 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
S2D2 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
S2D3 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
S3D1 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D2 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D3 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S4D1 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
S4D2 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
S4D3 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
S1D1 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
S1D2 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
S1D3 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
S2D1 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S2D2 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S2D3 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S3D1 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624
S3D2 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624
S3D3 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624
S4D1 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
S4D2 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
S4D3 | 41 | PWRWOFLKAXX | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
S1D1 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S1D2 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S1D3 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S2D1 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S2D2 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S2D3 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S3D1 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S3D2 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S3D3 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S4D1 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S4D2 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S4D3 | 42 | PWRWOFMDVXX | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S1D1 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D2 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S1D3 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S2D1 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
S2D2 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S2D3 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S3D1 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
S3D2 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
S3D3 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
S4D1 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58
S4D2 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D3 | 43 | PWRHYDNPLXX | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S1D1 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952
S1D2 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096
S1D3 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117
S2D1 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851
S2D2 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988
S2D3 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007
S3D1 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201
S3D2 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805
S3D3 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891
S4D1 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986
S4D2 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427
S4D3 | 44 | PWRHYDBTNXX | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649
S1D1 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D2 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D3 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S2D1 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S2D2 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S2D3 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D1 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
S3D2 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
S3D3 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
S4D1 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D2 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D3 | 45 | PWRHYDINDNO | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S1D1 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
S1D2 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
S1D3 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
S2D1 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S2D2 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S2D3 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S3D1 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
S3D2 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
S3D3 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
S4D1 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S4D2 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S4D3 | 46 | PWRHYDINDNE | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S1D1 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D2 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D3 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S2D1 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D2 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D3 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S3D1 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S3D2 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S3D3 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S4D1 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S4D2 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S4D3 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S1D1 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357
S1D2 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808
S1D3 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507
S2D1 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692
S2D2 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895
S2D3 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754
S3D1 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814
S3D2 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702
S3D3 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278
S4D1 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793
S4D2 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477
S4D3 | 48 | PWRHYDLKAXX | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914
S1D1 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D2 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S1D3 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S2D1 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
S2D2 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S2D3 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S3D1 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
S3D2 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
S3D3 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
S4D1 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58
S4D2 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D3 | 49 | PWRHYDNPLXX | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S1D1 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952
S1D2 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096
S1D3 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117
S2D1 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851
S2D2 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988
S2D3 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007
S3D1 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201
S3D2 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805
S3D3 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891
S4D1 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986
S4D2 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427
S4D3 | 50 | PWRHYDBTNXX | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649
S1D1 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
S1D2 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
S1D3 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
S2D1 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
S2D2 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
S2D3 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
S3D1 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
S3D2 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
S3D3 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
S4D1 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D2 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D3 | 51 | PWRHYDINDNO | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S1D1 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
S1D2 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
S1D3 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
S2D1 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D2 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D3 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S3D1 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
S3D2 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
S3D3 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
S4D1 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S4D2 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S4D3 | 52 | PWRHYDINDNE | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S1D1 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 53 | PWRHYDINDSO | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 54 | PWRHYDINDWE | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 55 | PWRHYDINDNO | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
S1D2 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S1D3 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S2D1 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D2 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D3 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S3D1 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S3D2 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S3D3 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
S4D1 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S4D2 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S4D3 | 56 | PWRHYDNPLXX | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S1D1 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235
S1D2 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
S1D3 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131
S2D1 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188
S2D2 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833
S2D3 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877
S3D1 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503
S3D2 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457
S3D3 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542
S4D1 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778
S4D2 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854
S4D3 | 57 | PWRHYDLKAXX | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029
S1D1 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 59 | PWRSDSBTNXX | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 60 | PWRSDSINDNO | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 61 | PWRSDSINDSO | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 63 | PWRSDSINDWE | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 64 | PWRSDSINDNE | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 65 | PWRSDSNPLXX | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 66 | PWRSDSLKAXX | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 67 | PWRSDSMDVXX | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 69 | PWRLDSBTNXX | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 70 | PWRLDSINDNO | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 71 | PWRLDSINDSO | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 73 | PWRLDSINDWE | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 74 | PWRLDSINDNE | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 75 | PWRLDSNPLXX | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 76 | PWRLDSLKAXX | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 77 | PWRLDSMDVXX | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050

## VariableCost
Mode.Operation | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Parameter | Projection.Mode | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | 1 | MINCOABGD | Coal mining/import, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.28 | 4.26 | 4.24 | 4.22 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
1 | 2 | MINCOABTN | Coal mining/import, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.208 | 4.116 | 4.024 | 3.932 | 3.84 | 3.856 | 3.872 | 3.888 | 3.904 | 3.92 | 3.936 | 3.952 | 3.968 | 3.984 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
1 | 3 | MINCOAIND | Coal mining/import, India | 12 | VariableCost | USD/GJ | 0 | User defined | 2.2 | 2.2 | 2.2 | 2.22 | 2.24 | 2.26 | 2.28 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.32 | 2.34 | 2.36 | 2.38 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.42 | 2.44 | 2.46 | 2.48 | 2.5
1 | 4 | MINCOANPL | Coal mining/import, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.208 | 4.116 | 4.024 | 3.932 | 3.84 | 3.856 | 3.872 | 3.888 | 3.904 | 3.92 | 3.936 | 3.952 | 3.968 | 3.984 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
1 | 5 | MINCOALKA | Coal mining/import, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.208 | 4.116 | 4.024 | 3.932 | 3.84 | 3.856 | 3.872 | 3.888 | 3.904 | 3.92 | 3.936 | 3.952 | 3.968 | 3.984 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
1 | 6 | MINCOAMDV | Coal mining/import, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.208 | 4.116 | 4.024 | 3.932 | 3.84 | 3.856 | 3.872 | 3.888 | 3.904 | 3.92 | 3.936 | 3.952 | 3.968 | 3.984 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
1 | 7 | MINGASBGD | Natural Gas supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 5.5 | 5.5 | 5.5 | 5.54 | 5.58 | 5.62 | 5.66 | 5.7 | 5.72 | 5.74 | 5.76 | 5.78 | 5.8 | 5.82 | 5.84 | 5.86 | 5.88 | 5.9 | 5.92 | 5.94 | 5.96 | 5.98 | 6 | 6 | 6 | 6 | 6 | 6
1 | 8 | MINGASBTN | Natural Gas supply, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1 | 9 | MINGASIND | Natural Gas supply, India | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1 | 10 | MINGASNPL | Natural Gas supply, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1 | 11 | MINGASLKA | Natural Gas supply, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1 | 12 | MINGASMDV | Natural Gas supply, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
1 | 13 | MINOILBGD | Oil supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.64 | 14.48 | 14.32 | 14.16 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
1 | 14 | MINOILBTN | Oil supply, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.64 | 14.48 | 14.32 | 14.16 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
1 | 15 | MINOILIND | Oil supply, India | 12 | VariableCost | USD/GJ | 0 | User defined | 13.56 | 12.825 | 12.09 | 12.286 | 12.482 | 12.678 | 12.874 | 13.07 | 13.07 | 13.07 | 13.07 | 13.07 | 13.07 | 13.136 | 13.202 | 13.268 | 13.334 | 13.4 | 13.302 | 13.204 | 13.106 | 13.008 | 12.91 | 12.812 | 12.714 | 12.616 | 12.518 | 12.42
1 | 16 | MINOILNPL | Oil supply, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.64 | 14.48 | 14.32 | 14.16 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
1 | 17 | MINOILLKA | Oil supply, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.64 | 14.48 | 14.32 | 14.16 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
1 | 18 | MINOILMDV | Oil supply, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 24.5 | 22.75 | 21 | 20.7 | 20.4 | 20.1 | 19.8 | 19.5 | 19.3 | 19.1 | 18.9 | 18.7 | 18.5 | 18.3 | 18.1 | 17.9 | 17.7 | 17.5 | 17.3 | 17.1 | 16.9 | 16.7 | 16.5 | 16.3 | 16.1 | 15.9 | 15.7 | 15.5
1 | 19 | MINURNBGD | Uranium supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 20 | MINURNBTN | Uranium supply, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 21 | MINURNIND | Uranium supply, India | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 22 | MINURNNPL | Uranium supply, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 23 | MINURNLKA | Uranium supply, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 24 | MINURNMDV | Uranium supply, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 26 | RNWBIOBTNXX | Biomass supply, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 27 | RNWBIOINDNO | Biomass supply, India – North | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 28 | RNWBIOINDSO | Biomass supply, India – South | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 29 | RNWBIOINDEA | Biomass supply, India – East | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 30 | RNWBIOINDWE | Biomass supply, India – West | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 31 | RNWBIOINDNE | Biomass supply, India – Northeast | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 32 | RNWBIONPLXX | Biomass supply, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 33 | RNWBIOLKAXX | Biomass supply, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
1 | 34 | RNWBIOMDVXX | Biomass supply, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5

## Demand_Projection
Demand/Share | Fuel/Tech | Name | Ref.Cap.BY | Ref.OAR.BY | Ref.km.BY | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Improvement_Notes | References
Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 427.324 | 456.303 | 487.247 | 520.29 | 555.573 | 593.249 | 633.481 | 676.44 | 712.658 | 750.815 | 791.015 | 833.367 | 877.987 | 924.996 | 974.521 | 1026.699 | 1081.67 | 1139.585 | 1200.6 | 1251.814 | 1305.212 | 1360.888 | 1418.939 | 1479.467 | 1542.576 | 1608.377 | 1676.985 | 1748.52 | Actualizado a IEPMP 2023 (Power Div / JICA-IEEJ, Nov 2023), escenario ATS (Advanced Technology Scenario) / GDP case In-Between — caso principal IEEJ para planificación de potencia (Capítulo 5). Anchors oficiales IEPMP Tabla 4.3-1 (p.56): 2019=328.68 PJ (histórico), 2030=676.44 PJ, 2041=1200.60 PJ, 2050=1748.52 PJ. Años intermedios: interpolación log-lineal (CAGR entre milestones) — el IEPMP solo publica los 4 milestone years, años intermedios requieren interpolación externa. CAGRs implícitos: 6.78%/año (2019-2030), 5.35%/año (2030-2041), 4.27%/año (2041-2050). Caveat: IEPMP 2023 está en revisión por el gobierno interino; plan sucesor EPSMP 2026-2050 en preparación. IEPMP 2023 sigue siendo el plan aprobado oficial. El alternativo PP2041 (high-growth, 2425 PJ @2050) disponible en workbook fuente para sensibilidad. | Power Division / MoPEMR / JICA-IEEJ (2023). Integrated Energy and Power Master Plan (IEPMP) 2023. Government of Bangladesh, Nov 2023. Tabla 4.3-1 'Outlook of Power Supply' (p.56, PDF p.109): Power Generation TWh por GDP case (PP2041 / In-Between) en years 2019, 2030, 2041, 2050. Tabla 5.2-1 'Maximum Electric Power Demand' (p.64, PDF p.117) para peak cross-check. Escenario central: ATS (Advanced Technology Scenario, JICA-recommended). GDP case: In-Between (caso principal IEEJ Cap.5). Conversión: PJ = TWh × 3.6. URL: https://powerdivision.portal.gov.bd (repositorio IEPMP 2023). Status Abr-2026: plan aprobado vigente, en revisión por gobierno interino (plan sucesor EPSMP 2026-2050 en preparación).
Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 21.222 | 22.705 | 24.293 | 25.991 | 27.807 | 29.751 | 31.831 | 34.056 | 36.438 | 38.987 | 41.714 | 44.632 | 47.753 | 51.094 | 54.667 | 58.491 | 62.583 | 66.96 | 71.644 | 76.655 | 82.017 | 87.753 | 93.892 | 100.459 | 107.486 | 115.004 | 123.048 | 131.655 | Actualizado a National Energy Policy 2025 (MoENR, Jun-2025) — escenario Conservative (7%/año CAGR, consistente con tasa histórica PSMP 7.1%). 2023: valor observado 5,895 GWh (NSB Environmental Accounts 2024). 2024-2040: proyección suavizada con CAGR 7% hasta target Conservative 2030 (9,460 GWh) y 2040 (18,600 GWh). 2041-2050: extrapolación continuando al mismo 7% CAGR (horizonte del documento termina en 2040). Asume que Bhutan NO ejecuta en plazo los targets ambiciosos del NEP (15 GW hydro + 5 GW solar by 2040) — trayectoria baja defendible por retrasos históricos observados en Pun-I/II. Para alta-ejecución del NEP ver escenarios Central (DoHPS 400% by 2030) o High (NEP 10× vision) del workbook fuente. v2 reemplaza al NTGMP 2018 que sobreestimaba exportaciones ~4× y subestimaba demanda doméstica ~30% respecto a actuales 2023. | MoENR (2025). National Energy Policy 2025 — Empowering Energy Security & Sustainable Growth. Ministry of Energy & Natural Resources, Royal Government of Bhutan, aprobada 5-Jun-2025 (en vigor 10-Jun-2025). 33 pp. §1.4 (final energy 2022), §1.5 (installed capacity Jun-2025), §1.9 y §4.1 (targets 2040: 15 GW hydro + 5 GW solar), §4.2 (demand outlook). ¦ NSB (2024). Environmental Accounts Statistics 2024, National Statistics Bureau, RGoB — observado 2023: supply 11,158 GWh, domestic 5,895 GWh, export 5,143 GWh. ¦ DGPC Annual Report 2023 — generation by plant. ¦ MoENR/DoHPS (2024). Proyección 400% growth by 2030 (citada en Kuensel, REDR-2024) — base de escenario Central. URL NEP 2025: https://www.moenr.gov.bt/wp-content/uploads/2017/07/National-Energy-Policy-2025.pdf ¦ Conversión: PJ = GWh × 0.0036.
Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 1797.26 | 1902.218 | 2013.185 | 2132.323 | 2258.795 | 2391.757 | 2547.194 | 2665.462 | 2784.762 | 2925.014 | 3065.265 | 3205.517 | 3345.768 | 3486.02 | 3638.537 | 3791.054 | 3943.571 | 4096.088 | 4248.605 | 4420.075 | 4598.466 | 4784.056 | 4977.136 | 5178.009 | 5386.99 | 5604.404 | 5830.593 | 6065.911 | Actualizado a 20th EPS (CEA Nov 2022). 2023-2031: Tabla 2.5 valores exactos (anual). 2036 y 2041: Tabla 6.2 valores exactos. 2032-2035 y 2037-2040: interpolación lineal entre anchors del 20th EPS. 2042-2050: extrapolación con CAGR 4.04%/año (tasa 2036-37 a 2041-42 del 20th EPS) — fuera del horizonte del documento original. | CEA (2022). Report on Twentieth Electric Power Survey of India (Volume-I). Central Electricity Authority, Ministry of Power, Government of India, Nov 2022. Table 2.5 (Chapter 2, Sec. 2.3, printed p.33 / PDF p.34): Region-wise electrical energy requirement at power station bus bars in MU, FY2021-22 to FY2031-32. Table 6.2 (Chapter 6, printed p.166 / PDF p.167): Perspective demand projection for FY2031-32, FY2036-37, FY2041-42. Conversion: PJ = MU × 0.0036. URL: https://cea.nic.in/wp-content/uploads/ps___lf/2023/02/Volume_I_Report_of_20th_Electric_Power_Survey.pdf
Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 1396.998 | 1478.113 | 1564.24 | 1659.071 | 1755.004 | 1854.932 | 1970.672 | 2060.276 | 2147.605 | 2252.516 | 2357.426 | 2462.337 | 2567.247 | 2672.158 | 2784.321 | 2896.484 | 3008.647 | 3120.81 | 3232.973 | 3358.536 | 3488.977 | 3624.483 | 3765.252 | 3911.488 | 4063.404 | 4221.22 | 4385.165 | 4555.478 | Actualizado a 20th EPS (CEA Nov 2022). 2023-2031: Tabla 2.5 valores exactos (anual). 2036 y 2041: Tabla 6.2 valores exactos. 2032-2035 y 2037-2040: interpolación lineal entre anchors del 20th EPS. 2042-2050: extrapolación con CAGR 3.88%/año (tasa 2036-37 a 2041-42 del 20th EPS) — fuera del horizonte del documento original. | CEA (2022). Report on Twentieth Electric Power Survey of India (Volume-I). Central Electricity Authority, Ministry of Power, Government of India, Nov 2022. Table 2.5 (Chapter 2, Sec. 2.3, printed p.33 / PDF p.34): Region-wise electrical energy requirement at power station bus bars in MU, FY2021-22 to FY2031-32. Table 6.2 (Chapter 6, printed p.166 / PDF p.167): Perspective demand projection for FY2031-32, FY2036-37, FY2041-42. Conversion: PJ = MU × 0.0036. URL: https://cea.nic.in/wp-content/uploads/ps___lf/2023/02/Volume_I_Report_of_20th_Electric_Power_Survey.pdf
Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 695.444 | 738.864 | 788.26 | 838.696 | 892.667 | 948.668 | 1016.15 | 1063.35 | 1109.171 | 1171.99 | 1234.808 | 1297.627 | 1360.445 | 1423.264 | 1494.272 | 1565.28 | 1636.287 | 1707.295 | 1778.303 | 1859.302 | 1943.989 | 2032.535 | 2125.113 | 2221.908 | 2323.112 | 2428.925 | 2539.559 | 2655.231 | Actualizado a 20th EPS (CEA Nov 2022). 2023-2031: Tabla 2.5 valores exactos (anual). 2036 y 2041: Tabla 6.2 valores exactos. 2032-2035 y 2037-2040: interpolación lineal entre anchors del 20th EPS. 2042-2050: extrapolación con CAGR 4.55%/año (tasa 2036-37 a 2041-42 del 20th EPS) — fuera del horizonte del documento original. | CEA (2022). Report on Twentieth Electric Power Survey of India (Volume-I). Central Electricity Authority, Ministry of Power, Government of India, Nov 2022. Table 2.5 (Chapter 2, Sec. 2.3, printed p.33 / PDF p.34): Region-wise electrical energy requirement at power station bus bars in MU, FY2021-22 to FY2031-32. Table 6.2 (Chapter 6, printed p.166 / PDF p.167): Perspective demand projection for FY2031-32, FY2036-37, FY2041-42. Conversion: PJ = MU × 0.0036. URL: https://cea.nic.in/wp-content/uploads/ps___lf/2023/02/Volume_I_Report_of_20th_Electric_Power_Survey.pdf
Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 1795.194 | 1901.347 | 2017.498 | 2148.455 | 2274.743 | 2405.585 | 2567.12 | 2659.27 | 2747.513 | 2880.729 | 3013.945 | 3147.16 | 3280.376 | 3413.592 | 3560.561 | 3707.53 | 3854.5 | 4001.469 | 4148.438 | 4313.395 | 4484.911 | 4663.247 | 4848.674 | 5041.475 | 5241.942 | 5450.38 | 5667.107 | 5892.451 | Actualizado a 20th EPS (CEA Nov 2022). 2023-2031: Tabla 2.5 valores exactos (anual). 2036 y 2041: Tabla 6.2 valores exactos. 2032-2035 y 2037-2040: interpolación lineal entre anchors del 20th EPS. 2042-2050: extrapolación con CAGR 3.98%/año (tasa 2036-37 a 2041-42 del 20th EPS) — fuera del horizonte del documento original. | CEA (2022). Report on Twentieth Electric Power Survey of India (Volume-I). Central Electricity Authority, Ministry of Power, Government of India, Nov 2022. Table 2.5 (Chapter 2, Sec. 2.3, printed p.33 / PDF p.34): Region-wise electrical energy requirement at power station bus bars in MU, FY2021-22 to FY2031-32. Table 6.2 (Chapter 6, printed p.166 / PDF p.167): Perspective demand projection for FY2031-32, FY2036-37, FY2041-42. Conversion: PJ = MU × 0.0036. URL: https://cea.nic.in/wp-content/uploads/ps___lf/2023/02/Volume_I_Report_of_20th_Electric_Power_Survey.pdf
Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 75.874 | 80.14 | 84.676 | 89.654 | 94.651 | 99.907 | 105.692 | 111.168 | 116.543 | 122.979 | 129.415 | 135.851 | 142.287 | 148.723 | 156.266 | 163.809 | 171.351 | 178.894 | 186.437 | 195.058 | 204.077 | 213.513 | 223.386 | 233.715 | 244.521 | 255.828 | 267.657 | 280.033 | Actualizado a 20th EPS (CEA Nov 2022). 2023-2031: Tabla 2.5 valores exactos (anual). 2036 y 2041: Tabla 6.2 valores exactos. 2032-2035 y 2037-2040: interpolación lineal entre anchors del 20th EPS. 2042-2050: extrapolación con CAGR 4.62%/año (tasa 2036-37 a 2041-42 del 20th EPS) — fuera del horizonte del documento original. | CEA (2022). Report on Twentieth Electric Power Survey of India (Volume-I). Central Electricity Authority, Ministry of Power, Government of India, Nov 2022. Table 2.5 (Chapter 2, Sec. 2.3, printed p.33 / PDF p.34): Region-wise electrical energy requirement at power station bus bars in MU, FY2021-22 to FY2031-32. Table 6.2 (Chapter 6, printed p.166 / PDF p.167): Perspective demand projection for FY2031-32, FY2036-37, FY2041-42. Conversion: PJ = MU × 0.0036. URL: https://cea.nic.in/wp-content/uploads/ps___lf/2023/02/Volume_I_Report_of_20th_Electric_Power_Survey.pdf
Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 47.862 | 51.657 | 55.656 | 59.874 | 64.328 | 69.39 | 74.922 | 80.909 | 87.387 | 94.399 | 101.988 | 106.577 | 111.166 | 115.755 | 120.343 | 124.932 | 129.521 | 134.11 | 138.699 | 143.288 | 147.877 | 152.466 | 157.055 | 161.644 | 166.233 | 170.822 | 175.411 | 180 | Actualizado combinando dos fuentes oficiales, escenario REFERENCE 100REMAP. 2023-2033: NEA System Load Forecast (NEA Planning Dept 2017), valores anuales oficiales de la utility — 2023 anchor = 13,295 GWh. 2034-2049: interpolación lineal entre endpoint NEA 2033 (28,330 GWh) y anchor 100REMAP REFERENCE 2050 (50,000 GWh); CAGR implícito 2033-2050 ≈ 3.4%/año. 2050: 100REMAP REFERENCE scenario (Teske, Niklas, Miyake 2023 — UTS-ISF para WWF/WFC). Caveat: NEA forecast tiende a sobreestimar el observado (~11% vs ADB 2023 reportado 11,023 GWh), pero es la proyección oficial utility disponible. Alternativas del mismo estudio 100REMAP: WEM 60 TWh @2050 (con políticas NDC), N-1.5°C 62 TWh @2050 (Paris-aligned) — disponibles en el workbook fuente si se cambia supuesto de escenario. | NEA (2017). System Load Forecast, NEA System Planning Department — vía Shakya 'A Glimpse of NEA Transmission System' (EDC Nepal 2017). Proyección anual FY2016/17 a FY2033/34 (System Energy Requirement ex-bus, incluye pérdidas T&D). ¦ Teske, S., Niklas, S., Miyake, S. (2023). Technical Scenario for 100% Renewable Energy in Nepal by 2050 — UTS Institute for Sustainable Futures para WWF/WFC. Tres escenarios (REFERENCE=50 TWh, WEM=60 TWh, N-1.5°C=62 TWh) en 2050. Este template usa REFERENCE. ¦ Cross-check: ADB Sector Assessment Energy Nepal 2023 (FY2023 observado = 11,023 GWh); NEA Annual Report FY2022/23 (9,358 GWh ventas internas). ¦ Government of Nepal (2021). Long-term Strategy for Net-Zero Emissions — marco sobre el que se construye 100REMAP. Conversión: PJ = GWh × 0.0036.
Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 56.074 | 60.487 | 63.81 | 67.14 | 70.668 | 74.383 | 78.3 | 82.537 | 86.494 | 90.626 | 94.928 | 99.446 | 104.26 | 109.48 | 115.031 | 120.938 | 126.99 | 133.337 | 140.011 | 146.761 | 153.68 | 160.823 | 167.846 | 174.931 | 182.138 | 189.158 | 196.366 | 203.846 | Actualizado a CEB LTGEP 2025-2044 (aprobado por PUCSL 15-May-2025, reemplaza al LTGEP 2023-2042). Basis: Net Generation en bus-bar de planta (definición consistente con la 'Energy Requirement at power station bus bars' del CEA). 2023: dato observado (15,576 GWh, restated en Statistical Digest 2024 desde 15,728 GWh preliminar). 2024: observado oficial (Statistical Digest 2024). 2025-2049: Tabla E1/3.3 Base Demand Forecast valores exactos. 2050: extrapolación con YoY 3.81% (tasa 2048-2049 del LTGEP, consistente con desaceleración trayectoria oficial). Caveat: 2022-2023 reflejan crisis económica + load shedding, no representan tendencia larga — LTGEP asume recuperación desde 2025. | CEB (2025). Long Term Generation Expansion Plan 2025-2044. Ceylon Electricity Board, Transmission and Generation Planning Branch. Presentado a PUCSL 4-Sep-2024, aprobado 15-May-2025. Tabla E1 / Tabla 3.3 (p. E-4 / p. 3-11): Base Demand Forecast Net Generation 2025-2049 (GWh). Tabla 1.6 (p. 1-17): Historical Electricity Generation 2009-2023. ¦ CEB (2025). Statistical Digest 2024, publicado Marzo 2025: Summary of Statistics (p.i) y Generation Statistics (p.01) — 2024 observado oficial y 2023 restated a 15,576 GWh. Conversión: PJ = GWh × 0.0036.
Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 6.77 | 7.096 | 7.444 | 7.816 | 8.214 | 8.64 | 9.167 | 9.727 | 10.323 | 10.958 | 11.634 | 12.249 | 12.901 | 13.594 | 14.331 | 15.115 | 15.949 | 16.836 | 17.341 | 17.861 | 18.397 | 18.949 | 19.518 | 20.006 | 20.506 | 21.018 | 21.544 | 22.082 | Actualizado a MCCEE Roadmap 2024-2033 (Nov 2024), Definición A (país completo, incluye autogeneración de resorts). 2023-2028: CAGRs por segmento del Roadmap (Malé 7.9%, Outer Islands 9.0%, Resorts 2.0%), calibrado al anchor oficial de 2400 GWh en 2028 (Figura 8, p.41). 2029-2040: Malé sostenido 8.05%/año para alcanzar el anchor de 400 MW peak en 2040 (p.34); otros segmentos 5% (2029-33) y 3.5% (2034-40). 2041-2045: extrapolación 3%/año. 2046-2050: extrapolación 2.5%/año. Caveat: Roadmap solo proyecta oficialmente a 2033 — años 2034-2050 construidos con CAGRs tapering típicos de SIDS maduros. | MCCEE (2024). Paving the Way for a Just Energy Transition in Maldives — Road Map for the Energy Sector 2024-2033. Ministry of Climate Change, Environment and Energy, Republic of Maldives, November 2024 (con apoyo técnico de ADB). Figura 8 (p.41): Forecasted Electricity Consumption — anchor 2028 = 2,400 GWh. pp.24-26: CAGRs por segmento (STELCO draft Master Plan). p.34 Sec. 5.1.6: Peak demand Greater Malé 2040 = 400 MW. Conversión: PJ = GWh × 0.0036. URL: https://www.environment.gov.mv/v2/wp-content/files/publications/20241107-pub-energy-roadmap-maldives-2024-2033-.pdf

## Demand_Profiles
Timeslices | Demand/Share | Fuel/Tech | Name | Ref.Cap.BY | Ref.OAR.BY | Ref.km.BY | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
S1D1 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691
S1D2 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911
S1D3 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581
S2D1 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407
S2D2 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106
S2D3 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101
S3D1 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481
S3D2 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232
S3D3 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388
S4D1 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289
S4D2 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386
S4D3 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437
S1D1 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974
S1D2 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287
S1D3 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996
S2D1 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086
S2D2 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688
S2D3 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711
S3D1 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967
S3D2 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545
S3D3 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739
S4D1 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526
S4D2 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366
S4D3 | Demand | ELCBTNXX03 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406
S1D1 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999
S1D2 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685
S1D3 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356
S2D1 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519
S2D2 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239
S2D3 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888
S3D1 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746
S3D2 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004
S3D3 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334
S4D1 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431
S4D2 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165
S4D3 | Demand | ELCINDNO03 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962
S1D1 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288
S1D2 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709
S1D3 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586
S2D1 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484
S2D2 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064
S2D3 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608
S3D1 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159
S3D2 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989
S3D3 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843
S4D1 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319
S4D2 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214
S4D3 | Demand | ELCINDSO03 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738
S1D1 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448
S1D2 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493
S1D3 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355
S2D1 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608
S2D2 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377
S2D3 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643
S3D1 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683
S3D2 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517
S3D3 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176
S4D1 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389
S4D2 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987
S4D3 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351
S1D1 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402
S1D2 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672
S1D3 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999
S2D1 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323
S2D2 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801
S2D3 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569
S3D1 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555
S3D2 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107
S3D3 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052
S4D1 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732
S4D2 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706
S4D3 | Demand | ELCINDWE03 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082
S1D1 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086
S1D2 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095
S1D3 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025
S2D1 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992
S2D2 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163
S2D3 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658
S3D1 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416
S3D2 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696
S3D3 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595
S4D1 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292
S4D2 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078
S4D3 | Demand | ELCINDNE03 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581
S1D1 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918
S1D2 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214
S1D3 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488
S2D1 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068
S2D2 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335
S2D3 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326
S3D1 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379
S3D2 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753
S3D3 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213
S4D1 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377
S4D2 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598
S4D3 | Demand | ELCNPLXX03 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789
S1D1 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317
S1D2 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308
S1D3 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397
S2D1 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457
S2D2 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898
S2D3 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015
S3D1 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649
S3D2 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064
S3D3 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028
S4D1 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725
S4D2 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501
S4D3 | Demand | ELCLKAXX03 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706
S1D1 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256
S1D2 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183
S1D3 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895
S2D1 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715
S2D2 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281
S2D3 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066
S3D1 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387
S3D2 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117
S3D3 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073
S4D1 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159
S4D2 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892
S4D3 | Demand | ELCMDVXX03 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307

## Demand_Techs
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
2 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 1 | CapitalCost | USD/kW | User defined | 0
2 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
2 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 3 | ResidualCapacity | GW | User defined | 0
2 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
2 | PWRTRNBTNXX | Existing internal transmission (non-RE), Bhutan, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
3 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 1 | CapitalCost | USD/kW | User defined | 0
3 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
3 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 3 | ResidualCapacity | GW | User defined | 0
3 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
3 | PWRTRNINDNO | Existing internal transmission (non-RE), India – North, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
4 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 1 | CapitalCost | USD/kW | User defined | 0
4 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
4 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 3 | ResidualCapacity | GW | User defined | 0
4 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
4 | PWRTRNINDSO | Existing internal transmission (non-RE), India – South, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
6 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 1 | CapitalCost | USD/kW | User defined | 0
6 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
6 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 3 | ResidualCapacity | GW | User defined | 0
6 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
6 | PWRTRNINDWE | Existing internal transmission (non-RE), India – West, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
7 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 1 | CapitalCost | USD/kW | User defined | 0
7 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
7 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 3 | ResidualCapacity | GW | User defined | 0
7 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
7 | PWRTRNINDNE | Existing internal transmission (non-RE), India – Northeast, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
8 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 1 | CapitalCost | USD/kW | User defined | 0
8 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
8 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 3 | ResidualCapacity | GW | User defined | 0
8 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
8 | PWRTRNNPLXX | Existing internal transmission (non-RE), Nepal, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
9 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 1 | CapitalCost | USD/kW | User defined | 0
9 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
9 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 3 | ResidualCapacity | GW | User defined | 0
9 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
9 | PWRTRNLKAXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
10 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 1 | CapitalCost | USD/kW | User defined | 0
10 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
10 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 3 | ResidualCapacity | GW | User defined | 0
10 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
10 | PWRTRNMDVXX | Existing internal transmission (non-RE), Maldives, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
12 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 1 | CapitalCost | USD/kW | User defined | 0
12 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
12 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 3 | ResidualCapacity | GW | User defined | 0
12 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
12 | RNWTRNBTNXX | Existing internal transmission (RE), Bhutan, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
13 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 1 | CapitalCost | USD/kW | User defined | 0
13 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
13 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 3 | ResidualCapacity | GW | User defined | 0
13 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
13 | RNWTRNINDNO | Existing internal transmission (RE), India – North, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
14 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 1 | CapitalCost | USD/kW | User defined | 0
14 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
14 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 3 | ResidualCapacity | GW | User defined | 0
14 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
14 | RNWTRNINDSO | Existing internal transmission (RE), India – South, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
16 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 1 | CapitalCost | USD/kW | User defined | 0
16 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
16 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 3 | ResidualCapacity | GW | User defined | 0
16 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
16 | RNWTRNINDWE | Existing internal transmission (RE), India – West, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
17 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 1 | CapitalCost | USD/kW | User defined | 0
17 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
17 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 3 | ResidualCapacity | GW | User defined | 0
17 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
17 | RNWTRNINDNE | Existing internal transmission (RE), India – Northeast, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
18 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 1 | CapitalCost | USD/kW | User defined | 0
18 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
18 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 3 | ResidualCapacity | GW | User defined | 0
18 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
18 | RNWTRNNPLXX | Existing internal transmission (RE), Nepal, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
19 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 1 | CapitalCost | USD/kW | User defined | 0
19 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
19 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 3 | ResidualCapacity | GW | User defined | 0
19 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
19 | RNWTRNLKAXX | Existing internal transmission (RE), Sri Lanka, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
20 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 1 | CapitalCost | USD/kW | User defined | 0
20 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
20 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 3 | ResidualCapacity | GW | User defined | 0
20 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
20 | RNWTRNMDVXX | Existing internal transmission (RE), Maldives, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
22 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 1 | CapitalCost | USD/kW | User defined | 0
22 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
22 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 3 | ResidualCapacity | GW | User defined | 0
22 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
22 | TRNNLIBTNXX | New internal transmission line, Bhutan, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
23 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 1 | CapitalCost | USD/kW | User defined | 0
23 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
23 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 3 | ResidualCapacity | GW | User defined | 0
23 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
23 | TRNNLIINDNO | New internal transmission line, India – North, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
24 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 1 | CapitalCost | USD/kW | User defined | 0
24 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
24 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 3 | ResidualCapacity | GW | User defined | 0
24 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
24 | TRNNLIINDSO | New internal transmission line, India – South, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
26 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 1 | CapitalCost | USD/kW | User defined | 0
26 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
26 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 3 | ResidualCapacity | GW | User defined | 0
26 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
26 | TRNNLIINDWE | New internal transmission line, India – West, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
27 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 1 | CapitalCost | USD/kW | User defined | 0
27 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
27 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 3 | ResidualCapacity | GW | User defined | 0
27 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
27 | TRNNLIINDNE | New internal transmission line, India – Northeast, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
28 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 1 | CapitalCost | USD/kW | User defined | 0
28 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
28 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 3 | ResidualCapacity | GW | User defined | 0
28 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
28 | TRNNLINPLXX | New internal transmission line, Nepal, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
29 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 1 | CapitalCost | USD/kW | User defined | 0
29 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
29 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 3 | ResidualCapacity | GW | User defined | 0
29 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
29 | TRNNLILKAXX | New internal transmission line, Sri Lanka, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
30 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 1 | CapitalCost | USD/kW | User defined | 0
30 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
30 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 3 | ResidualCapacity | GW | User defined | 0
30 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
30 | TRNNLIMDVXX | New internal transmission line, Maldives, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
32 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 1 | CapitalCost | USD/kW | User defined | 0
32 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
32 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 3 | ResidualCapacity | GW | User defined | 0
32 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
32 | TRNRPOBTNXX | Repower/upgrade internal transmission, Bhutan, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
33 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 1 | CapitalCost | USD/kW | User defined | 0
33 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
33 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 3 | ResidualCapacity | GW | User defined | 0
33 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
33 | TRNRPOINDNO | Repower/upgrade internal transmission, India – North, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
34 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 1 | CapitalCost | USD/kW | User defined | 0
34 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
34 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 3 | ResidualCapacity | GW | User defined | 0
34 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
34 | TRNRPOINDSO | Repower/upgrade internal transmission, India – South, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
36 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 1 | CapitalCost | USD/kW | User defined | 0
36 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
36 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 3 | ResidualCapacity | GW | User defined | 0
36 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
36 | TRNRPOINDWE | Repower/upgrade internal transmission, India – West, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
37 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 1 | CapitalCost | USD/kW | User defined | 0
37 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
37 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 3 | ResidualCapacity | GW | User defined | 0
37 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
37 | TRNRPOINDNE | Repower/upgrade internal transmission, India – Northeast, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
38 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 1 | CapitalCost | USD/kW | User defined | 0
38 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
38 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 3 | ResidualCapacity | GW | User defined | 0
38 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
38 | TRNRPONPLXX | Repower/upgrade internal transmission, Nepal, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
39 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 1 | CapitalCost | USD/kW | User defined | 0
39 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
39 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 3 | ResidualCapacity | GW | User defined | 0
39 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
39 | TRNRPOLKAXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
40 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 1 | CapitalCost | USD/kW | User defined | 0
40 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
40 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 3 | ResidualCapacity | GW | User defined | 0
40 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
40 | TRNRPOMDVXX | Repower/upgrade internal transmission, Maldives, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0

## Emissions
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
2 | PWRCOAINDNO | Coal-fired Power, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300
3 | PWRCOAINDSO | Coal-fired Power, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300
4 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300
5 | PWRCOAINDWE | Coal-fired Power, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300
6 | PWRCOALKAXX | Coal – Supercritical, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
7 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
8 | PWRNGSINDNO | Gas-fired Power, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
9 | PWRNGSINDSO | Gas-fired Power, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
10 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
11 | PWRNGSINDWE | Gas-fired Power, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
12 | PWRNGSINDNE | Gas-fired Power, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
13 | PWRNGSMDVXX | Gas-fired Power, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
14 | PWRNGSLKAXX | Gas-fired Power, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
15 | PWROILMDVXX | Oil/Diesel generation, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300
16 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300
17 | PWROILLKAXX | Oil/Diesel generation, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300
18 | PWRWASINDNO | Waste-to-Energy, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
19 | PWRWASINDSO | Waste-to-Energy, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
20 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
21 | PWRWASINDWE | Waste-to-Energy, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
22 | PWRWASINDNE | Waste-to-Energy, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
23 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
24 | PWRWASLKAXX | Waste-to-Energy, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000

## Yearsplit_Template
Timeslices | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
S1D1 | 14 | YearSplit | fraction | User defined | 0 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556
S1D2 | 14 | YearSplit | fraction | User defined | 0 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389
S1D3 | 14 | YearSplit | fraction | User defined | 0 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722
S2D1 | 14 | YearSplit | fraction | User defined | 0 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111
S2D2 | 14 | YearSplit | fraction | User defined | 0 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278
S2D3 | 14 | YearSplit | fraction | User defined | 0 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444
S3D1 | 14 | YearSplit | fraction | User defined | 0 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556
S3D2 | 14 | YearSplit | fraction | User defined | 0 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389
S3D3 | 14 | YearSplit | fraction | User defined | 0 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722
S4D1 | 14 | YearSplit | fraction | User defined | 0 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111
S4D2 | 14 | YearSplit | fraction | User defined | 0 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278
S4D3 | 14 | YearSplit | fraction | User defined | 0 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444
Note on G2: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G3: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G4: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G5: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G6: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G7: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G8: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G9: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G10: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G11: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G12: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G13: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.

## DaySplit
DAILYTIMEBRACKET | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | 12 | DaySplit | fraction | User defined | 0 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913
2 | 12 | DaySplit | fraction | User defined | 0 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256
3 | 12 | DaySplit | fraction | User defined | 0 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571

## Interconnectors
NO | Project | From_Node | To_Node | Circuits | COD_Date | Affiliated_Power | Capacity_MW | Voltage_kV | DC_AC | Directionality | Status | Export_Resource_Type | Source
1 | Chukha → Birpara 220 kV D/C | BT | IN_E | 2 | 1988 | Chukha Hydro | 336 | 220 kV | AC | Uni‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
2 | Chukha → Birpara via Singhigaon 220 kV S/C | BT | IN_E | 1 | 1988 | Chukha Hydro | 336 | 220 kV | AC | Uni‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
3 | Kurichhu → Gelephu → Salakati 132 kV S/C | BT | IN_NE | 1 | 2010 | Kurichhu | 60 | 132 kV | AC | Uni‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
4 | Tala → Siliguri 400 kV 2×D/C | BT | IN_E | 2 | 2006 | Tala | 1020 | 400 kV | AC | Uni‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
5 | Jigmeling → Alipurduar 400 kV D/C (Quad) | BT | IN_E | 1 | 2019 | Punatsangchhu‑I &2,Mangdechhu | 3000 | 400 kV | AC | Bi‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
6 | Bheramara back‑to‑back HVDC (India → Bangladesh) | IN_E | BD | 1 | 2013 | Grid-to-Grid | 1000 | ±400 kV | DC | Bi‑directional | Operational | Fossil / mixed | Zixuan v3 (Sheet 1)
7 | Surajmaninagar- Comilla | IN_NE | BD | 1 | 2013 | Grid-to-Grid | 160 | 132 kV | AC | Bi-directional | Operational | Mixed | Zixuan v3 (Sheet 1)
8 | Bornagar-Parbotipur | IN_NE | BD | 1 | 2028 | Grid-to-Grid | 1000 | 765kV | DC | Bi-directional | Planned | Mixed | Zixuan v3 (Sheet 1)
9 | Muzaffarpur → Dhalkebar 400 kV D/C | IN_E | NP | 2 | 2016 | Grid-to-Grid | 1000 | 400 kV | AC | Bi‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
10 | Raxaul (India) – Parwanipur (Nepal) | IN_N | NP | 2 | 2018 | Grid-to-Grid | 150 | 132kV | AC | Bi-directional | Operational | Mixed | Zixuan v3 (Sheet 1)
11 | Kataiya (India) – Kusaha (Nepal) | IN_E | NP | 2 | 2018 | Grid-to-Grid | 150 | 132kV | AC | Bi-directional | Operational | Mixed | Zixuan v3 (Sheet 1)
12 | Kushinagar (India) – Bhairahawa (Nepal) | IN_N | NP | 1 | 2018 | Grid-to-Grid | 100 | 132kV | AC | Bi-directional | Operational | Mixed | Zixuan v3 (Sheet 1)
13 | Tanakpur (India) – Mahendranagar (Nepal) | IN_N | NP | 1 | 2018 | Grid-to-Grid | 100 | 132kV | AC | Bi-directional | Operational | Mixed | Zixuan v3 (Sheet 1)
14 | Jogbani (India) – Biratnagar (Nepal) | IN_E | NP | 1 | 2018 | Grid-to-Grid | 50 | 132kV | AC | Bi-directional | Operational | Mixed | Zixuan v3 (Sheet 1)
15 | Mainahiya (India) – Sampatiya (Nepal) | IN_N | NP | 1 | 2019 | Grid-to-Grid | 150 | 132kV | AC | Bi-directional | Operational | Mixed | Zixuan v3 (Sheet 1)
16 | New Butwal (Nepal) – Gorakhpur (India) | NP | IN_N | 2 | 2025 | Grid-to-Grid | 1000 | 400 kV | AC | Bi‑directional | Under Construction | Hydro | Zixuan v3 (Sheet 1)
17 | Inaruwa (Duhabi) → Purnia 400 kV | NP | IN_E | 1 | 2027 | Grid-to-Grid | 1000 | 400 kV | AC | Bi‑directional | Planned | Hydro | Zixuan v3 (Sheet 1)
18 | Dodhara (Lamki) → Bareli 400 kV | NP | IN_N | 1 | 2028 | Grid-to-Grid | 1000 | 400 kV | AC | Bi‑directional | Planned | Hydro | Zixuan v3 (Sheet 1)
19 | India → Sri Lanka HVDC interconnector (Madurai ↔ Mannar / Anuradhapura) | IN_S | LK | 1 | 2039 | Grid-to-Grid | 500 | ±500 kV | DC | Bi‑directional | Proposed / Planning | Mixed (hydro / renewables / fossil) | Zixuan v3 (Sheet 1)
20 | Anarmani (Nepal) – Kishanganj (India) | NP | IN_E | 1 |  | Grid-to-Grid | 1000 | 400 | AC | Bi-directional | Proposed | Mixed | https://kathmandupost.com/national/2024/01/08/nepal-and-india-to-explore-potential-of-more-high-capacity-electricity-transmission-lines?utm_source=chatgpt.com
21 | Lamahi (Dang)-Lucknow (Uttar Pradesh) | NP | IN_N | 1 |  | Grid-to-Grid | 1000 | 400 | AC | Bi-directional | Proposed | Mixed | Zixuan v3
22 | Nijgadh (Bara)-Motihari (Bihar) | NP | IN_E | 1 |  | Grid-to-Grid | 1000 | 400 | AC | Bi-directional | Proposed | Mixed | Zixuan v3
23 | Katihar- Parbatipur | IN_E | BD | 1 | 2028 | Grid-to-Grid | 2000 | 765 | DC | Bi-directional | Proposed | Mixed | https://cpd-power-energy-study.com/bangladesh-india-review-progress-of-katihar-parbatipur-baranagar-765kv-transmission-line/?utm_source=chatgpt.com
24 | Parbatipur-Boronagar | BD | IN_E | 1 | 2028 | Grid-to-Grid | 2000 | 765 | DC | Bi-directional | Proposed | Mixed | Zixuan v3
25 | Adani Company explore 5GW to India | BT | IN_E | 1 |  | Grid-to-Grid | 5000 |  | AC | Bi-directional | Proposed | Mixed | Zixuan v3
26 | Adani Power Godda HVDC (India → Bangladesh) | IN_E | BD | 1 | 2023 | Godda Coal Plant | 1496 | 400 kV | HVDC | Uni-directional | Operational | Fossil | Bangladesh_Power_Sector.xlsx
27 | Nepal Hydro Import Trial (via India) | NP | BD | 1 | 2025 | Grid-to-Grid | 40 | HVDC | DC | Uni-directional | Trial/Partial | Hydro | Bangladesh_Power_Sector.xlsx
28 | Barapukuria HVDC B2B Station | IN_E | BD | 1 | 2030 | Grid-to-Grid | 750 | 400 kV | HVDC B2B | Bi-directional | Planned | Mixed | IEPMP 2023
29 | Cumilla HVDC B2B Station (expansion) | IN_NE | BD | 1 | 2032 | Grid-to-Grid | 750 | 400 kV | HVDC B2B | Bi-directional | Planned | Mixed | IEPMP 2023
30 | Jamalpur HVDC B2B Station | IN_E | BD | 1 | 2033 | Grid-to-Grid | 750 | 400 kV | HVDC B2B | Bi-directional | Proposed | Mixed | IEPMP 2023
31 | Sylhet HVDC B2B Station | IN_NE | BD | 1 | 2035 | Grid-to-Grid | 750 | 400 kV | HVDC B2B | Bi-directional | Proposed | Mixed | IEPMP 2023
32 | Second Bheramara HVDC Expansion | IN_E | BD | 1 | 2029 | Grid-to-Grid | 500 | 400 kV | HVDC B2B | Bi-directional | Proposed | Mixed | PGCB / IEPMP 2023
33 | Nepal Hydro Import – Dedicated Line | NP | BD | 1 | 2033 | Hydro | 1000 | 400 kV / 765 kV | AC/HVDC | Uni-directional | Under Study | Hydro | IEPMP 2023
34 | Bhutan Hydro Import – Dedicated Line | BT | BD | 1 | 2035 | Hydro | 750 | 400 kV | AC | Uni-directional | Under Study | Hydro | IEPMP 2023
35 | Punatsangchhu-I → Alipurduar 400 kV D/C | BT | IN_E | 2 | 2020 | Punatsangchhu-I HP | 1200 | 400 kV | AC | Uni-directional | Operational | Hydro | BPC PDB 2024
36 | Punatsangchhu-II → Alipurduar 400 kV D/C | BT | IN_E | 2 | 2024 | Punatsangchhu-II HP | 1200 | 400 kV | AC | Uni-directional | Operational | Hydro | BPC PDB 2024
37 | Samtse → Singhigaon 220 kV D/C | BT | IN_E | 1 | 2022 | Grid-to-Grid | 100 | 220 kV | AC | Bi-directional | Operational | Mixed | BPC PDB 2024
38 | Deothang → Motanga 132 kV S/C (India Border) | BT | IN_NE | 1 | 2010 | Kurichhu | 60 | 132 kV | AC | Uni-directional | Operational | Hydro | BPC PDB 2024
39 | Gelephu → Salakati 132 kV S/C | BT | IN_NE | 1 | 2010 | Grid-to-Grid | 50 | 132 kV | AC | Bi-directional | Operational | Mixed | BPC PDB 2024
40 | Kholongchhu HP Export Line 400 kV | BT | IN_NE | 2 | 2027 | Kholongchhu HP | 600 | 400 kV | AC | Uni-directional | Under Study | Hydro | NTGMP 2018
41 | Bunakha Reservoir Export Line 400 kV | BT | IN_E | 2 | 2030 | Bunakha HP | 2400 | 400 kV | AC | Uni-directional | Proposed | Hydro | BPSMP 2040
42 | Dorjilung HP Export Line 400 kV | BT | IN_NE | 2 | 2030 | Dorjilung HP | 1125 | 400 kV | AC | Uni-directional | Proposed | Hydro | BPSMP 2040
43 | Chamkharchhu HP Export Line 400 kV | BT | IN_E | 2 | 2028 | Chamkharchhu HP | 670 | 400 kV | AC | Uni-directional | Under Study | Hydro | BPSMP 2040
44 | Gelephu Mindfulness City Interconnection | BT | IN_NE | 1 | 2029 | Grid-to-Grid | 500 | 220/400 kV | AC | Bi-directional | Under Planning | Mixed | BPSMP 2040
45 | Nepalgunj → Nanpara 132 kV Cross-Border | NP | IN_N | 1 | 2026 | Grid-to-Grid | 150 | 132 kV | AC | Bi-directional | Under Construction | Mixed | NEA Annual 2024/25
46 | Dhalkebar → Loharpatti 132 kV Expansion | NP | IN_E | 1 | 2025 | Grid-to-Grid | 150 | 132 kV | AC | Bi-directional | Operational/Expansion | Mixed | NEA Annual 2024/25
47 | India–Sri Lanka HVDC Phase 2 (expansion) | IN_S | LK | 1 | 2040 | Grid-to-Grid | 500 | ±320 kV | HVDC VSC | Bi-directional | Conceptual | Mixed | LTGEP 2025-2044
48 | Raipur–Pugalur 2nd HVDC ±800kV | IN_E | IN_S | 1 | 2029 | Bulk Transfer | 6000 | ±800 kV | HVDC | Bi-directional | Planning | Mixed | NEP Vol.II
49 | Khargone–Pune 765kV | IN_W | IN_S | 2 | 2028 | WR-SR strengthening | 5000 | 765 kV | AC | Bi-directional | DPR Stage | Mixed | NEP Vol.II
50 | Sipat–Ranchi 765kV | IN_E | IN_N | 2 | 2029 | ER-NR strengthening | 3000 | 765 kV | AC | Bi-directional | Planning | Mixed | NEP Vol.II
51 | Bongaigaon–Siliguri 400kV NER Strengthening | IN_NE | IN_E | 2 | 2027 | NER-ER strengthening | 2000 | 400 kV | AC | Bi-directional | Under Construction | Mixed | NEP Vol.II / PGCIL

## Interconnector_Params
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 1 | CapitalCost | USD/kW | User defined | 0 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 2 | FixedCost | USD/kW/yr | User defined | 0 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 3 | ResidualCapacity | GW | User defined | 0 | 2.496 | 2.496 | 2.496 | 2.496 | 2.496 | 2.496 | 2.996 | 3.746 | 3.746 | 3.746 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496
1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
2 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 1 | CapitalCost | USD/kW | User defined | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
2 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
2 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 3 | ResidualCapacity | GW | User defined | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 1.16 | 1.16 | 1.16 | 1.16 | 1.91 | 1.91 | 1.91 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66
2 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
2 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
2 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
2 | TRNBGDXXINDNE | Cross-border interconnector: Bangladesh ↔ India Northeast | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
3 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 1 | CapitalCost | USD/kW | User defined | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
3 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 2 | FixedCost | USD/kW/yr | User defined | 0 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
3 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 3 | ResidualCapacity | GW | User defined | 0 | 5.992 | 7.192 | 7.192 | 7.192 | 7.192 | 7.862 | 7.862 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262 | 10.262
3 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
3 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 13 | CapacityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
3 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025
3 | TRNBTNXXINDEA | Cross-border interconnector: Bhutan ↔ India East | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
4 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 1 | CapitalCost | USD/kW | User defined | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
4 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
4 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 3 | ResidualCapacity | GW | User defined | 0 | 0.17 | 0.17 | 0.17 | 0.17 | 0.77 | 0.77 | 1.27 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395 | 2.395
4 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
4 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
4 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
4 | TRNBTNXXINDNE | Cross-border interconnector: Bhutan ↔ India Northeast | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
5 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 1 | CapitalCost | USD/kW | User defined | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 2 | FixedCost | USD/kW/yr | User defined | 0 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
5 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 3 | ResidualCapacity | GW | User defined | 0 | 0.5 | 0.5 | 1.5 | 1.65 | 1.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65
5 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
5 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
5 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
5 | TRNINDNONPLXX | Cross-border interconnector: Nepal ↔ India North | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
6 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 1 | CapitalCost | USD/kW | User defined | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
6 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 2 | FixedCost | USD/kW/yr | User defined | 0 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
6 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 3 | ResidualCapacity | GW | User defined | 0 | 1.2 | 1.2 | 1.35 | 1.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35
6 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
6 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
6 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
6 | TRNINDEANPLXX | Cross-border interconnector: Nepal ↔ India East | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
7 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 1 | CapitalCost | USD/kW | User defined | 0 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031
7 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 2 | FixedCost | USD/kW/yr | User defined | 0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
7 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
7 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
7 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
7 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
7 | TRNINDSOLKAXX | Cross-border interconnector: Sri Lanka ↔ India South | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
8 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
8 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
8 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 3 | ResidualCapacity | GW | User defined | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
8 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
8 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 13 | CapacityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
8 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
8 | TRNINDEAINDNO | Cross-border interconnector: India North ↔ India East (internal) | 2 | OperationalLife | years | User defined | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
9 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
9 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
9 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 3 | ResidualCapacity | GW | User defined | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
9 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
9 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 13 | CapacityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
9 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025
9 | TRNINDNOINDWE | Cross-border interconnector: India North ↔ India West (internal) | 2 | OperationalLife | years | User defined | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
10 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
10 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
10 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 3 | ResidualCapacity | GW | User defined | 0 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
10 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
10 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
10 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
10 | TRNINDEAINDNE | Cross-border interconnector: India East ↔ India Northeast (internal) | 2 | OperationalLife | years | User defined | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
11 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550
11 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
11 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 3 | ResidualCapacity | GW | User defined | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
11 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
11 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 13 | CapacityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
11 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
11 | TRNINDEAINDSO | Cross-border interconnector: India East ↔ India South (internal) | 2 | OperationalLife | years | User defined | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
12 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
12 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
12 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 3 | ResidualCapacity | GW | User defined | 0 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
12 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
12 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 13 | CapacityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
12 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025
12 | TRNINDSOINDWE | Cross-border interconnector: India West ↔ India South (internal) | 2 | OperationalLife | years | User defined | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
13 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600
13 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
13 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
13 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
13 | TRNMDVXXINDSO | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 2 | OperationalLife | years | User defined | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
14 | TRNNPLXXBGDXX | Cross-border interconnector: Nepal ↔ Bangladesh | 1 | CapitalCost | USD/kW | User defined | 0 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
14 | TRNNPLXXBGDXX | Cross-border interconnector: Nepal ↔ Bangladesh | 2 | FixedCost | USD/kW/yr | User defined | 0 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
14 | TRNNPLXXBGDXX | Cross-border interconnector: Nepal ↔ Bangladesh | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04
14 | TRNNPLXXBGDXX | Cross-border interconnector: Nepal ↔ Bangladesh | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
14 | TRNNPLXXBGDXX | Cross-border interconnector: Nepal ↔ Bangladesh | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
14 | TRNNPLXXBGDXX | Cross-border interconnector: Nepal ↔ Bangladesh | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
15 | TRNBTNXXBGDXX | Cross-border interconnector: Bhutan ↔ Bangladesh | 1 | CapitalCost | USD/kW | User defined | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
15 | TRNBTNXXBGDXX | Cross-border interconnector: Bhutan ↔ Bangladesh | 2 | FixedCost | USD/kW/yr | User defined | 0 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
15 | TRNBTNXXBGDXX | Cross-border interconnector: Bhutan ↔ Bangladesh | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
15 | TRNBTNXXBGDXX | Cross-border interconnector: Bhutan ↔ Bangladesh | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
15 | TRNBTNXXBGDXX | Cross-border interconnector: Bhutan ↔ Bangladesh | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
15 | TRNBTNXXBGDXX | Cross-border interconnector: Bhutan ↔ Bangladesh | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40

## Existing_Generation
Country | Node | Plant_Name | Technology_Code | Technology_Name | Fuel | Capacity_MW | Commissioning_Year | Expected_Retirement_Year | Capacity_Factor_Annual | Status | Source
Bangladesh | BD | Ghorasal Repowered CCPP Unit-3 (GT) | PWRNGSBGDXX | Natural Gas CC | Gas | 260 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ghorasal Repowered CCPP Unit-4 | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ghorasal TPP Unit-5 | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ghorasal 365 MW CCPP Unit-7 | PWRNGSBGDXX | Natural Gas CC | Gas | 365 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ghorashal 108MW PP (Regent) | PWRNGSBGDXX | Natural Gas CC | Gas | 108 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Tongi 80 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 105 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat 450 MW CCPP (MPL) | PWRNGSBGDXX | Natural Gas CC | Gas | 450 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | 210 MW Siddhirgonj TPP | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Haripur 412 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 412 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Siddhirgonj 2x120 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Siddhirganj 335 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 335 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat 335MW CCPP (Summit) | PWRNGSBGDXX | Natural Gas CC | Gas | 335 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Madanganj-55 MW PP (Summit) | PWROILBGDXX | HFO Engine | HFO | 55 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Gagnagar 102 MW PP (Digital Power) | PWROILBGDXX | HFO Engine | HFO | 102 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Summit Power Ashulia | PWRNGSBGDXX | Natural Gas CC | Gas | 45 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Summit Power Madhabdi | PWRNGSBGDXX | Natural Gas CC | Gas | 35 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Gazipur 52 MW PP | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Gazipur 100 MW PP | PWROILBGDXX | HFO Engine | HFO | 105 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kodda 150MW PP (BR-Power gen) | PWROILBGDXX | HFO Engine | HFO | 149 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kamalaghat 54 MW PP (Banco Energy) | PWROILBGDXX | HFO Engine | HFO | 54 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kodda 300 MW PP Unit-2 (Summit) | PWROILBGDXX | HFO Engine | HFO | 300 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kodda 149 MW PP Unit-1 (Summit) | PWROILBGDXX | HFO Engine | HFO | 149 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Nababganj 55 MW PP (Southern Power) | PWROILBGDXX | HFO Engine | HFO | 55 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Manikganj 55 MW PP (Northern) | PWROILBGDXX | HFO Engine | HFO | 55 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat 104 MW PP (OPSL) | PWROILBGDXX | HFO Engine | HFO | 104 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Manikgonj 162MW PP (MPGL) | PWROILBGDXX | HFO Engine | HFO | 162 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Manikgonj 35MW Solar PP (Inspectra Solar) | PWRSPVBGDXX | Solar PV | Solar | 35 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kanchan Purbachal Power Generation | PWROILBGDXX | HFO Engine | HFO | 55 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Unique Meghnaghat 584MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 584 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat 583 MW CCPP (Summit) | PWRNGSBGDXX | Natural Gas CC | Gas | 583 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat (Jera) 718MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 718 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sripur 150 MW (BR-Power gen) | PWROILBGDXX | HFO Engine | HFO | 150 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Karnaphuli Hydro PP Unit-1,2,3,4,5 | PWRHYDBGDXX | Hydro | Hydro | 230 | 2010 | 2060 | 0.45 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chattogram TPP | PWRNGSBGDXX | Natural Gas CC | Gas | 420 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kaptai 7 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 6 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Raozan 25 MW PP | PWROILBGDXX | HFO Engine | HFO | 25 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Teknaf 20MW PP (Solartech) | PWRSPVBGDXX | Solar PV | Solar | 20 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Patenga 50MW PP (Baraka) | PWROILBGDXX | HFO Engine | HFO | 50 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sikalbaha 105 MW PP (Baraka Sikalbaha) | PWROILBGDXX | HFO Engine | HFO | 105 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shikalbaha Peaking GT | PWRNGSBGDXX | Natural Gas CC | Gas | 150 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sikalbaha 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 225 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Anwara 300 MW PP (United) | PWROILBGDXX | HFO Engine | HFO | 300 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Juldah 100 MW PP Unit-3 (Acorn) | PWROILBGDXX | HFO Engine | HFO | 100 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Dohazari-Kalaish 100 MW Peaking | PWROILBGDXX | HFO Engine | HFO | 102 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Hathazari 100 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 98 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chattogram 108 MW PP (ECPV) | PWROILBGDXX | HFO Engine | HFO | 108 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sikalbaha 54 MW PP (Jodiac Power) | PWROILBGDXX | HFO Engine | HFO | 54 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Karnaphuli Power Ltd. | PWROILBGDXX | HFO Engine | HFO | 110 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Juldah Unit-2 (Acorn) | PWROILBGDXX | HFO Engine | HFO | 100 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chattogram 116 MW PP (Anlima Energy) | PWROILBGDXX | HFO Engine | HFO | 116 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Mirsharai 150 MW (BR-Power gen) | PWROILBGDXX | HFO Engine | HFO | 163 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | SS Power 2x612MW Coal PP | PWRCOABGDXX | Coal Steam | Coal | 1224 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Matarbari 2x600 MW (CPGCL) | PWRCOABGDXX | Coal Steam | Coal | 1150 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Cox's Bazar Wind PP | PWRWONBGDXX | Wind | Wind | 60 | 2010 | 2035 | 0.25 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 50 MW PP | PWRNGSBGDXX | Natural Gas CC | Gas | 53 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 221 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 450 MW CCPP (South) | PWRNGSBGDXX | Natural Gas CC | Gas | 360 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 450 MW CCPP (North) | PWRNGSBGDXX | Natural Gas CC | Gas | 360 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 420 MW CCPP (East) | PWRNGSBGDXX | Natural Gas CC | Gas | 400 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 195MW PP (APSCL-United) | PWRNGSBGDXX | Natural Gas CC | Gas | 195 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 51 MW PP (Midland) | PWRNGSBGDXX | Natural Gas CC | Gas | 51 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 150MW PP (Midland) | PWROILBGDXX | HFO Engine | HFO | 150 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Titas 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chandpur 150 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 163 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chandpur 200MW (Desh Energy) | PWROILBGDXX | HFO Engine | HFO | 200 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Jangalia 52 MW PP (Lakdanavi) | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Cumilla 25 MW PP (Summit) | PWRNGSBGDXX | Natural Gas CC | Gas | 25 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Feni 114 MW (Lakdanavi) | PWROILBGDXX | HFO Engine | HFO | 114 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chowmuhani 113 MW | PWROILBGDXX | HFO Engine | HFO | 113 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chandpur 115MW PP (Doreen) | PWROILBGDXX | HFO Engine | HFO | 115 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 55 MW PP (Precision) | PWRNGSBGDXX | Natural Gas CC | Gas | 55 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sonagazi 75 MW Solar Plant (EGCB) | PWRSPVBGDXX | Solar PV | Solar | 75 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | RPCL 210MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Jamalpur 115 MW PP (United) | PWROILBGDXX | HFO Engine | HFO | 115 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Mymensingh 200 MW PP (United) | PWROILBGDXX | HFO Engine | HFO | 200 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sarishabari 3 MW Solar Plant | PWRSPVBGDXX | Solar PV | Solar | 3 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sutiakhali 50 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 50 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bhairob 54 MW PP | PWROILBGDXX | HFO Engine | HFO | 54 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Tangail 22 MW PP (PPGL) | PWROILBGDXX | HFO Engine | HFO | 22 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Fenchugonj CCPP Phase-1 | PWRNGSBGDXX | Natural Gas CC | Gas | 97 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Fenchugonj CCPP Phase-2 | PWRNGSBGDXX | Natural Gas CC | Gas | 104 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kushiara 163 MW CCPP (KP) | PWRNGSBGDXX | Natural Gas CC | Gas | 163 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shahjibazar GTPP Unit-8 & 9 | PWRNGSBGDXX | Natural Gas CC | Gas | 70 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shajibazar 330 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 330 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sylhet 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 231 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sylhet 20 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 20 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shahjahanulla 25 MW PP | PWRNGSBGDXX | Natural Gas CC | Gas | 25 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bibiana-II 341 MW CCPP (Summit) | PWRNGSBGDXX | Natural Gas CC | Gas | 341 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bibiyana-III 400 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 400 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bibiyana South 383 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 383 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shahjibazar 100 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 100 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shahjibazar 86MW PP (Shahjibazar) | PWRNGSBGDXX | Natural Gas CC | Gas | 86 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bheramara 410 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 410 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Faridpur 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 54 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Gopalganj 100 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 109 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Khulna 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | HSD/Gas | 230 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rupsha 105 MW PP (Orion rupsha) | PWROILBGDXX | HFO Engine | HFO | 105 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Madhumati 100 MW PP | PWROILBGDXX | HFO Engine | HFO | 105 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Mongla Orion 100 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 100 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Maitree Super Thermal 1320 MW PP (BIFPCL) | PWRCOABGDXX | Coal Steam | Coal | 1234 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Khulna 330 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas/HSD | 336 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barisal 110 MW PP (Summit) | PWROILBGDXX | HFO Engine | HFO | 110 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bhola 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 194 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Payra 1320 MW TPP (BCPCL) | PWRCOABGDXX | Coal Steam | Coal | 1244 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Potuakhali 150MW PP (UPPL) | PWROILBGDXX | HFO Engine | HFO | 150 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barisal Electric 307 MW Coal | PWRCOABGDXX | Coal Steam | Coal | 307 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barisal 1 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 1 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bhola 220MW CCPP (Nutan Bidyut BD) | PWRNGSBGDXX | Natural Gas CC | Gas/HSD | 220 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Baghabari 71 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 71 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Baghabari 100 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 100 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Baghabari 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bera 70 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 71 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chapainawabganj 100 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 104 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Katakhali 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 50 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Santahar 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 50 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 225MW CCPP Unit-1 | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 225MW CCPP Unit-2 | PWRNGSBGDXX | Natural Gas CC | Gas | 220 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 225MW CCPP Unit-3 | PWRNGSBGDXX | Natural Gas CC | Gas | 220 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 400 MW CCPP Unit-4 | PWRNGSBGDXX | Natural Gas CC | Gas | 414 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Natore 52 MW PP (Rajlanka) | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bagura 113 MW PP (Confidence) U-1 | PWROILBGDXX | HFO Engine | HFO | 113 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bagura 113 MW PP (Confidence) U-2 | PWROILBGDXX | HFO Engine | HFO | 113 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 6.55 MW Solar | PWRSPVBGDXX | Solar PV | Solar | 6 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajganj 68 MW Solar Park | PWRSPVBGDXX | Solar PV | Solar | 68 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Pabna Solar 100 MW | PWRSPVBGDXX | Solar PV | Solar | 100 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 2 MW Wind Power Plant | PWRWONBGDXX | Wind | Wind | 2 | 2010 | 2035 | 0.25 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Pabna 64 MW Solar Plant | PWRSPVBGDXX | Solar PV | Solar | 65 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barapukuria TPP Unit-1 & 2 | PWRCOABGDXX | Coal Steam | Coal | 250 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barapukuria 275 MW TPP Unit-3 | PWRCOABGDXX | Coal Steam | Coal | 274 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rangpur 20 MW GTPP | PWROILBGDXX | High Speed Diesel | HSD | 20 | 2010 | 2045 | 0.2 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rangpur 113 MW PP (Confidence) | PWROILBGDXX | HFO Engine | HFO | 113 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Saidpur 20 MW GTPP | PWROILBGDXX | High Speed Diesel | HSD | 20 | 2010 | 2045 | 0.2 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Majipara Tatulia 8 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 8 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Thakurgaon 115MW PP (Energypac) | PWROILBGDXX | HFO Engine | HFO | 115 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Lalmonirhat 30 MW Solar (Intraco) | PWRSPVBGDXX | Solar PV | Solar | 30 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Teesta Solar Limited 200 MW | PWRSPVBGDXX | Solar PV | Solar | 200 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Saidpur 150 MW Simple Cycle PP | PWROILBGDXX | High Speed Diesel | HSD | 162 | 2010 | 2045 | 0.2 | Operational | Bangladesh_Power_Sector.xlsx
Bhutan | BT | Tala Hydropower Plant | PWRHYDBTNXX | Hydro | Hydro | 1020 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Mangdechhu Hydropower Plant | PWRHYDBTNXX | Hydro | Hydro | 720 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Chhukha Hydropower Plant | PWRHYDBTNXX | Hydro | Hydro | 336 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Dagachhu Hydropower Plant | PWRHYDBTNXX | Hydro | Hydro | 252 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Nikachhu Hydropower Plant | PWRHYDBTNXX | Hydro | Hydro | 118 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Kurichhu Hydropower Plant | PWRHYDBTNXX | Hydro | Hydro | 60 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Basochhu Hydropower Plant | PWRHYDBTNXX | Hydro | Hydro | 64 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Punatsangchhu-II Hydropower Plant (PHP-II) | PWRHYDBTNXX | Hydro | Hydro | 1020 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Mini/Micro Hydel Plants (various) | PWRHYDBTNXX | Hydro | Hydro | 4 | 2005 | 2060 | 0.45 | Operational | Bhutan_Power_Infrastructure.xlsx ¦ Capacity estimated: 16.90 MU (2024) ÷ (8760h × CF≈0.45) ≈ 4 MW
Bhutan | BT | DSP Solar Plant | PWRSPVBTNXX | Solar PV | Solar | 2 | 2005 | 2030 | 0.18 | Operational | Bhutan_Power_Infrastructure.xlsx ¦ Capacity estimated: 3.23 MU (2024) ÷ (8760h × CF≈0.18) ≈ 2 MW
Nepal | NP | Kaligandaki 'A' (KGA) | PWRHYDNPLXX | Hydro | Hydro | 144 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Middle Marsyangdi (MMHPS) | PWRHYDNPLXX | Hydro | Hydro | 70 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Marsyangdi (MHPS) | PWRHYDNPLXX | Hydro | Hydro | 69 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Kulekhani I | PWRHYDNPLXX | Hydro | Hydro | 60 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Trishuli 3A HEP | PWRHYDNPLXX | Hydro | Hydro | 60 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Kulekhani II | PWRHYDNPLXX | Hydro | Hydro | 32 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Chameliya | PWRHYDNPLXX | Hydro | Hydro | 30 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Trishuli | PWRHYDNPLXX | Hydro | Hydro | 24 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Gandak | PWRHYDNPLXX | Hydro | Hydro | 15 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Devighat | PWRHYDNPLXX | Hydro | Hydro | 14.1 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Modikhola | PWRHYDNPLXX | Hydro | Hydro | 14.8 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Kulekhani III HEP | PWRHYDNPLXX | Hydro | Hydro | 14 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Sunkoshi | PWRHYDNPLXX | Hydro | Hydro | 10.05 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Puwa Khola (Ilam) | PWRHYDNPLXX | Hydro | Hydro | 6.2 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Chatara | PWRHYDNPLXX | Hydro | Hydro | 3.2 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Panauti | PWRHYDNPLXX | Hydro | Hydro | 2.4 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tatopani | PWRHYDNPLXX | Hydro | Hydro | 2 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Seti (Pokhara) | PWRHYDNPLXX | Hydro | Hydro | 1.5 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tinau | PWRHYDNPLXX | Hydro | Hydro | 1.024 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Fewa | PWRHYDNPLXX | Hydro | Hydro | 1 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Sundarijal | PWRHYDNPLXX | Hydro | Hydro | 0.97 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Pharping | PWRHYDNPLXX | Hydro | Hydro | 0.5 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Gamgad | PWRHYDNPLXX | Hydro | Hydro | 0.4 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khandbari | PWRHYDNPLXX | Hydro | Hydro | 0.25 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Jomsom | PWRHYDNPLXX | Hydro | Hydro | 0.24 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Phidim | PWRHYDNPLXX | Hydro | Hydro | 0.24 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Baglung | PWRHYDNPLXX | Hydro | Hydro | 0.2 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Surnaiyagad | PWRHYDNPLXX | Hydro | Hydro | 0.2 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Doti | PWRHYDNPLXX | Hydro | Hydro | 0.2 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Ramechhap | PWRHYDNPLXX | Hydro | Hydro | 0.15 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Terhathum | PWRHYDNPLXX | Hydro | Hydro | 0.1 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Multifuel Power Plant (Duhabi) | PWRNGSNPLXX | Multi-fuel Thermal | Thermal (Multi-fuel) | 39 | 2008 | 2043 | 0.5 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Hetauda Diesel Power Plant | PWROILNPLXX | Diesel | Thermal (Diesel) | 14.41 | 2008 | 2043 | 0.25 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Chilime HEP | PWRHYDNPLXX | Hydro | Hydro | 22.1 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Tamakoshi HEP | PWRHYDNPLXX | Hydro | Hydro | 456 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Sanjen HEP | PWRHYDNPLXX | Hydro | Hydro | 14.8 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Sanjen HEP | PWRHYDNPLXX | Hydro | Hydro | 42.5 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rasuwagadhi HEP | PWRHYDNPLXX | Hydro | Hydro | 111 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khimti Khola HEP | PWRHYDNPLXX | Hydro | Hydro | 60 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Bhotekoshi HEP | PWRHYDNPLXX | Hydro | Hydro | 45 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Indrawati III HEP | PWRHYDNPLXX | Hydro | Hydro | 7.5 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Jhimruk Khola HEP | PWRHYDNPLXX | Hydro | Hydro | 12 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Andhi Khola HEP | PWRHYDNPLXX | Hydro | Hydro | 9.4 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Mardi Khola HEP | PWRHYDNPLXX | Hydro | Hydro | 4.8 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Lower Modi 1 HEP | PWRHYDNPLXX | Hydro | Hydro | 10 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Sipring Khola HEP | PWRHYDNPLXX | Hydro | Hydro | 9.658 | 2008 | 2060 | 0.45 | Operational | Nepal_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Victoria | PWRHYDLKAXX | Hydro | Major Hydro | 210 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kotmale | PWRHYDLKAXX | Hydro | Major Hydro | 201 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Upper Kotmale | PWRHYDLKAXX | Hydro | Major Hydro | 150 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Randenigala | PWRHYDLKAXX | Hydro | Major Hydro | 122.6 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Rantembe | PWRHYDLKAXX | Hydro | Major Hydro | 50 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Ukuwela | PWRHYDLKAXX | Hydro | Major Hydro | 40 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Bowatenna | PWRHYDLKAXX | Hydro | Major Hydro | 40 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Nillambe | PWRHYDLKAXX | Hydro | Major Hydro | 3.2 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Uma Oya | PWRHYDLKAXX | Hydro | Major Hydro | 122 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Samanalawewa | PWRHYDLKAXX | Hydro | Major Hydro | 120 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kukuleganga | PWRHYDLKAXX | Hydro | Major Hydro | 75 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Inginiyagala | PWRHYDLKAXX | Hydro | Major Hydro | 8.8 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Udawalawa | PWRHYDLKAXX | Hydro | Major Hydro | 4 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Laxapana | PWRHYDLKAXX | Hydro | Major Hydro | 153.8 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Polpitiya | PWRHYDLKAXX | Hydro | Major Hydro | 90 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Canyon | PWRHYDLKAXX | Hydro | Major Hydro | 60 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wimalasurendra | PWRHYDLKAXX | Hydro | Major Hydro | 50 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Broadlands | PWRHYDLKAXX | Hydro | Major Hydro | 35 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Lakvijaya Unit 1 | PWRCOALKAXX | Coal Steam | Coal | 300 | 2005 | 2040 | 0.65 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Lakvijaya Unit 2 | PWRCOALKAXX | Coal Steam | Coal | 300 | 2005 | 2040 | 0.65 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Lakvijaya Unit 3 | PWRCOALKAXX | Coal Steam | Coal | 300 | 2005 | 2040 | 0.65 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa GT-07 | PWROILLKAXX | Oil/Diesel | Oil | 115 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa CCY-1 GT (KCCP1) | PWROILLKAXX | Oil/Diesel | Oil | 101 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa CCY-1 ST (KCCP1) | PWROILLKAXX | Oil/Diesel | Oil | 54 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa CCY-2 GT (KCCP2) | PWROILLKAXX | Oil/Diesel | Oil | 101 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa CCY-2 ST (KCCP2) | PWROILLKAXX | Oil/Diesel | Oil | 54 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa Frame V GTs | PWROILLKAXX | Oil/Diesel | Oil | 80 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda A | PWROILLKAXX | Oil/Diesel | Oil | 80 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda B | PWROILLKAXX | Oil/Diesel | Oil | 80 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Barge Mounted Plant | PWROILLKAXX | Oil/Diesel | Oil | 60 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Uthuru Janani | PWROILLKAXX | Oil/Diesel | Oil | 24 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Old Kelanitissa Diesel | PWROILLKAXX | Oil/Diesel | Oil | 40 | 2005 | 2040 | 0.3 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Thambapavani (Mannar) Wind Farm | PWRWONLKAXX | Wind | Wind | 103.5 | 2005 | 2030 | 0.25 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | IPP Wind (various) | PWRWONLKAXX | Wind | Wind | 163 | 2005 | 2030 | 0.25 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | IPP Ground-Mounted Solar | PWRSPVLKAXX | Solar PV | Solar | 138 | 2005 | 2030 | 0.18 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Rooftop Solar (CEB network) | PWRSPVLKAXX | Solar PV | Solar | 657 | 2005 | 2030 | 0.18 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Rooftop Solar (LECO network) | PWRSPVLKAXX | Solar PV | Solar | 158 | 2005 | 2030 | 0.18 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | IPP Mini Hydro (aggregate) | PWRHYDLKAXX | Hydro | Mini Hydro | 419 | 2005 | 2060 | 0.45 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | IPP Biomass / Waste Heat (aggregate) | PWRBIOLKAXX | Biomass | Biomass/Waste Heat | 54 | 2005 | 2040 | 0.5 | Operational | SriLanka_Electricity_Infrastructure.xlsx
Maldives | MV | Greater Male' Diesel Power Plants | PWROILMDVXX | Diesel | Diesel | 140 | 2015 | 2050 | 0.25 | Operational | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Greater Male' Solar PV (rooftop + ground) | PWRSPVMDVXX | Solar PV | Solar PV | 10 | 2015 | 2040 | 0.18 | Operational | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Outer Inhabited Islands — Diesel Gensets | PWROILMDVXX | Diesel | Diesel | 181 | 2015 | 2050 | 0.25 | Operational | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Outer Inhabited Islands — Solar PV | PWRSPVMDVXX | Solar PV | Solar PV | 27 | 2015 | 2040 | 0.18 | Operational | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Resort Islands — Diesel Gensets | PWROILMDVXX | Diesel | Diesel | 211 | 2015 | 2050 | 0.25 | Operational | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Resort Islands — Solar PV | PWRSPVMDVXX | Solar PV | Solar PV | 31 | 2015 | 2040 | 0.18 | Operational | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ADh. Maamigili Island Power System | PWROILMDVXX | Diesel | Diesel | 0 | 2015 | 2050 | 0.25 | Operational | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | R. Dhuvaafaru Island Power System | PWROILMDVXX | Diesel | Diesel | 0 | 2015 | 2050 | 0.25 | Operational | Maldives_Energy_Infrastructure.xlsx
India | IN_E | Amrit Bio Energy & Industries Ltd West Bengal Bankura 10 | PWRBIOINDEA | Biomass Power | Bio Power | 10 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Harinagar Sugar Mills Ltd Bihar Pashchim Champaran 14.5 | PWRBIOINDEA | Biomass Power | Bio Power | 14.5 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Ispat Alloys Ltd West Bengal Bardhaman 10 | PWRBIOINDEA | Biomass Power | Bio Power | 10 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Kamarhatty Power Ltd West Bengal Bardhaman 6 | PWRBIOINDEA | Biomass Power | Bio Power | 6 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | New Swadeshi Sugar Mill Ltd Bihar Pashchim Champaran 10 | PWRBIOINDEA | Biomass Power | Bio Power | 10 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] Bihar N.A. 88 | PWRBIOINDEA | Biomass Power | Bio Power | 88 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] Odisha N.A. 30 | PWRBIOINDEA | Biomass Power | Bio Power | 30.4 | Pre-2000 | Odisha | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] West Bengal N. | PWRBIOINDEA | Biomass Power | Bio Power | 274 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Bihar N.A. 26.4 | PWRBIOINDEA | Biomass Power | Bio Power | 26.4 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Jharkhand N.A. 20.14 | PWRBIOINDEA | Biomass Power | Bio Power | 20.14 | Pre-2000 | Jharkhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Odisha N.A. 8.82 | PWRBIOINDEA | Biomass Power | Bio Power | 8.82 | Pre-2000 | Odisha | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] West Bengal N.A. 43. | PWRBIOINDEA | Biomass Power | Bio Power | 43.52 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] Bihar N.A. 1.32 | PWRBIOINDEA | Biomass Power | Bio Power | 1.32 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] Odisha N.A. 5 | PWRBIOINDEA | Biomass Power | Bio Power | 5 | Pre-2000 | Odisha | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] West Bengal N.A. 8 | PWRBIOINDEA | Biomass Power | Bio Power | 8.34 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Shalivahana Green Energy Ltd Odisha Dhenkanal 20 | PWRBIOINDEA | Biomass Power | Bio Power | 20 | Pre-2000 | Odisha | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Bakreshwar TPS | PWRCOAINDEA | Coal Steam | Coal | 1050 | 1999-07-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Bandel TPS | PWRCOAINDEA | Coal Steam | Coal | 270 | 1965-05-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Barauni TPS | PWRCOAINDEA | Coal Steam | Coal | 500 | 2018-01-01 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Barh STPP | PWRCOAINDEA | Coal Steam | Coal | 3300 | 2013-11-30 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Bokaro A Extension TPS | PWRCOAINDEA | Coal Steam | Coal | 500 | 2016-03-22 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Budge Budge TPS | PWRCOAINDEA | Coal Steam | Coal | 750 | 1997-09-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Chandrapura (DVC) TPS | PWRCOAINDEA | Coal Steam | Coal | 500 | 2009-11-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Darlipali STPP | PWRCOAINDEA | Coal Steam | Coal | 1600 | 2019-12-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Derang TPP | PWRCOAINDEA | Coal Steam | Coal | 1200 | 2014-05-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Durgapur Projects (D.P.L.) TPS | PWRCOAINDEA | Coal Steam | Coal | 550 | 2007-11-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Durgapur Steel TPS | PWRCOAINDEA | Coal Steam | Coal | 1000 | 2011-07-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Farakka STPS | PWRCOAINDEA | Coal Steam | Coal | 2100 | 1986-01-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Haldia TPP | PWRCOAINDEA | Coal Steam | Coal | 600 | 2014-01-14 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Hiranmaye TPP | PWRCOAINDEA | Coal Steam | Coal | 300 | 2017-08-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | IB Valley TPS | PWRCOAINDEA | Coal Steam | Coal | 1740 | 1994-05-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Ind Barath (Utkal)/JSW Energy (Utkal) Ltd. | PWRCOAINDEA | Coal Steam | Coal | 700 | 2016-02-25 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Jojobera TPS | PWRCOAINDEA | Coal Steam | Coal | 240 | 2001-10-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Kahalgaon STPS | PWRCOAINDEA | Coal Steam | Coal | 2340 | 1992-03-01 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Kamalanga TPS | PWRCOAINDEA | Coal Steam | Coal | 1050 | 2013-03-29 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Kodarma TPP | PWRCOAINDEA | Coal Steam | Coal | 1000 | 2011-07-20 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Kolaghat TPS | PWRCOAINDEA | Coal Steam | Coal | 840 | 1984-10-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Maadurga Thermal Power (MTPCL) | PWRCOAINDEA | Coal Steam | Coal | 60 | 2024-09-23 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Mahadev Prasad or Jamshedpur Kandra STPP | PWRCOAINDEA | Coal Steam | Coal | 540 | 2012-11-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Maithon TPP | PWRCOAINDEA | Coal Steam | Coal | 1050 | 2011-09-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Mejia TPS | PWRCOAINDEA | Coal Steam | Coal | 2340 | 1995-12-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Muzaffarpur TPS | PWRCOAINDEA | Coal Steam | Coal | 390 | 2015-03-31 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Nabi Nagar TPP | PWRCOAINDEA | Coal Steam | Coal | 1000 | 2016-03-20 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | New NabiNagar TPP (Majhiyan) | PWRCOAINDEA | Coal Steam | Coal | 1980 | 2019-07-01 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | North Karanpura TPP | PWRCOAINDEA | Coal Steam | Coal | 1980 | 2023-01-18 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Patratu TPS | PWRCOAINDEA | Coal Steam | Coal | 800 | 2025-10-16 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Raghunathpur TPS | PWRCOAINDEA | Coal Steam | Coal | 1200 | 2014-08-24 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Sagardighi TPS | PWRCOAINDEA | Coal Steam | Coal | 1600 | 2007-09-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Santaldih TPS | PWRCOAINDEA | Coal Steam | Coal | 500 | 2007-11-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Southern Generating Power Station (Southern Repl. TPS) | PWRCOAINDEA | Coal Steam | Coal | 135 | 1990-04-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Sterlite (Jharsuguda)/ Vedanta Thermal Power Plant | PWRCOAINDEA | Coal Steam | Coal | 600 | 2010-10-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Super Critical Buxar Thermal Power Plant | PWRCOAINDEA | Coal Steam | Coal | 660 | 2025-11-05 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Talcher or Kaniha Talcher STPS | PWRCOAINDEA | Coal Steam | Coal | 3000 | 1995-02-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Tenughat TPS | PWRCOAINDEA | Coal Steam | Coal | 420 | 1994-04-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Balimela Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 510 | 1973-08-14 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Chuzachen Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 110 | 2013-04-20 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Dikchu Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 96 | 2017-04-11 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Hirakud (Burla & Chiplima) Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 359.8 | 1956-12-18 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Jaldhaka I Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 36 | 1967-08-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Jorethang Loop Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 96 | 2015-09-22 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Machkund Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 114.75 | 1955-08-19 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Maithon Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 63.2 | 1957-10-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Panchet Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 80 | 1959-06-12 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Purulia Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 900 | 2007-12-17 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Rammam II Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 50 | 1995-08-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Rangit Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 60 | 2000-02-03 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Rengali Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 250 | 1985-08-27 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Rongnichu Hydro Power Project | PWRHYDINDEA | Hydro | Hydro | 113 | 2021-06-01 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Subernarekha I & II Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 130 | 1977-05-30 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Tashiding Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 97 | 2018-11-06 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta III Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 1200 | 2017-01-14 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Low Dam III Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 132 | 2013-01-20 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Low Dam IV Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 160 | 2016-02-14 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta V Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 510 | 2008-02-06 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Upper Indravati Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 600 | 1999-09-19 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Upper Kolab Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 320 | 1988-03-15 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Amethi Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.5 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Angoor Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Arwal Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.5 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | BSHPC Small Hydro Project 1 | PWRHYDINDEA | Hydro | Small Hydro | 2 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | BSHPC Small Hydro Project 2 | PWRHYDINDEA | Hydro | Small Hydro | 3.3 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Baitarini Power Hydel Project | PWRHYDINDEA | Hydro | Small Hydro | 24 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Barun Small Hydel Power Station | PWRHYDINDEA | Hydro | Small Hydro | 3.3 | 1996-12-01 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Belsar Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Dehri Small Hydel Power Station | PWRHYDINDEA | Hydro | Small Hydro | 6.6 | 1995-12-01 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Dhelabagh Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Fazi Hydel Project | PWRHYDINDEA | Hydro | Small Hydro | 1.2 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Goutamghagh Mini Hydel Scheme | PWRHYDINDEA | Hydro | Small Hydro | 0.01 | 1999-01-07 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Jaldhaka Small Hydro Project II | PWRHYDINDEA | Hydro | Small Hydro | 8 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Jalimghagh Mini Hydel Scheme | PWRHYDINDEA | Hydro | Small Hydro | 0.02 | 1997-03-14 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Kakatiya Hydroelectric Project | PWRHYDINDEA | Hydro | Small Hydro | 9 | 2022-04-30 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Kataiya Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Kosi Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 20 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Little Rangit Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 2 | 1970-01-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Lower Kolab Small Hydro Electric Project | PWRHYDINDEA | Hydro | Small Hydro | 12 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Massanjore Hydel Project | PWRHYDINDEA | Hydro | Small Hydro | 4 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Middle Kolab Small Hydro Electric Project | PWRHYDINDEA | Hydro | Small Hydro | 25 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Mungopoo-Kalikhola Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | 2003-12-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Nasriganj Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Neora Hydro Limited Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | 2006-04-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Nindighagh Mini Hydel Scheme | PWRHYDINDEA | Hydro | Small Hydro | 0.02 | 1997-03-14 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Nippon Power Limited Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | 2007-03-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Paharma Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Potteru Hydro Electric Project Phase I | PWRHYDINDEA | Hydro | Small Hydro | 6 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Rajpur Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.7 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Rampur Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.25 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Richington Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 2 | 1979-12-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 1 | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 10 | PWRHYDINDEA | Hydro | Small Hydro | 8 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 2 | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 3 | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 4 | PWRHYDINDEA | Hydro | Small Hydro | 2 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 5 | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 6 | PWRHYDINDEA | Hydro | Small Hydro | 2 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 7 | PWRHYDINDEA | Hydro | Small Hydro | 12 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 8 | PWRHYDINDEA | Hydro | Small Hydro | 4 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 9 | PWRHYDINDEA | Hydro | Small Hydro | 2.5 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Samal Hydro Electric Project | PWRHYDINDEA | Hydro | Small Hydro | 20 | 2009-10-11 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Sapthadharo Small Hydroelectric Project | PWRHYDINDEA | Hydro | Small Hydro | 18 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Sebari Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Shrikhinda Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.7 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Sidrapong Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.6 | 1897-10-11 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Falls Small Hydro Project Phase 1 | PWRHYDINDEA | Hydro | Small Hydro | 22.5 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Falls Small Hydro Project Phase 2 | PWRHYDINDEA | Hydro | Small Hydro | 22.5 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Falls Small Hydro Project Phase 3 | PWRHYDINDEA | Hydro | Small Hydro | 22.5 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Tejpura Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1.5 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Titaiya Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 4 | 1953-02-01 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Triveni Link Canal Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_E | Valmikinagar Hydroelectric Power Station | PWRHYDINDEA | Hydro | Small Hydro | 15 | 1993-12-01 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kalpong Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 5.25 | 2001-09-01 | Andaman and Nicobar Islan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Others (districts not specified) [Non-Bagasse based cogen.] Assam N.A. 2 | PWRBIOINDNE | Biomass Power | Bio Power | 2 | Pre-2000 | Assam | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Others (districts not specified) [Non-Bagasse based cogen.] Meghalaya N.A. 13.8 | PWRBIOINDNE | Biomass Power | Bio Power | 13.8 | Pre-2000 | Meghalaya | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Bongaigaon TPP | PWRCOAINDNE | Coal Steam | Coal | 750 | 2015-06-02 | Assam | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Doyang Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 75 | 2000-06-29 | Nagaland | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kameng Hydro Power Project | PWRHYDINDNE | Hydro | Hydro | 600 | 2020-02-01 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Karbi Langpai Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 100 | 2007-06-29 | Assam | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Khandong Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 46 | 1984-03-08 | Assam | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kopili Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 200 | 1988-07-04 | Assam | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kyrdemkulai (Umium III) Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 60 | 1979-06-01 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Loktak Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 105 | 1983-06-01 | Manipur | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Myntdu I Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 126 | 2011-11-23 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | New Umtru Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 40 | 2017-04-22 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Pare Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 110 | 2018-05-21 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Ranganadi Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 405 | 2002-01-26 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Subansiri Lower Hydro Power Project | PWRHYDINDNE | Hydro | Hydro | 250 | 2025-12-18 | Assam | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tuirial Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 60 | 2017-08-25 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Umium I Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 36 | 1965-02-21 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Umium IV Hydroelectric Power Project | PWRHYDINDNE | Hydro | Hydro | 60 | 1992-08-11 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Agartala Gas Turbine Power Station | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 135 | 1998-02-06 | Tripura | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Baramura Gas Thermal Project | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 42 | 2002-11-27 | Tripura | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kathalguri (Assam) Gas Combined Cycle Gas Turbine Power Plant | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 291 | 1995-03-16 | Assam | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lakwa GT Replacement Power Project (LRPP ) | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 69.75 | 2018-10-01 | Assam | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lakwa Gas Turbine Power Station | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 97.2 | 1994-01-03 | Assam | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Namrup Thermal Power Station (NTPS) | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 139.4 | 1965-04-01 | Assam | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Rokhia Gas Thermal Project | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 63 | 2002-08-02 | Tripura | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tripura (Monarchak) Gas based Combined Cycle Power Plant | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 101 | 2015-03-30 | Tripura | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tripura (Palatana) Combined Cycle Gas Turbine Power Plant | PWRNGSINDNE | Natural Gas CC | Oil & Gas | 726.6 | 2013-01-02 | Tripura | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Atenglok Multipurpose Pico Hydel Power Project | PWRHYDINDNE | Hydro | Small Hydro | 0.01 | 2008-11-14 | Manipur | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Chadong Kong Micro Hydel Power Project | PWRHYDINDNE | Hydro | Small Hydro | 0.03 | 2011-06-27 | Manipur | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 1 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 10 | PWRHYDINDNE | Hydro | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 11 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 12 | PWRHYDINDNE | Hydro | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 13 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 14 | PWRHYDINDNE | Hydro | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 15 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 16 | PWRHYDINDNE | Hydro | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 17 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 18 | PWRHYDINDNE | Hydro | Small Hydro | 4.5 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 2 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 3 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 4 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 5 | PWRHYDINDNE | Hydro | Small Hydro | 4 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 6 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 7 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 8 | PWRHYDINDNE | Hydro | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 9 | PWRHYDINDNE | Hydro | Small Hydro | 4.5 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Dhansiri Small Hydro Power Project | PWRHYDINDNE | Hydro | Small Hydro | 20 | Pre-2000 | Assam | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Flovel Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 16 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Ganol Hydro Power Project | PWRHYDINDNE | Hydro | Small Hydro | 22.5 | 2023-07-31 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Gelnel Mini Hydel Power Project | PWRHYDINDNE | Hydro | Small Hydro | 0.4 | 2010-09-04 | Manipur | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Gumti Hydel Project | PWRHYDINDNE | Hydro | Small Hydro | 15 | 1976-12-01 | Tripura | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Iru Lok Hydel Power Project | PWRHYDINDNE | Hydro | Small Hydro | 0.01 | 2012-01-21 | Manipur | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kau Tlabung Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 3 | 2005-05-05 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Khawiva Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 1.05 | 1988-12-08 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lakhroh Mini Hydel Project | PWRHYDINDNE | Hydro | Small Hydro | 1.5 | 2019-03-01 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lamsial Mini Hydel Project | PWRHYDINDNE | Hydro | Small Hydro | 0.5 | 2008-08-26 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lang Hydro Electric Project | PWRHYDINDNE | Hydro | Small Hydro | 1 | Pre-2000 | Nagaland | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Likimro Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 24 | Pre-2000 | Nagaland | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Machima I Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 2 | 1996-01-05 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Machima II Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 3 | 2009-11-11 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Mizoram Small Hydro Project Bunched | PWRHYDINDNE | Hydro | Small Hydro | 10.62 | Pre-2000 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Mizoram State Hydro Project 1 | PWRHYDINDNE | Hydro | Small Hydro | 3 | Pre-2000 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Mizoram State Hydro Project 2 | PWRHYDINDNE | Hydro | Small Hydro | 2.5 | Pre-2000 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Multipurpose Pico Hydel Project | PWRHYDINDNE | Hydro | Small Hydro | 0.01 | 2009-12-30 | Manipur | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Myntriang Small Hydroelectric Project (MSHEP) | PWRHYDINDNE | Hydro | Small Hydro | 13.5 | Pre-2000 | Assam | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Nametrang Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Nuranang Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 6 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Serlui A Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 1 | 1984-04-24 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Serlui B Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 12 | 2010-04-30 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Siru Small Hydro Electric Project | PWRHYDINDNE | Hydro | Small Hydro | 6 | Pre-2000 | Arunachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Sonapani Mini Hydel Electric Project | PWRHYDINDNE | Hydro | Small Hydro | 1.5 | 2009-10-27 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tehok Hydro Electric Project | PWRHYDINDNE | Hydro | Small Hydro | 1 | Pre-2000 | Nagaland | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Terei Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 3 | 1999-10-12 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tsütsüng hydro electric project | PWRHYDINDNE | Hydro | Small Hydro | 1 | 2022-05-03 | Nagaland | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tuipanglui Small hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 3 | 2004-12-17 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tuipui Mini Hydel Project | PWRHYDINDNE | Hydro | Small Hydro | 0.5 | 1991-12-15 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tuirivang Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 0.3 | 1989-08-14 | Mizoram | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Umium Stage II Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 18 | 1970-07-22 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_NE | Umtru Small Hydro Project | PWRHYDINDNE | Hydro | Small Hydro | 11.2 | 1957-05-01 | Meghalaya | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | A2Z Gurgaon Uttar Pradesh Kanpur Nagar 15 | PWRBIOINDNO | Biomass Power | Bio Power | 15 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | AB Grains Spirits Pvt. Ltd. Haryana Ambala 8.9 2014-15 | PWRBIOINDNO | Biomass Power | Bio Power | 8.9 | 2014-01-15 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | ADS Spirits Pvt.Ltd. Haryana Jhajjar 2.3 2013-14 | PWRBIOINDNO | Biomass Power | Bio Power | 2.3 | 2013-01-14 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Aguata Sugar and Chemicals Uttar Pradesh Bulandshahar 2.5 | PWRBIOINDNO | Biomass Power | Bio Power | 2.5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Akbarchinimill Uttar Pradesh Ayodhya 11 | PWRBIOINDNO | Biomass Power | Bio Power | 11 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Amrit Envi. Tech. (P) Ltd. Rajasthan Jaipur 8 2006-10-01 | PWRBIOINDNO | Biomass Power | Bio Power | 8 | 2006-10-01 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Anand Triplex board Uttar Pradesh Meerut 10 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Arohal Food Pvt.Ltd, Uttar Pradesh Bahraich 0.4 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 0.4 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ashoka Distillers& Chemicals Ltd. Haryana Palwal 3 2015-16 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2015-01-16 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Avani Tripura Dev Uttarakhand Pithoragarh 0.12 | PWRBIOINDNO | Biomass Power | Bio Power | 0.12 | Pre-2000 | Uttarakhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Awadh sugarmill Uttar Pradesh Sitapur 10 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | BAHL Paper Mill Uttarakhand Udham Singh Nagar 4 | PWRBIOINDNO | Biomass Power | Bio Power | 4 | Pre-2000 | Uttarakhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj Chinimill Uttar Pradesh Kheri 12 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj Hindustan sugarmill Uttar Pradesh Kheri 12 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj Hindustan sugarmill Uttar Pradesh Shahjahanpur 12 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj Kagaj Pvt Ltd Uttar Pradesh Unnao 1 2009-10 | PWRBIOINDNO | Biomass Power | Bio Power | 1 | 2009-10-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj sugarmill Uttar Pradesh Gonda 12 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz Hindustan Kinaunee Uttar Pradesh Meerut 10 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz Hindustan Ltd Uttar Pradesh Bijnor 10 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz Hindustan Ltd Uttar Pradesh Shamli 10 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz sugar Limited Uttar Pradesh Pilibhit 7 | PWRBIOINDNO | Biomass Power | Bio Power | 7 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz sugarmill Uttar Pradesh Muzaffarnagar 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz sugarmill Uttar Pradesh Pilibhit 12 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz sugarmill Uttar Pradesh Saharanpur 10 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balrampur Chinimill Uttar Pradesh Balrampur 22.25 | PWRBIOINDNO | Biomass Power | Bio Power | 22.25 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balrampur Chinimill Uttar Pradesh Gonda 5 | PWRBIOINDNO | Biomass Power | Bio Power | 5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balrampur Chinimill Uttar Pradesh Kheri 11 | PWRBIOINDNO | Biomass Power | Bio Power | 11 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balrampur Chinimill Uttar Pradesh Kheri 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Best Food International (P) Ltd Haryana Karnal 4 2010-11 | PWRBIOINDNO | Biomass Power | Bio Power | 4 | 2010-11-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Best Food International (P) Ltd Haryana Karnal 6 2012-13 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2012-01-13 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhaghauli sugarmill and Distilery Uttar Pradesh Hardoi 12 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bharat Sugar Mills Uttar Pradesh Prayagraj 15 | PWRBIOINDNO | Biomass Power | Bio Power | 15 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhavani papermill Uttar Pradesh Rae Bareli 6 2007-08 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2007-08-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bindal papermill Uttar Pradesh Muzaffarnagar 15 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 15 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Centuri lamination Uttar Pradesh Ghaziabad 4.2 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 4.2 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ch.DeviLal Co-operative Sugar Mill Ltd. Haryana Sonipat 6 2003-04 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2003-04-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chaddha sugarmill Uttar Pradesh Amroha 23 | PWRBIOINDNO | Biomass Power | Bio Power | 23 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | DSCL Uttar Pradesh Kheri 12 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | DSCL sugarmill Uttar Pradesh Hardoi 15 | PWRBIOINDNO | Biomass Power | Bio Power | 30 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dalmiya chinimill Uttar Pradesh Shahjahanpur 25 | PWRBIOINDNO | Biomass Power | Bio Power | 25 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dalmiya chinimill Uttar Pradesh Sitapur 25 | PWRBIOINDNO | Biomass Power | Bio Power | 50 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Daurala Sugar Mills Uttar Pradesh Meerut 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dawarala sugarmill Uttar Pradesh Meerut 10 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dee Development Engineers Pvt. Ltd Punjab Ferozepur 8 2009-02-01 | PWRBIOINDNO | Biomass Power | Bio Power | 8 | 2009-02-01 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Deopriya papermill Uttar Pradesh Meerut 6 2006-07 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2006-07-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhampur Sugars Ltd (DSM) Uttar Pradesh Bijnor 30 | PWRBIOINDNO | Biomass Power | Bio Power | 30 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhampur Sugars Ltd (DSM) Uttar Pradesh Kanpur Dehat 40 | PWRBIOINDNO | Biomass Power | Bio Power | 40 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhampur Sugars Ltd (DSM) Uttar Pradesh Moradabad 40 | PWRBIOINDNO | Biomass Power | Bio Power | 40 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhampur Sugars Ltd (DSM) Uttar Pradesh Muzaffarnagar 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dwarkesh chinimill Uttar Pradesh Bijnor 7.5 | PWRBIOINDNO | Biomass Power | Bio Power | 7.5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dwarkesh sugarmill Uttar Pradesh Bareilly 24 | PWRBIOINDNO | Biomass Power | Bio Power | 24 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dwarkesh sugarmill Uttar Pradesh Bijnor 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | EICL Ltd. (Bharat Starch Industries) Haryana Yamuna Nagar 2 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 2 | 2008-09-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | East Delhi Waste Processing Company Limited (EDWRCL) Delhi East Delhi 12 21.10.2 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | 2012-10-21 | Delhi | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | GEMCO Energy Limited Haryana Bhiwani 8 2013-14 | PWRBIOINDNO | Biomass Power | Bio Power | 8 | 2013-01-14 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ganga papermill Uttar Pradesh Varanasi 1.5 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 1.5 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ginus papermill Uttar Pradesh Moradabad 6 2007-08 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2007-08-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Goel International Pvt. Ltd. Haryana Karnal 3 2011-12 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2011-12-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Govindnagar Sugar Uttar Pradesh Basti 6 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Green Planet Energy Pvt. Ltd. Punjab Hoshiarpur 6 2012-03-01 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2012-03-01 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Green Planet Energy Pvt. Ltd. Punjab Jalandhar 6 2013-02-01 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2013-02-01 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gulsan sugar and Chemical Uttar Pradesh Muzaffarnagar 4 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 4 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Haidergarh chinimill Uttar Pradesh Bara Banki 20.95 | PWRBIOINDNO | Biomass Power | Bio Power | 20.95 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Haryana Liquors Haryana Karnal 2.5 2014-15 | PWRBIOINDNO | Biomass Power | Bio Power | 2.5 | 2014-01-15 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | J.H.V.Sugar Uttar Pradesh Maharajganj 17 | PWRBIOINDNO | Biomass Power | Bio Power | 17 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | J.K.Sugarmill Uttar Pradesh Bareilly 12.5 | PWRBIOINDNO | Biomass Power | Bio Power | 12.5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jhunjunwala Vanaspati, Uttar Pradesh Jaunpur 3 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | K. R. Pulp and Paper Ltd. Uttar Pradesh Shahjahanpur 2.5 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 2.5 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | K.M.Sugarmill Uttar Pradesh Ayodhya 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | K.R. Pulp paper Uttar Pradesh Shahjahanpur 12 2009-10 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | 2009-10-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | KalpaTaru Power Transmission Ltd. Rajasthan Ganganagar 7.8 2003-07-15 | PWRBIOINDNO | Biomass Power | Bio Power | 7.8 | 2003-07-15 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | KalpaTaru Power Transmission Ltd. Rajasthan Tonk 8 2006-11-10 | PWRBIOINDNO | Biomass Power | Bio Power | 8 | 2006-11-10 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kamlapur Sugar and Industries Uttar Pradesh Sitapur 45 | PWRBIOINDNO | Biomass Power | Bio Power | 45 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kayem (PAN) Foods Industries (P ) Ltd. Haryana Panipat 0.5 2011-12 | PWRBIOINDNO | Biomass Power | Bio Power | 0.5 | 2011-12-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kesar Industries Uttar Pradesh Bareilly 25 | PWRBIOINDNO | Biomass Power | Bio Power | 25 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | L.H.Sugar Factory Ltd Uttar Pradesh Pilibhit 28 | PWRBIOINDNO | Biomass Power | Bio Power | 28 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Laxmi Sugar Mill Uttarakhand Haridwar 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttarakhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Laxmi cotton Uttar Pradesh Fatehpur 8 2009-10 | PWRBIOINDNO | Biomass Power | Bio Power | 8 | 2009-10-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Laxmi cottonmill Uttar Pradesh Fatehpur 17.5 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 17.5 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | MSW Bawana Delhi N.A. 24 09.07.2016 | PWRBIOINDNO | Biomass Power | Bio Power | 24 | 2016-09-07 | Delhi | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mahavir spin Uttar Pradesh Unnao 0.4 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 0.4 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Malwa Power Ltd. Punjab Sri Muktsar Sahib 6 2005-05-01 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2005-05-01 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mankapur chinimill Uttar Pradesh Gonda 25 | PWRBIOINDNO | Biomass Power | Bio Power | 25 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Maruti papermill Uttar Pradesh Muzaffarnagar 1.5 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 1.5 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mawana sugars Ltd Uttar Pradesh Meerut 11 | PWRBIOINDNO | Biomass Power | Bio Power | 11 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mawana sugars Ltd Uttar Pradesh Meerut 9 | PWRBIOINDNO | Biomass Power | Bio Power | 9 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mawana sugars Ltd Uttar Pradesh Muzaffarnagar 17 | PWRBIOINDNO | Biomass Power | Bio Power | 17 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mohit Petro Chemi Uttar Pradesh Bijnor 1 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 1 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mohit papermill Uttar Pradesh Bijnor 4.5 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 4.5 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | NV Distilleries Limited Haryana Ambala 2.1 2012-13 | PWRBIOINDNO | Biomass Power | Bio Power | 2.1 | 2012-01-13 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | NV International Haryana Ambala 4 2014-15 | PWRBIOINDNO | Biomass Power | Bio Power | 4 | 2014-01-15 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | New India sugar Ltd. Uttar Pradesh Kushinagar 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Nova Uttar Pradesh Farrukhabad 1 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 1 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Orient Green Power Co. Rajasthan Baran 8 2013-10-06 | PWRBIOINDNO | Biomass Power | Bio Power | 8 | 2013-10-06 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Oswal overseas Uttar Pradesh Bareilly 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) (Waste to Energy) Delhi N.A. 33.17 | PWRBIOINDNO | Biomass Power | Bio Power | 33.17 | Pre-2000 | Delhi | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) (Waste to Energy) Haryana N.A. 11.2 | PWRBIOINDNO | Biomass Power | Bio Power | 11.2 | Pre-2000 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) (Waste to Energy) Punjab N.A. 10.75 | PWRBIOINDNO | Biomass Power | Bio Power | 10.75 | Pre-2000 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) (Waste to Energy) Rajasthan N.A. 59.6 | PWRBIOINDNO | Biomass Power | Bio Power | 59.6 | Pre-2000 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Haryana N.A. 4 | PWRBIOINDNO | Biomass Power | Bio Power | 47.03 | Pre-2000 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Punjab N.A. 23 | PWRBIOINDNO | Biomass Power | Bio Power | 237 | Pre-2000 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Rajasthan N.A. | PWRBIOINDNO | Biomass Power | Bio Power | 29.9 | Pre-2000 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Uttar Pradesh | PWRBIOINDNO | Biomass Power | Bio Power | 834.69 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Uttarakhand N. | PWRBIOINDNO | Biomass Power | Bio Power | 4 | Pre-2000 | Uttarakhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Haryana N.A. 65.88 | PWRBIOINDNO | Biomass Power | Bio Power | 65.88 | Pre-2000 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Himachal Pradesh N.A | PWRBIOINDNO | Biomass Power | Bio Power | 9.2 | Pre-2000 | Himachal Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Punjab N.A. 231.7900 | PWRBIOINDNO | Biomass Power | Bio Power | 231.79 | Pre-2000 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Rajasthan N.A. 2 | PWRBIOINDNO | Biomass Power | Bio Power | 2 | Pre-2000 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Uttar Pradesh N.A. 7 | PWRBIOINDNO | Biomass Power | Bio Power | 7.86 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Uttarakhand N.A. 60 | PWRBIOINDNO | Biomass Power | Bio Power | 60 | Pre-2000 | Uttarakhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Haryana N.A. 38.61 | PWRBIOINDNO | Biomass Power | Bio Power | 38.61 | Pre-2000 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Himachal Pradesh N | PWRBIOINDNO | Biomass Power | Bio Power | 1 | Pre-2000 | Himachal Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Punjab N.A. 34.55 | PWRBIOINDNO | Biomass Power | Bio Power | 34.55 | Pre-2000 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Rajasthan N.A. 11. | PWRBIOINDNO | Biomass Power | Bio Power | 11.77 | Pre-2000 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Uttar Pradesh N.A. | PWRBIOINDNO | Biomass Power | Bio Power | 159.63 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Uttarakhand N.A. 1 | PWRBIOINDNO | Biomass Power | Bio Power | 16.85 | Pre-2000 | Uttarakhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Parle zee Ltd Uttar Pradesh Bahraich 10 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Punjab Biomass Power Pvt. Ltd. Punjab Patiala 12 2010-06-01 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | 2010-06-01 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | R.P Basmati Rice Ltd Haryana Karnal 0.5 2010-11 | PWRBIOINDNO | Biomass Power | Bio Power | 0.5 | 2010-11-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | REI Agro Ltd, (Unit-I) Haryana Rewari 3 2011-12 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2011-12-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | REI Agro Ltd, (Unit-II) Bawal Growth Centres Haryana Rewari 2.5 2010-11 | PWRBIOINDNO | Biomass Power | Bio Power | 2.5 | 2010-11-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Raghuraji Agro Ind. Uttar Pradesh Ambedkar Nagar 1.1 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 1.1 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rai Bahadur Narain Singh Sugar Mills Ltd Uttarakhand Haridwar 29.6 | PWRBIOINDNO | Biomass Power | Bio Power | 29.6 | Pre-2000 | Uttarakhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rama papers Ltd Uttar Pradesh Bijnor 6 2006-07 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2006-07-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ramnagar Chini Mills Uttar Pradesh Shahjahanpur 16 | PWRBIOINDNO | Biomass Power | Bio Power | 16 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rana Sugars Ltd. Uttar Pradesh Rampur 15 | PWRBIOINDNO | Biomass Power | Bio Power | 15 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ranya papermill Uttar Pradesh Basti 3 2007-08 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2007-08-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rozagaon chinimill Uttar Pradesh Bara Banki 16 | PWRBIOINDNO | Biomass Power | Bio Power | 16 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | S.M. Environmental Technologies Pvt. Ltd. Rajasthan Baran 8 2010-02-19 | PWRBIOINDNO | Biomass Power | Bio Power | 8 | 2010-02-19 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | SIAL SBEC Bioenergy Uttar Pradesh Baghpat 14 | PWRBIOINDNO | Biomass Power | Bio Power | 14 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | SSA International Ltd, Haryana Panipat 1.1 | PWRBIOINDNO | Biomass Power | Bio Power | 1.1 | Pre-2000 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sainsons Paper Industries Haryana Kurukshetra 3 2009-10 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2009-10-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sakumbhari Stra Ltd. Uttar Pradesh Moradabad 12 2006-07 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | 2006-07-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sambhav Energy Ltd. Rajasthan Sirohi 20 2010-02-19 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | 2010-02-19 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sangal Papermill Uttar Pradesh Meerut 3 2007-08 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2007-08-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sanjog Sugar & Eco Power Pvt. Ltd. Rajasthan Hanumangarh 10 2011-10-07 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | 2011-10-07 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sant lal ricemill Uttar Pradesh Mainpuri 2.25 2009-10 | PWRBIOINDNO | Biomass Power | Bio Power | 2.25 | 2009-10-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sathyam Power Pvt Ltd Rajasthan Nagaur 10 2011-03-31 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | 2011-03-31 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Satyam Industries Pvt. Ltd Haryana Panipat 3 2011-12 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2011-12-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Saxsaria, Biswal Sugar Factory Uttar Pradesh Sitapur 45 | PWRBIOINDNO | Biomass Power | Bio Power | 45 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shaktibhog Foods Ltd Haryana Karnal 3.5 2014-15 | PWRBIOINDNO | Biomass Power | Bio Power | 3.5 | 2014-01-15 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shakumbari Sugar and Allied Industries Ltd Uttar Pradesh Hardoi 16 | PWRBIOINDNO | Biomass Power | Bio Power | 16 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shri. Vishnu Overseas Pvt. Ltd Haryana Kaithal 1.5 2010-11 | PWRBIOINDNO | Biomass Power | Bio Power | 1.5 | 2010-11-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Simbholi sugar Ltd Uttar Pradesh Ghaziabad 5 | PWRBIOINDNO | Biomass Power | Bio Power | 5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Simbholi sugarmill Uttar Pradesh Bahraich 19 | PWRBIOINDNO | Biomass Power | Bio Power | 19 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sri Jyoti Renewable Energy Pvt. Ltd. Haryana Bhiwani 9.5 2014-15 | PWRBIOINDNO | Biomass Power | Bio Power | 9.5 | 2014-01-15 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Star Papermill Ltd. Uttar Pradesh Saharanpur 5 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 5 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Starwire (India) Ltd Haryana Mahendragarh 9.9 2013-14 | PWRBIOINDNO | Biomass Power | Bio Power | 9.9 | 2013-01-14 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sukhvir Agro Energy Ltd, Uttar Pradesh Ghazipur 13 | PWRBIOINDNO | Biomass Power | Bio Power | 13 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sumit Agro project, Uttar Pradesh Meerut 3 2007-08 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2007-08-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunstar Overseas Ltd Haryana Sonipat 1.95 2010-11 | PWRBIOINDNO | Biomass Power | Bio Power | 1.95 | 2010-11-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Surya Chambal Power Ltd. Rajasthan Kota 7.5 2006-03-31 | PWRBIOINDNO | Biomass Power | Bio Power | 7.5 | 2006-03-31 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Syus papermill Uttar Pradesh Basti 3 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | The HAFED Cooperative Sugar Mill Haryana Karnal 6 2010-11 | PWRBIOINDNO | Biomass Power | Bio Power | 6 | 2010-11-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | The Meham Cooperative Sugar Mill Haryana Rohtak 5 2007-08 | PWRBIOINDNO | Biomass Power | Bio Power | 5 | 2007-08-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | The Piccadily Agro Industries Haryana Karnal 17 2010-11 | PWRBIOINDNO | Biomass Power | Bio Power | 17 | 2010-11-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | The Rajasthan State Ganganagar Sugar Mills Ltd. Rajasthan Ganganagar 4.95 2016-0 | PWRBIOINDNO | Biomass Power | Bio Power | 4.95 | 2016-05-09 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | The Rohtak Cooperative Sugar Mill Haryana Rohtak 16 2009-10 | PWRBIOINDNO | Biomass Power | Bio Power | 16 | 2009-10-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | The Shahbad Cooperative Sugar Mill Haryana Kurukshetra 24 2009-10 | PWRBIOINDNO | Biomass Power | Bio Power | 24 | 2009-10-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | The Sonepat Cooperative Sugar Mill Ltd. Haryana Sonipat 3 2004- 05 | PWRBIOINDNO | Biomass Power | Bio Power | 3 | 2004-05-21 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tikola sugarmill Ltd. Uttar Pradesh Muzaffarnagar 5 | PWRBIOINDNO | Biomass Power | Bio Power | 5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Timarpur Okhla Waste Management Co Pvt Ltd (TOWMCL) Delhi N.A. 16 27.01.2012 | PWRBIOINDNO | Biomass Power | Bio Power | 16 | 2012-01-27 | Delhi | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tirupati Basmati Exports Private Limited Haryana Karnal 1.2 2016-17 | PWRBIOINDNO | Biomass Power | Bio Power | 1.2 | 2016-01-17 | Haryana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Transtech Green Power Ltd. Rajasthan Jalore 12 2010-07-28 | PWRBIOINDNO | Biomass Power | Bio Power | 12 | 2010-07-28 | Rajasthan | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Triveni sugarmill Uttar Pradesh Muzaffarnagar 20 | PWRBIOINDNO | Biomass Power | Bio Power | 20 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Triveni sugarmill Uttar Pradesh Saharanpur 19.16 | PWRBIOINDNO | Biomass Power | Bio Power | 19.16 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Universal Biomass Energy Pvt. Ltd. Punjab Sri Muktsar Sahib 14.5 2009-10-01 | PWRBIOINDNO | Biomass Power | Bio Power | 14.5 | 2009-10-01 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Gangej sugarmill Uttar Pradesh Bijnor 24 | PWRBIOINDNO | Biomass Power | Bio Power | 24 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ushar Agro Uttar Pradesh Mathura 1 2008-09 | PWRBIOINDNO | Biomass Power | Bio Power | 1 | 2008-09-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttam sugarmill Uttar Pradesh Bijnor 13.5 | PWRBIOINDNO | Biomass Power | Bio Power | 13.5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttar Sugar Mills Ltd Uttarakhand Haridwar 15 | PWRBIOINDNO | Biomass Power | Bio Power | 15 | Pre-2000 | Uttarakhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttar sugarmill Uttar Pradesh Saharanpur 10 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttar sugarmill Uttar Pradesh Shahjahanpur 6.5 | PWRBIOINDNO | Biomass Power | Bio Power | 6.5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Viaton Energy Pvt. Ltd. Punjab Mansa 10 2013-07-01 | PWRBIOINDNO | Biomass Power | Bio Power | 10 | 2013-07-01 | Punjab | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Yado Sugar Uttar Pradesh Budaun 5 | PWRBIOINDNO | Biomass Power | Bio Power | 5 | Pre-2000 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Yes papermill Uttar Pradesh Ayodhya 12.5 2006-07 | PWRBIOINDNO | Biomass Power | Bio Power | 12.5 | 2006-07-21 | Uttar Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Anpara C TPS or Lanco Anapara | PWRCOAINDNO | Coal Steam | Coal | 1200 | 2011-11-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Anpara TPS | PWRCOAINDNO | Coal Steam | Coal | 2630 | 1986-01-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Barkhera TPS | PWRCOAINDNO | Coal Steam | Coal | 90 | 2011-11-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Barsingar Lignite TPP | PWRCOAINDNO | Coal Steam | Coal | 250 | 2010-06-01 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chhabra TPP | PWRCOAINDNO | Coal Steam | Coal | 2320 | 2009-10-01 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dadri TPP (NCTPP) | PWRCOAINDNO | Coal Steam | Coal | 1820 | 1991-12-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghatampur TPP | PWRCOAINDNO | Coal Steam | Coal | 1320 | 2024-12-03 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Giral Lignite TPS | PWRCOAINDNO | Coal Steam | Coal | 250 | 2007-02-01 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Goindwal Sahib TPP | PWRCOAINDNO | Coal Steam | Coal | 540 | 2016-02-14 | Punjab | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Guru Hargobind TPS | PWRCOAINDNO | Coal Steam | Coal | 920 | 1997-12-01 | Punjab | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Harduaganj TPS | PWRCOAINDNO | Coal Steam | Coal | 1265 | 1978-03-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Indira Gandhi STPP | PWRCOAINDNO | Coal Steam | Coal | 1500 | 2010-10-01 | Haryana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jalipa- Kapurdi TPP | PWRCOAINDNO | Coal Steam | Coal | 1080 | 2009-10-01 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jawaharpur STPP | PWRCOAINDNO | Coal Steam | Coal | 1320 | 2024-02-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kalisindh STPS | PWRCOAINDNO | Coal Steam | Coal | 1200 | 2014-05-01 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kawai TPS | PWRCOAINDNO | Coal Steam | Coal | 1320 | 2013-05-01 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khamberkhera TPS | PWRCOAINDNO | Coal Steam | Coal | 90 | 2011-10-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khurja Power Project | PWRCOAINDNO | Coal Steam | Coal | 1320 | 2025-01-23 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kota TPS | PWRCOAINDNO | Coal Steam | Coal | 1240 | 1983-01-01 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kundarkhi TPS | PWRCOAINDNO | Coal Steam | Coal | 90 | 2012-01-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lalitpur TPP | PWRCOAINDNO | Coal Steam | Coal | 1980 | 2016-01-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mahatma Gandhi TPS or Jhajjhar TPS | PWRCOAINDNO | Coal Steam | Coal | 1320 | 2012-01-01 | Haryana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Maqsoodpur TPS | PWRCOAINDNO | Coal Steam | Coal | 90 | 2011-11-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Meja STPP | PWRCOAINDNO | Coal Steam | Coal | 1320 | 2018-03-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Obra TPS | PWRCOAINDNO | Coal Steam | Coal | 2320 | 1977-12-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Panipat TPS | PWRCOAINDNO | Coal Steam | Coal | 710 | 2001-03-01 | Haryana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Panki TPS | PWRCOAINDNO | Coal Steam | Coal | 660 | 2025-02-25 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Parichha TPS | PWRCOAINDNO | Coal Steam | Coal | 920 | 2006-03-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Prayagraj (Bara) TPP | PWRCOAINDNO | Coal Steam | Coal | 1980 | 2015-12-25 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rajiv Gandhi TPS | PWRCOAINDNO | Coal Steam | Coal | 1200 | 2010-03-01 | Haryana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rajpura TPP | PWRCOAINDNO | Coal Steam | Coal | 1400 | 2014-02-01 | Punjab | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rihand STPS | PWRCOAINDNO | Coal Steam | Coal | 3000 | 1988-03-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ropar TPS or Guru Gobind Singh STPP | PWRCOAINDNO | Coal Steam | Coal | 840 | 1988-03-01 | Punjab | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rosa TPP | PWRCOAINDNO | Coal Steam | Coal | 1200 | 2010-02-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shree Cement Ltd. TPS | PWRCOAINDNO | Coal Steam | Coal | 344 | 2023-08-31 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Singrauli STPS | PWRCOAINDNO | Coal Steam | Coal | 2000 | 1982-02-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Suratgarh STPS | PWRCOAINDNO | Coal Steam | Coal | 2820 | 1998-02-01 | Rajasthan | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Talwandi Sabo TPP | PWRCOAINDNO | Coal Steam | Coal | 1980 | 2014-06-01 | Punjab | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tanda TPS | PWRCOAINDNO | Coal Steam | Coal | 1760 | 1988-01-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Unchahar or Feroz Gandhi TPS | PWRCOAINDNO | Coal Steam | Coal | 1550 | 1988-11-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Utraula TPS | PWRCOAINDNO | Coal Steam | Coal | 90 | 2012-02-01 | Uttar Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Yamuna Nagar or Deenbandhu Chotu Ram TPS | PWRCOAINDNO | Coal Steam | Coal | 600 | 2007-04-01 | Haryana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Allain Duhangan Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 192 | 2010-09-16 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Anandpur Sahib I & II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 134 | 1985-04-27 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baglihar I Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 450 | 2008-08-10 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baglihar II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 450 | 2015-09-05 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baira Siul Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 180 | 1980-05-18 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajoli Holi Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 180 | 2022-03-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baspa II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 300 | 2003-05-24 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bassi Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 66 | 1970-06-12 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhakra Nangal (Left & Right) Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 1415 | 1960-11-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Budhil Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 70 | 2012-05-26 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chamera I Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 540 | 1994-05-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chamera II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 300 | 2003-11-02 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chamera III Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 231 | 2012-06-07 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chanju I Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 36 | 2017-02-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chibro (Yamuna St.II) Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 240 | 1975-04-20 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chilla Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 144 | 1980-07-17 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chutak Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 44 | 2012-11-08 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dehar Power House | PWRHYDINDNO | Hydro | Hydro | 990 | 1977-11-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhakrani (Yamuna St.I) Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 33.75 | 1965-11-15 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhalipur (Yamuna St.I) Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 51 | 1965-12-10 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhauliganga Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 280 | 2005-10-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dulhasti Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 390 | 2007-04-07 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ganguwal Power House | PWRHYDINDNO | Hydro | Hydro | 77.65 | 1955-01-01 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Giri Bata Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 60 | 1978-05-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jawahar Sagar Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 99 | 1972-05-09 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Karcham Wangtoo Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 1045 | 2011-05-24 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kashang Integrated Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 195 | 2016-08-28 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khara Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 72 | 1992-06-14 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khatima Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 41.4 | 1955-01-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khodri (Yamuna St.II) Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 120 | 1984-01-29 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kishenganga Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 330 | 2018-03-13 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Koldam Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 800 | 2015-03-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Koteshwar Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 400 | 2011-03-28 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kotla Power House | PWRHYDINDNO | Hydro | Hydro | 77.65 | 1956-05-01 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kulhal (Yamuna St.IV) Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 30 | 1975-03-12 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kutehr Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 240 | 2025-08-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Larji Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 126 | 2006-06-28 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lower Jhelum Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 105 | 1978-02-01 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mahi Bajaj Sagar I & II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 140 | 1986-01-22 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Malana Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 86 | 2001-07-05 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Malana II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 100 | 2011-08-06 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Maneri Bhali I Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 90 | 1984-06-06 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Maneri Bhali II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 304 | 2008-06-30 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Matatilla Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 30.6 | 1965-05-18 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mukerian I to IV Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 207 | 1983-10-02 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Naitwar Mori Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 60 | 2023-11-24 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Naptha Jhakri Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 1500 | 2003-05-06 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Nimoo Bazgo Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 45 | 2013-10-30 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Obra Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 99 | 1970-08-01 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Parbati III Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 520 | 2014-02-18 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Parbati St. II Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 800 | 2025-03-24 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pong Power House | PWRHYDINDNO | Hydro | Hydro | 396 | 1978-01-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ram Ganga Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 198 | 1975-12-31 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rampur Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 412.02 | 2014-03-21 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rana Pratap Sagar Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 172 | 1968-08-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ranjit Sagar Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 600 | 2000-08-12 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rihand Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 300 | 1962-08-01 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sainj Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 100 | 2017-09-04 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Salal I & II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 690 | 1987-11-20 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sanjay Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 120 | 1989-06-11 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sawra Kuddu Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 111 | 2021-01-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sewa II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 120 | 2010-06-22 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shanan Power House | PWRHYDINDNO | Hydro | Hydro | 110 | 1932-08-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shrinagar Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 330 | 2015-04-10 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Singoli Bhatwari Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 99 | 2020-12-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sorang Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 100 | 2021-09-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tanakpur Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 94.2 | 1993-04-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tehri I Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 1000 | 2006-09-22 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tehri Pumped Storage Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 750 | 2025-06-05 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uhl-III Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 99.99 | 2025-03-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Sindh II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 105 | 2000-06-01 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uri I Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 480 | 1997-06-01 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uri II Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 240 | 2013-09-25 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Vishnuprayag Hydroelectric Power Project | PWRHYDINDNO | Hydro | Hydro | 400 | 2006-06-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Vyasi Hydro Power Project | PWRHYDINDNO | Hydro | Hydro | 120 | 2022-06-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Narora Atomic Power Station | PWRURNINDNO | Nuclear | Nuclear | 440 | 1991-01-01 | Uttar Pradesh | 0.85 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rajasthan Atomic Power Station | PWRURNINDNO | Nuclear | Nuclear | 1780 | 1981-04-01 | Rajasthan | 0.85 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Anta Gas Combined Cycle Gas Turbine Power Plant | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 419.33 | 1989-01-20 | Rajasthan | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Auraiya Combined Cycle Gas Turbine Power Plant | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 663.36 | 1989-03-29 | Uttar Pradesh | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dadri Combined Cycle Gas Turbine Power Plant | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 829.78 | 1992-05-01 | Uttar Pradesh | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dholpur Combined Cycle Power Station | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 330 | 2007-03-29 | Rajasthan | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Faridabad NTPC Gas Combined Cycle Gas Turbine Power Plant | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 431.59 | 1999-06-18 | Haryana | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gama Combined Cycle Power Plant | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 225 | 2016-04-25 | Uttarakhand | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | I.P. Gas Turbine Power Station | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 270 | 1986-05-14 | Delhi | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kashipur Combined Cycle Power Plant Phase I | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 225 | 2016-11-20 | Uttarakhand | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kashipur Combined Cycle Power Plant Phase II | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 214 | 2023-06-13 | Uttarakhand | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pragati-I Combined Cycle Gas Power Station | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 330.4 | 2002-03-15 | Delhi | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pragati-III Combined Cycle Gas Power Project | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 1500 | 2010-10-24 | Delhi | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ramgarh Gas Thermal Power Station | PWRNGSINDNO | Natural Gas CC | Oil & Gas | 273.5 | 1994-11-15 | Rajasthan | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ajog Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Akhara Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.1 | 2010-03-25 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Aleo II Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 4.8 | 2010-08-05 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Aleo Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2005-08-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Alwas Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 2.25 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Andhra II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2004-07-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Andhra Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 16.95 | 1987-06-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ani Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Anoopgarh Phase I Mini Hydel Station | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 1987-09-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Anoopgarh Phase II Mini Hydel Station | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 1987-12-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Awa Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2000-05-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Babail Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Babbanpur Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.25 | 2004-07-01 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bachham Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Badiyakot Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bagar Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bagipul Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 1 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bagrood Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 0.24 | 2013-07-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balh Padhar Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4 | 2008-03-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balij Ka Nallah-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3.5 | 2002-10-24 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balij Ka Nallah-III Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balij ka Nala Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baloot Fozal Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 4.6 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Balsio Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2011-02-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baltikulan Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baner II Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 6 | 2001-10-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baner III Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-11-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baner Sangam Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2016-06-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baner Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 12 | 1996-06-18 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bank Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baragaon Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 24 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Baragran Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.9 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Barewal & Jhammal Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.9 | 2010-06-12 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Barseu Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Barthi Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 1 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bazgo Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.3 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Beas Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2.25 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Behna-I Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2006-07-25 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Belij Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2007-06-14 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Belka Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhaba Augmentation Hydro Electric Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2011-07-09 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhaderwah Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhanubhura Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.3 | 2003-04-26 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhilganga Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 24 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhola Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 2.7 | 1928-12-01 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhujal Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 1 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bibiwala Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.4 | 2016-04-11 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Binwa Parai Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2007-06-07 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Binwa Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 6 | 1984-06-06 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Binwa Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Binwa-IV Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4 | 2011-12-13 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Birahi Ganga Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 7.2 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Birsalpur Mini Hydel Station | PWRHYDINDNO | Hydro | Small Hydro | 0.54 | 1998-10-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Borbalda Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.03 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bowani Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2002-08-22 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Bowani Small Hydro Project 2 | PWRHYDINDNO | Hydro | Small Hydro | 1.2 | 2012-03-20 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Brahal Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Braham Ganga Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2002-08-02 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Brahl Top Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2012-04-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Brua Hydroelectric Project | PWRHYDINDNO | Hydro | Small Hydro | 9 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | CLC India (Spentex Industries Ltd.) Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chaba Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.75 | 1919-06-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chachyot Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3.5 | 2008-02-25 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chaini Tepa Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chaksi Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 2.4 | 2012-06-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chamoli Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chandigarh Distillers and Bottlers Ltd. (CDB Group) Plant 1 | PWRHYDINDNO | Hydro | Small Hydro | 9 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chandigarh Distillers and Bottlers Ltd. (CDB Group) Plant 2 | PWRHYDINDNO | Hydro | Small Hydro | 4 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chandni Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Channuwal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.9 | 2009-09-30 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Charanwala Mini Hydel Station | PWRHYDINDNO | Hydro | Small Hydro | 1.2 | 1994-03-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chenani -III Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 7.5 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chenani-I Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 23.3 | 1971-12-01 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chenani-II Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chho Tundah Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chhoned-I Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chiludgad Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ching Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2000-05-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chirchind Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2001-05-16 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chitraura Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Choting Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Choudhary Power Projects | PWRHYDINDNO | Hydro | Small Hydro | 15 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Chupki Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 1999-11-12 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dadahur & Chakbhai Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2004-11-18 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dadupur Mini Hydel Scheme | PWRHYDINDNO | Hydro | Small Hydro | 6 | 2010-12-01 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dah Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 6 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dalla Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 1999-05-24 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Daredi Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 4 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Daudhar Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | Pre-2000 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Daudhar Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 1987-07-16 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dawaitwal, Issewal & Kailpur Combined Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.9 | 2011-07-15 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dehar II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 2005-12-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dehar Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhugli Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dikleri Small Hydo Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2009-01-12 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dogtigaun Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.02 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dolowal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.4 | 2003-04-26 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Drinidhar Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dug Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dukrund Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dukrund-I Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dunali Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2002-11-18 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Dunao Small Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 2017-07-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Durghed Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 1.1 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | GTV Engineering Ltd. Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gaj II Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gaj Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 10.5 | 1996-06-18 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gaj Top Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3.8 | 2011-06-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gaj-III Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3.6 | 2011-04-07 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Galogi Hydel Power Station | PWRHYDINDNO | Hydro | Small Hydro | 3 | 1912-11-19 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gamshali Bampa Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ganderbal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 15 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gangotri Kedarganga Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.15 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gangotri Rudragara Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.15 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gehra Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 2 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghanvi II Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 10 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghanvi Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 22.5 | 2000-12-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gharwan Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghator Top Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 4.98 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghator-I Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 2.2 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gholian Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.8 | 2009-10-04 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gogina - II Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gogina Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gogripur Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2010-08-13 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gondar Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 12 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 10 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 11 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 12 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 13 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 14 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 2 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 3 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 4 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 5 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 6 | PWRHYDINDNO | Hydro | Small Hydro | 24 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 7 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 8 | PWRHYDINDNO | Hydro | Small Hydro | 14 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 9 | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gulari Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.02 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gumma Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2000-07-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gumma-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2.5 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gunshola Hydro Power Generations Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gurahan Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 2003-05-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Gurdittiwala Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2018-03-08 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Haftal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Hamal Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2006-09-06 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Hanu Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 9 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Haripur Nallah Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2004-07-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Holi II Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 7 | 2010-10-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Holi Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2004-06-26 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Hul-II Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3.4 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Hunder Small Hydo Project | PWRHYDINDNO | Hydro | Small Hydro | 0.4 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Hurla Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2003-08-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Hysrund Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3.3 | 2012-02-24 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ichoo Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Igo-Marcellong Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Iku II Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2009-11-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Iku Khad Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Iqbal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 3.75 | 1956-12-01 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Iqu II Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-11-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Iqu Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2000-05-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Istargad Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.2 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jabbal Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2006-09-06 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jagera Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2003-07-31 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jail Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2013-08-14 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jakhana Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Janki Chutti Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.2 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jirah Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4 | 2006-07-25 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jiwa Kothari Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jogni-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2012-08-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Joiner Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Joli Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 1.4 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Jugthana Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kaachrang Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2011-05-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kachela Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kakroi Micro Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 0.3 | 1987-12-01 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kalath Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.2 | 2010-08-05 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kalhel Chatri Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 2.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kaliganga-I Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 4 | 2020-07-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kalm Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2011-11-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kanganwal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.3 | 2001-08-28 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kanolgad Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kanyali kot Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Karmi - I Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Karmi - II Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Karmi - III Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Karnah Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Karnuwasharam Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kartaul Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2.4 | 2006-07-25 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kedarnath - I Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kedarnath - II Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.2 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kesta Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2011-05-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khalara Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2.5 | 2012-05-18 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khanpur Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.1 | 2010-04-24 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khanyara Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khapugad Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.04 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khari Hydro Electric Project | PWRHYDINDNO | Hydro | Small Hydro | 3.75 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khatra Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2001-01-23 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khauli Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 12 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Khukni Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 1.4 | 2011-08-31 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Killa & Burga Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.75 | 2005-11-01 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Killar Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 0.3 | 1995-12-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Killi Behl Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 7.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kiunr Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2012-02-09 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kotagad Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3.5 | 2012-11-07 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kotlu Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.8 | 2003-05-14 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kunjar Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2017-06-23 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kunwari Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kurhed Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2004-07-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kurpan Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kurtha Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2015-01-06 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Kuwarsi Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2008-11-14 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lambagar Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.2 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lamchula Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lathi Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lehrun Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2010-07-23 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Leond Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2012-02-15 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Liti - I Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Liti - II Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lohgarh & Maholi Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2005-10-10 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lower Aleo Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2.5 | 2010-11-11 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Lower Baijnath Kuhl Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2000-12-27 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Luni Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2000-05-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Luni Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Luni-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-12-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Luni-III Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Magpie Hydel Construction Operation Industries Pvt. Ltd. Small Hydro Project 1 | PWRHYDINDNO | Hydro | Small Hydro | 10 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Magpie Hydel Construction Operation Industries Pvt. Ltd. Small Hydro Project 2 | PWRHYDINDNO | Hydro | Small Hydro | 10 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Malana Top Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2012-01-04 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Manal Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mangalam Energy Development Company Pvt. Ltd. Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Manglad Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2007-07-24 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mangrol Mini Hydel Power Station | PWRHYDINDNO | Hydro | Small Hydro | 2 | 1992-11-28 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mangrol Mini Hydel Power Station | PWRHYDINDNO | Hydro | Small Hydro | 4 | 1992-11-29 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Manihar Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2011-07-11 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Manjhal Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Manuni Small Hydro Electric Project | PWRHYDINDNO | Hydro | Small Hydro | 3.5 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Manuni-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.8 | 2010-03-06 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Marhi Mini Hydel Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2004-07-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Marpachoo Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.75 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Masli Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2002-10-28 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Maujhi II Small Hydro Electric Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2007-07-25 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Maujhi Small Hydro Electric Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2001-05-16 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Milkhet Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mohammadpur Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 9.3 | 1952-12-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mukerian Hydel Channel II | PWRHYDINDNO | Hydro | Small Hydro | 18 | 2017-05-19 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Mussapur Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 1.4 | 2011-06-17 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Nadampur Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.8 | 1985-12-14 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Nakkian Super Passage Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.3 | 2020-02-19 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Namik Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Napalchu Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Narangwal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 1999-06-07 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Neogal II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2000-05-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Neogal Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Nidampur Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.8 | Pre-2000 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Nirgajani Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Niti Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.03 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Nogli Last Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2017-04-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Nogli Stage I Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 1969-12-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | P & R Group Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 7.5 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pahalgam Mini Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pallor Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2002-09-18 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pallor-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pangi Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2004-07-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Panwi Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4 | 2001-08-03 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pathri Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 11.04 | 1956-01-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Patikari Power Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 16 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Phoola Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.6 | 2014-06-21 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pugal Phase I Mini Hydel Station | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 1994-10-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Pugal Phase II Mini Hydel Station | PWRHYDINDNO | Hydro | Small Hydro | 0.65 | 1992-07-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | RD Combined Hydro Project 1 | PWRHYDINDNO | Hydro | Small Hydro | 6 | 2016-10-23 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | RD Combined Hydro Project 2 | PWRHYDINDNO | Hydro | Small Hydro | 3.8 | 2017-01-11 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Raajratna Energy Holdings Pvt. Ltd. (REHPL) Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rakchad Small Hydro Electric Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2001-08-03 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ramgad Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Raowal & Bangsipura Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.85 | 2011-08-29 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Raskat Mini Hydel Power Project | PWRHYDINDNO | Hydro | Small Hydro | 0.8 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ratmoli Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rayil Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Right Main Canal Mahi Mini Hydel Station Phase I | PWRHYDINDNO | Hydro | Small Hydro | 0.8 | 1993-11-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Right Main Canal Mahi Mini Hydel Station Phase II | PWRHYDINDNO | Hydro | Small Hydro | 0.17 | 1991-03-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rohti Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.8 | 1989-03-21 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rongtong Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 1986-06-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ropar Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.7 | 2007-05-27 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rotan Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rukti II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2009-03-09 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Rukti Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 1980-12-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sahoke & Harigarh Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.2 | 2006-11-01 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sahu Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2003-05-14 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Saikothi Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 15 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sainj Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2004-07-26 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sal-I Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2000-06-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sal-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2007-09-11 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Salag Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 0.15 | 2000-05-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Salar Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 2003-04-26 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Salawa Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 3 | Pre-2000 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sanjak Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.26 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sarbari III Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2013-08-27 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sarbari Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2003-05-14 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sarda Energy & Minerals Ltd. Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 4.8 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sarma Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sateshwar Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sechi Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2001-08-03 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sechi-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 2008-03-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sela Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Serai Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2 | 2013-10-17 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sewa III Small Hydo Project | PWRHYDINDNO | Hydro | Small Hydro | 9 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shamshar Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 2002-11-02 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shansha Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4 | 2013-07-19 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sharan Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2.6 | 2002-05-25 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shatul Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 4.75 | 2008-04-28 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shaung Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2016-04-15 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sheetla Small Hydro Power Station | PWRHYDINDNO | Hydro | Small Hydro | 3.6 | Pre-2000 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shimla Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2011-06-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Shyang Mini Hydel Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2009-11-05 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sidhana & Baloke Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.2 | 2007-10-25 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sidhwan Bet & Mansian Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.5 | 2010-09-22 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sidhwan Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 0.7 | 2014-05-11 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Singrauli Small Hydel Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 8 | 2018-03-05 | Uttar Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Siunr Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sodhi Brothers Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Solang Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2000-08-10 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Soldan Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2012-10-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Somani Group Small Hydro Plant 1 | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Somani Group Small Hydro Plant 2 | PWRHYDINDNO | Hydro | Small Hydro | 5.4 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sorag Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sravanthi Group Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Stakna Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 4 | Pre-2000 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sudhar Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.4 | 2010-05-03 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Suil-I Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2006-09-06 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Suman Sarwari Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2002-08-28 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sumoor Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | 1993-12-01 | Ladakh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunehar Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Sup Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1 | 2001-09-19 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Surah Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 2008-10-03 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Suratgarh Mini Hydel Power Station | PWRHYDINDNO | Hydro | Small Hydro | 4 | 1992-02-01 | Rajasthan | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Swad Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2008-10-03 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Swaddi Kalan, Khudai Chak & Bharowal Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.75 | 2013-01-21 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Swati Power Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 21.5 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Talewal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.6 | 2019-12-31 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tangling Mini Hydel Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2010-12-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Taraila Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2003-05-14 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Taraila-II Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-12-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Taraila-III Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2007-12-31 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Terkiana Head Works Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.65 | 2010-08-31 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Thirot Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 4.5 | 1995-12-01 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Thuhi Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.8 | Pre-2000 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Thuhi Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.8 | 1989-03-14 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tibri & Babehali Combined Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 2.7 | 2006-10-06 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Timbi Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2000-03-30 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Titang Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 0.9 | 2000-08-17 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Toli Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Toss Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 10 | 2004-07-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tugal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 1.5 | 1999-09-08 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tugalwala Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.85 | 2019-05-29 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Tulang Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 2004-07-20 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | UREDA Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 22.5 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Ubharah Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 2.4 | 2005-06-08 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Udhanwal Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 0.65 | 2018-03-02 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Awa Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-12-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Bari Doab Canal (UBDC) Stage I | PWRHYDINDNO | Hydro | Small Hydro | 45 | 1971-08-30 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Bari Doab Canal (UBDC) Stage II | PWRHYDINDNO | Hydro | Small Hydro | 46.35 | 1989-08-06 | Punjab | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Khauli Small Hydro Power Plant | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-11-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Sindh I Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 22.6 | Pre-2000 | Jammu and Kashmir | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Taraila Small Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 5 | 2005-12-22 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Urgam Small Hydro Project | PWRHYDINDNO | Hydro | Small Hydro | 3 | 1997-12-01 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttar Bharat Hydro Power Project | PWRHYDINDNO | Hydro | Small Hydro | 25.5 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttarkashi Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.02 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Wan Micro Hydel Project | PWRHYDINDNO | Hydro | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Wanger Homte Hydro Electric Project | PWRHYDINDNO | Hydro | Small Hydro | 24.6 | Pre-2000 | Himachal Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Western Yamuna Canal Hydro Power Project Power House A | PWRHYDINDNO | Hydro | Small Hydro | 16 | 1986-05-29 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Western Yamuna Canal Hydro Power Project Power House B | PWRHYDINDNO | Hydro | Small Hydro | 16 | 1987-05-15 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Western Yamuna Canal Hydro Power Project Power House C | PWRHYDINDNO | Hydro | Small Hydro | 16 | 1989-03-27 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Western Yamuna Canal Hydro Power Project Power House D | PWRHYDINDNO | Hydro | Small Hydro | 14.4 | 2004-04-16 | Haryana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Dadra and Naga | PWRBIOINDNO | Biomass Power | Bio Power | 3.75 | Pre-2000 | Dadra and Nagar Haveli an | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Adilaxmi Industries Andhra Pradesh East Godavari 0.41 2014-04-01 | PWRBIOINDSO | Biomass Power | Bio Power | 0.41 | 2014-04-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Agri Gold Projects Ltd Andhra Pradesh Prakasam 6 2003-06-19 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2003-06-19 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ambika Sugars (Previously M/s. SREL) Tamil Nadu Cuddalore 40 | PWRBIOINDSO | Biomass Power | Bio Power | 40 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ananda Enterprises (India) Pvt Ltd Andhra Pradesh West Godavari 2 2014-04-01 | PWRBIOINDSO | Biomass Power | Bio Power | 2 | 2014-04-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Andhra Sugars Ltd. Andhra Pradesh West Godavari 7 1999-01-21 | PWRBIOINDSO | Biomass Power | Bio Power | 7 | 1999-01-21 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Arashi Hi-Tech Bio-Power Ltd. Tamil Nadu Coimbatore 1.6 | PWRBIOINDSO | Biomass Power | Bio Power | 1.6 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Aroma Biotech Pvt Ltd Andhra Pradesh West Godavari 2.2 2012-05-12 | PWRBIOINDSO | Biomass Power | Bio Power | 2.2 | 2012-05-12 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Arunachala Sugars Ltd. Tamil Nadu Tiruvannamalai 19 | PWRBIOINDSO | Biomass Power | Bio Power | 19 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Astro Energy and Bio Systems Ltd. Tamil Nadu Madurai 10 | PWRBIOINDSO | Biomass Power | Bio Power | 10 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Athani Farmers Sugar factory Ltd Karnataka Belagavi 24 01.01.2012 | PWRBIOINDSO | Biomass Power | Bio Power | 24 | 2012-01-01 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Auro Energy Ltd. Tamil Nadu Thanjavur 16 | PWRBIOINDSO | Biomass Power | Bio Power | 16 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Aurobindo Agro Energy Pvt. Ltd. Tamil Nadu Sivaganga 15 | PWRBIOINDSO | Biomass Power | Bio Power | 15 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Auromira Bio Power India (P) Ltd Tamil Nadu Tirunelveli 15 | PWRBIOINDSO | Biomass Power | Bio Power | 15 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Balaji Agro Oils Ltd Andhra Pradesh Krishna 4.5 2003-06-01 | PWRBIOINDSO | Biomass Power | Bio Power | 4.5 | 2003-06-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Balaji Boiled & Raw Rice Mill Andhra Pradesh East Godavari 0.89 2016-06-01 | PWRBIOINDSO | Biomass Power | Bio Power | 0.89 | 2016-06-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Balaji Sugars and Chemicals Pvt Ltd Karnataka Vijayapura 18 | PWRBIOINDSO | Biomass Power | Bio Power | 18 | Pre-2000 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bannari Amman Sugars Ltd. Karnataka Chamarajanagar 20 | PWRBIOINDSO | Biomass Power | Bio Power | 20 | Pre-2000 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bannari Amman Sugars Ltd. Karnataka Mysuru 36.3 10.03.2004 | PWRBIOINDSO | Biomass Power | Bio Power | 36.3 | 2004-10-03 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bannari Amman Sugars Ltd. Tamil Nadu Erode 20 | PWRBIOINDSO | Biomass Power | Bio Power | 20 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bannari Amman Sugars and Chemicals Ltd. Tamil Nadu Tiruvannamalai 28.8 | PWRBIOINDSO | Biomass Power | Bio Power | 28.8 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhagyanagar Solvents & Extractions Pvt. Ltd. Karnataka Raichur 7.5 01.09.2003 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | 2003-01-09 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bilagi Sugar Mill Ltd Karnataka Bagalkote 8 01.12.2009 | PWRBIOINDSO | Biomass Power | Bio Power | 8 | 2009-01-12 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bollineni Castings & Steels Ltd Andhra Pradesh Sri Potti Sriramulu Nellore 6 200 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2003-10-07 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Buddha Deva Power Ltd Telangana Nalgonda 6 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | Pre-2000 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | C.M.D.A., Koyambedu Veg. Market Bio-metharation plant Tamil Nadu Chennai 0.25 | PWRBIOINDSO | Biomass Power | Bio Power | 0.25 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chamundeshwari Sugars Ltd Karnataka Mandya 26 02.04.2008 | PWRBIOINDSO | Biomass Power | Bio Power | 26 | 2008-02-04 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Cheyyar Co.op Sugar Mills Tamil Nadu Tiruvannamalai 7.5 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chitra Bio Energy Ltd. Tamil Nadu Pudukkottai 7.5 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chodavaram Co-op. Sugars Ltd Andhra Pradesh Visakhapatnam 14 2003-04-06 | PWRBIOINDSO | Biomass Power | Bio Power | 14 | 2003-04-06 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Clarion Power Corp.Ltd Andhra Pradesh Prakasam 12 2004-01-23 | PWRBIOINDSO | Biomass Power | Bio Power | 12 | 2004-01-23 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Core Green Sugar & Fuels Pvt Ltd Karnataka Yadgir 24 16.10.2011 | PWRBIOINDSO | Biomass Power | Bio Power | 24 | 2011-10-16 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Coromandel Sugars Ltd Karnataka Mandya 12 06.02.2000 | PWRBIOINDSO | Biomass Power | Bio Power | 12 | 2000-06-02 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Davanagere Sugar Co. Ltd Karnataka Davangere 24 24.03.2004 | PWRBIOINDSO | Biomass Power | Bio Power | 24 | 2004-03-24 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Delta Paper Mills Ltd Andhra Pradesh West Godavari 9.9 2007-12-01 | PWRBIOINDSO | Biomass Power | Bio Power | 9.9 | 2007-12-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dhanalakshmi Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 8 12.03.2010 | PWRBIOINDSO | Biomass Power | Bio Power | 8 | 2010-12-03 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dhanalakshmi Srinivasan Sugars Pvt Ltd. Tamil Nadu Perambalur 25 | PWRBIOINDSO | Biomass Power | Bio Power | 25 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dharani Sugars & Chemical Ltd. Tamil Nadu Tiruvannamalai 15 | PWRBIOINDSO | Biomass Power | Bio Power | 15 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dharani Sugars & Chemical Ltd. Tamil Nadu Viluppuram 22 | PWRBIOINDSO | Biomass Power | Bio Power | 22 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dharwad Bio Energy Pvt. Ltd. Karnataka Dharwad 10 31.01.2013 | PWRBIOINDSO | Biomass Power | Bio Power | 10 | 2013-01-31 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Doodhganga Krishna Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 24 25.0 | PWRBIOINDSO | Biomass Power | Bio Power | 24 | 2004-03-25 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Karnataka Bagalkote 16 01.06.2008 | PWRBIOINDSO | Biomass Power | Bio Power | 16 | 2008-01-06 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Tamil Nadu Cuddalore 24.5 | PWRBIOINDSO | Biomass Power | Bio Power | 24.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Tamil Nadu Karur 22 | PWRBIOINDSO | Biomass Power | Bio Power | 22 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Tamil Nadu Pudukkottai 18 | PWRBIOINDSO | Biomass Power | Bio Power | 18 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Tamil Nadu Tiruchirappalli 18 | PWRBIOINDSO | Biomass Power | Bio Power | 18 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | ETA Power Gen.Pvt.Ltd. Tamil Nadu Virudhunagar 10 | PWRBIOINDSO | Biomass Power | Bio Power | 10 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Empee Distilleries (Pvt) Ltd. Tamil Nadu Pudukkottai 10 | PWRBIOINDSO | Biomass Power | Bio Power | 10 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Empee Power company (I) Ltd Andhra Pradesh Sri Potti Sriramulu Nellore 20 2009-1 | PWRBIOINDSO | Biomass Power | Bio Power | 20 | 2009-12-02 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Empee Sugars & Chemicals Ltd. Tamil Nadu Tirunelveli 50 | PWRBIOINDSO | Biomass Power | Bio Power | 50 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Falcon Tyres Ltd. Karnataka Mysuru 6 01.03.2009 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2009-01-03 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | G.K. Bio Energy Pvt. Ltd. Tamil Nadu Erode 1.5 | PWRBIOINDSO | Biomass Power | Bio Power | 1.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | GEM Sugars Ltd Karnataka Bagalkote 16.5 31.10.2002 | PWRBIOINDSO | Biomass Power | Bio Power | 16.5 | 2002-10-31 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | GMR Industries Ltd. Andhra Pradesh Srikakulam 16 2001-08-15 | PWRBIOINDSO | Biomass Power | Bio Power | 16 | 2001-08-15 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | GSR Sugars Pvt Ltd Telangana Nizamabad 16.1 16.05.2007 | PWRBIOINDSO | Biomass Power | Bio Power | 16.1 | 2007-05-16 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ganapati Sugars Industries Ltd Telangana Sangareddy 15 1.01.2003 | PWRBIOINDSO | Biomass Power | Bio Power | 15 | 2003-01-01 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gayatri Agro Industrial Power Ltd Telangana Nalgonda 6 28.2.2001 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2001-02-28 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gayatri Sugar Ltd Telangana Nizamabad 9 23.05.2001 | PWRBIOINDSO | Biomass Power | Bio Power | 9 | 2001-05-23 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Global Power Tech. Equipments Pvt.Ltd. Tamil Nadu Tiruvannamalai 7.5 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Godavari Bio Refineries Ltd Karnataka Bagalkote 21.6 07.01.2011 | PWRBIOINDSO | Biomass Power | Bio Power | 21.6 | 2011-07-01 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Godavari Bio Refineries Ltd Karnataka Bagalkote 24 01.09.2002 | PWRBIOINDSO | Biomass Power | Bio Power | 24 | 2002-01-09 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gokak SC & ST Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 14 24.12.200 | PWRBIOINDSO | Biomass Power | Bio Power | 14 | 2009-12-24 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gowthami Bio Energies Ltd Telangana Khammam 6 23.7.2001 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2001-07-23 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gowthami Solvent Oil Ltd Andhra Pradesh West Godavari 2.75 1996-03-31 | PWRBIOINDSO | Biomass Power | Bio Power | 2.75 | 1996-03-31 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Greenko Energies Pvt Ltd Andhra Pradesh Guntur 6 2002-07-19 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2002-07-19 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Greenko Energies Pvt Ltd Andhra Pradesh YSR Kadapa 6 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | Pre-2000 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gujarat Ambuja Exports Ltd (Biomass based Cogen) Karnataka Haveri 2.44 21.01.201 | PWRBIOINDSO | Biomass Power | Bio Power | 2.44 | 2013-01-21 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gujarat Ambuja Exports Ltd Karnataka Haveri 2.85 01.04.2014 | PWRBIOINDSO | Biomass Power | Bio Power | 2.85 | 2014-01-04 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | HCL Agro Power Ltd Andhra Pradesh Krishna 6 2000-10-24 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2000-10-24 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hassan Biomass Power Co. Pvt. Ltd. Karnataka Hassan 8 17.03.2003 | PWRBIOINDSO | Biomass Power | Bio Power | 8 | 2003-03-17 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Haveri Bio Energy Pvt. Ltd. Karnataka Haveri 10 01.04.2014 | PWRBIOINDSO | Biomass Power | Bio Power | 10 | 2014-01-04 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hiranyakeshi Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 26 15.11.2008 | PWRBIOINDSO | Biomass Power | Bio Power | 26 | 2008-11-15 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hiranyakeshi Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 26 27.08.2011 | PWRBIOINDSO | Biomass Power | Bio Power | 26 | 2011-08-27 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | IOT Mabagas Ltd. Tamil Nadu N.A. 2 | PWRBIOINDSO | Biomass Power | Bio Power | 2 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ind-Barath Energies Ltd Telangana Nalgonda 6 6.10.2000 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2000-06-10 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Indian Cane Power Ltd Karnataka Bagalkote 28 17.05.2008 | PWRBIOINDSO | Biomass Power | Bio Power | 28 | 2008-05-17 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Indian Sugar Manufacturing Co. Ltd Karnataka Vijayapura 19.5 24.02.2013 | PWRBIOINDSO | Biomass Power | Bio Power | 19.5 | 2013-02-24 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Indra Power Energies Ltd. Karnataka Koppal 6 13.02.2004 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2004-02-13 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Indur Green Power Pvt Ltd Telangana Nizamabad 6 15.2.2003 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2003-02-15 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jamakhandi Sugars Ltd Karnataka Bagalkote 12 08.02.2002 | PWRBIOINDSO | Biomass Power | Bio Power | 12 | 2002-08-02 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jamakhandi Sugars Ltd Karnataka Bagalkote 30 27.02.2012 | PWRBIOINDSO | Biomass Power | Bio Power | 30 | 2012-02-27 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jeypore Sugars Company Ltd (Unit II) Andhra Pradesh West Godavari 16.8 2003-10-1 | PWRBIOINDSO | Biomass Power | Bio Power | 16.8 | 2003-10-19 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jeypore Sugars Company Ltd Andhra Pradesh West Godavari 12 2003-10-19 | PWRBIOINDSO | Biomass Power | Bio Power | 12 | 2003-10-19 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jocil Limited Andhra Pradesh Guntur 6 2001-03-23 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2001-03-23 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jyothi Bio Energy Ltd Andhra Pradesh Prakasam 4.5 2000-11-17 | PWRBIOINDSO | Biomass Power | Bio Power | 4.5 | 2000-11-17 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jyothi Bio Energy Ltd Andhra Pradesh Prakasam 6 2003-11-14 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2003-11-14 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | KCP Sugar Industries & Corp.Ltd Andhra Pradesh Krishna 12 2005-12-26 | PWRBIOINDSO | Biomass Power | Bio Power | 12 | 2005-12-26 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | KCP Sugar Industries & Corp.Ltd Andhra Pradesh Krishna 5 2005-12-26 | PWRBIOINDSO | Biomass Power | Bio Power | 5 | 2005-12-26 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | KPR Sugar Mills Pvt Ltd Karnataka Vijayapura 30 23.11.2012 | PWRBIOINDSO | Biomass Power | Bio Power | 30 | 2012-11-23 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kakatiya Cement Sugars and Industries Ltd Telangana Khammam 15 12.04.2002 | PWRBIOINDSO | Biomass Power | Bio Power | 15 | 2002-12-04 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kedarnath Sugar and Agro Chemicals Ltd Karnataka Bagalkote 18 02.03.2010 | PWRBIOINDSO | Biomass Power | Bio Power | 18 | 2010-02-03 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Koganti Power Pvt. Ltd. Karnataka Raichur 7.5 26.11.2005 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | 2005-11-26 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Konark Power Ltd. Karnataka Tumakuru 73 05.05.2005 | PWRBIOINDSO | Biomass Power | Bio Power | 7.03 | 2005-05-05 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Koppal Green Power Ltd. Karnataka Koppal 6 01.01.2005 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2005-01-01 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kothari Sugars & Chemicals Ltd. Tamil Nadu Perambalur 12 | PWRBIOINDSO | Biomass Power | Bio Power | 12 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kothari Sugars & Chemicals Ltd. Tamil Nadu Perambalur 22 | PWRBIOINDSO | Biomass Power | Bio Power | 22 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Krishna Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 12 08.02.2013 | PWRBIOINDSO | Biomass Power | Bio Power | 12 | 2013-08-02 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Krishnaveni Sugars Ltd Andhra Pradesh West Godavari 28 2003-10-19 | PWRBIOINDSO | Biomass Power | Bio Power | 28 | 2003-10-19 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Krishnaveni Sugars Ltd Telangana Mahabubnagar 14 | PWRBIOINDSO | Biomass Power | Bio Power | 14 | Pre-2000 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lalitha Enterprises Andhra Pradesh East Godavari 0.5 2003-08-15 | PWRBIOINDSO | Biomass Power | Bio Power | 0.5 | 2003-08-15 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | M.R.K.Co.op Sugar Mills Tamil Nadu Cuddalore 7.5 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | MGRRice Industries Andhra Pradesh East Godavari 0.89 2013-07-01 | PWRBIOINDSO | Biomass Power | Bio Power | 0.89 | 2013-07-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Madras Sugars & Chemicals Ltd. Tamil Nadu Tirunelveli 25 | PWRBIOINDSO | Biomass Power | Bio Power | 25 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mahatma Gandhi Sahakari Sakkare Karkhane Niyamita Karnataka Bidar 13 04.07.2009 | PWRBIOINDSO | Biomass Power | Bio Power | 13 | 2009-04-07 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Malavalli Power Plant Pvt. Ltd. Karnataka Mandya 4.5 19.07.2001 | PWRBIOINDSO | Biomass Power | Bio Power | 4.5 | 2001-07-19 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Manali Petrochemicals Ltd. Tamil Nadu Thiruvallur 4.7 | PWRBIOINDSO | Biomass Power | Bio Power | 4.7 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Manali Sugar Ltd Karnataka Vijayapura 15 20.04.2013 | PWRBIOINDSO | Biomass Power | Bio Power | 15 | 2013-04-20 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Manchikonda Bio energy Pvt. Ltd Karnataka Raichur 6 01.03.2016 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2016-01-03 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mata Energy Ltd Telangana Nalgonda 6 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | Pre-2000 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Matix Power (p) Ltd Andhra Pradesh Guntur 4.5 2001-08-08 | PWRBIOINDSO | Biomass Power | Bio Power | 4.5 | 2001-08-08 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Matrix Agro Pvt Ltd Karnataka Kalaburagi 6 09.12.2016 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2016-09-12 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mohan Breweries & Distillaries Ltd Tamil Nadu Kancheepuram 18 | PWRBIOINDSO | Biomass Power | Bio Power | 18 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | NCS Sugars ltd. Andhra Pradesh Vizianagaram 20 2007-06-15 | PWRBIOINDSO | Biomass Power | Bio Power | 20 | 2007-06-15 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | NSL Sugars Ltd Karnataka Ballari 28 30.09.2011 | PWRBIOINDSO | Biomass Power | Bio Power | 28 | 2011-09-30 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | NSL Sugars Ltd Karnataka Kalaburagi 34 12.04.2012 | PWRBIOINDSO | Biomass Power | Bio Power | 34 | 2012-12-04 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | NSL Sugars Ltd Karnataka Mandya 26 30.06.2004 | PWRBIOINDSO | Biomass Power | Bio Power | 26 | 2004-06-30 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Naga Hanuman Solvent Oils Pvt Ltd Andhra Pradesh West Godavari 1.2 2013-12-01 | PWRBIOINDSO | Biomass Power | Bio Power | 1.2 | 2013-12-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Green Power Ltd / My Home Power Ltd Telangana Medak 9 5.2.2002 | PWRBIOINDSO | Biomass Power | Bio Power | 9 | 2002-05-02 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nandi Sahakari Sakkare Karkhane Niyamita Karnataka Vijayapura 21 31.03.2006 | PWRBIOINDSO | Biomass Power | Bio Power | 21 | 2006-03-31 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Naranja Sahakari Sakkare Karkhane Niyamita Karnataka Bidar 14 01.05.2005 | PWRBIOINDSO | Biomass Power | Bio Power | 14 | 2005-01-05 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nava Bharat Agro Products Ltd Andhra Pradesh West Godavari 0.95 2014-09-12 | PWRBIOINDSO | Biomass Power | Bio Power | 0.95 | 2014-09-12 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nava Bharat Agro Products Ltd Andhra Pradesh West Godavari 1 2015-03-15 | PWRBIOINDSO | Biomass Power | Bio Power | 1 | 2015-03-15 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nava Bharat Ventures Ltd. Andhra Pradesh East Godavari 9 2005-11-23 | PWRBIOINDSO | Biomass Power | Bio Power | 9 | 2005-11-23 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nava Bharath Ltd Andhra Pradesh West Godavari 6 2017-07-01 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2017-07-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nirani Sugars Ltd Karnataka Bagalkote 14 05.03.2010 | PWRBIOINDSO | Biomass Power | Bio Power | 14 | 2010-05-03 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nirani Sugars Ltd Karnataka Bagalkote 16 13.06.2008 | PWRBIOINDSO | Biomass Power | Bio Power | 16 | 2008-06-13 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nirani Sugars Ltd Karnataka Bagalkote 42 18.06.2011 | PWRBIOINDSO | Biomass Power | Bio Power | 42 | 2011-06-18 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nizam Deccan Sugar Ltd Telangana Nizamabad 20 17.01.2006 | PWRBIOINDSO | Biomass Power | Bio Power | 20 | 2006-01-17 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | OM Shakthi Reenergies Ltd Andhra Pradesh Chittoor 6 2004-01-24 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2004-01-24 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Orient Green Power Ltd. Tamil Nadu Coimbatore 10 | PWRBIOINDSO | Biomass Power | Bio Power | 10 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) (Waste to Energy) Andhra Pradesh N.A. 53.16 | PWRBIOINDSO | Biomass Power | Bio Power | 53.16 | Pre-2000 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) (Waste to Energy) Karnataka N.A. 1 | PWRBIOINDSO | Biomass Power | Bio Power | 1 | Pre-2000 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) (Waste to Energy) Tamil Nadu N.A. 6.4 | PWRBIOINDSO | Biomass Power | Bio Power | 6.4 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) (Waste to Energy) Telangana N.A. 45.8 | PWRBIOINDSO | Biomass Power | Bio Power | 45.8 | Pre-2000 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Biomass & bagasse based cogen.] Karnataka N.A. | PWRBIOINDSO | Biomass Power | Bio Power | 543.39 | Pre-2000 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Biomass & bagasse based cogen.] Tamil Nadu N.A | PWRBIOINDSO | Biomass Power | Bio Power | 138.2 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Andhra Pradesh N.A. | PWRBIOINDSO | Biomass Power | Bio Power | 48.02 | Pre-2000 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Karnataka N.A. 20.2 | PWRBIOINDSO | Biomass Power | Bio Power | 20.2 | Pre-2000 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Kerala N.A. 2.27 | PWRBIOINDSO | Biomass Power | Bio Power | 2.27 | Pre-2000 | Kerala | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Tamil Nadu N.A. 43.5 | PWRBIOINDSO | Biomass Power | Bio Power | 43.55 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Telangana N.A. 3.3 | PWRBIOINDSO | Biomass Power | Bio Power | 3.3 | Pre-2000 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Andhra Pradesh N.A | PWRBIOINDSO | Biomass Power | Bio Power | 49.19 | Pre-2000 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Karnataka N.A. 25. | PWRBIOINDSO | Biomass Power | Bio Power | 25.94 | Pre-2000 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Kerala N.A. 0.23 | PWRBIOINDSO | Biomass Power | Bio Power | 0.23 | Pre-2000 | Kerala | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Tamil Nadu N.A. 27 | PWRBIOINDSO | Biomass Power | Bio Power | 27.57 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Telangana N.A. 14. | PWRBIOINDSO | Biomass Power | Bio Power | 14.47 | Pre-2000 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pallavi Enterprises Andhra Pradesh Krishna 2.5 2010-02-10 | PWRBIOINDSO | Biomass Power | Bio Power | 2.5 | 2010-02-10 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Parrys Sugar Industries Ltd Karnataka Uttara Kannada 24 02.06.2008 | PWRBIOINDSO | Biomass Power | Bio Power | 24 | 2008-02-06 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Perpetual Energy Systems Ltd. Andhra Pradesh Vizianagaram 6 2003-03-23 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2003-03-23 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ponni Sugars Limited Tamil Nadu Erode 19 | PWRBIOINDSO | Biomass Power | Bio Power | 19 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Power Onicks Ltd. Karnataka Ballari 6 05.01.2005 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2005-05-01 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Prabhulingeshwara Sugar Works Ltd Karnataka Bagalkote 38.5 14.11.2000 | PWRBIOINDSO | Biomass Power | Bio Power | 38.5 | 2000-11-14 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Prathyusha Power Pvt. Ltd. Tamil Nadu Tirunelveli 10 | PWRBIOINDSO | Biomass Power | Bio Power | 10 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | RK Power Gen Pvt. Ltd. Karnataka Chitradurga 20 01.01.2004 | PWRBIOINDSO | Biomass Power | Bio Power | 20 | 2004-01-01 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Raichur Bio Energies Pvt. Ltd. Karnataka Raichur 9 04.02.2016 | PWRBIOINDSO | Biomass Power | Bio Power | 9 | 2016-04-02 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajashree Sugars & Chemicals Ltd. Tamil Nadu Theni 12 | PWRBIOINDSO | Biomass Power | Bio Power | 12 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajashree Sugars & Chemicals Ltd. Tamil Nadu Viluppuram 20 | PWRBIOINDSO | Biomass Power | Bio Power | 20 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajashree Sugars & Chemicals Ltd. Tamil Nadu Viluppuram 22 | PWRBIOINDSO | Biomass Power | Bio Power | 22 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajkumar Impex(P) Ltd. Tamil Nadu Thoothukkudi 6 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ravikiran Power Project Pvt. Ltd. Karnataka Koppal 7.5 01.06.2005 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | 2005-01-06 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rayalaseema Green Energy Ltd Andhra Pradesh Kurnool 5.5 2001-02-14 | PWRBIOINDSO | Biomass Power | Bio Power | 5.5 | 2001-02-14 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Raytar Sahakari Sakkare Karkhane Niyamita Karnataka Bagalkote 12.5 08.12.2001 | PWRBIOINDSO | Biomass Power | Bio Power | 12.5 | 2001-08-12 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Renuka Textiles Limited Tamil Nadu Theni 4.5 | PWRBIOINDSO | Biomass Power | Bio Power | 4.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rithwik Energy Systems Ltd Andhra Pradesh Chittoor 6 2002-08-28 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2002-08-28 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rithwik Power Projects Ltd Telangana Khammam 6 13.11.2002 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2002-11-13 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Roshni Power Tech Ltd Andhra Pradesh Krishna 6 2001-08-30 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2001-08-30 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | S.V Sugar Mills Ltd. Tamil Nadu Kancheepuram 45 | PWRBIOINDSO | Biomass Power | Bio Power | 45 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | SLS Power Ltd Andhra Pradesh Sri Potti Sriramulu Nellore 6 2001-08-30 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2001-08-30 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Saastha Energy(P) Ltd Tamil Nadu N.A. 2 | PWRBIOINDSO | Biomass Power | Bio Power | 2 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sakti Sugars Ltd. Tamil Nadu Erode 24.5 | PWRBIOINDSO | Biomass Power | Bio Power | 24.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sakti Sugars Ltd. Tamil Nadu Sivaganga 35 | PWRBIOINDSO | Biomass Power | Bio Power | 35 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Samsons Distilleries Pvt. Ltd. Karnataka Davangere 2 18.06.2003 | PWRBIOINDSO | Biomass Power | Bio Power | 2 | 2003-06-18 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Saritha Sugars Ltd Andhra Pradesh Sri Potti Sriramulu Nellore 6 01.04.2001 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2001-01-04 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Saro Power and Infrastructures Ltd Telangana Mahabubnagar 6 24.4.2003 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2003-04-24 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Satish Sugars Ltd Karnataka Belagavi 31 11.05.2012 | PWRBIOINDSO | Biomass Power | Bio Power | 31 | 2012-11-05 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Satyakala Power Projects (P) Ltd Andhra Pradesh Krishna 4 2001-11-02 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2001-11-02 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Satyamaharshi Power Corpn Ltd Andhra Pradesh Guntur 6 2004-07-13 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2004-07-13 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Seven Hills Papers (P) Ltd Andhra Pradesh East Godavari 1.2 2009-02-25 | PWRBIOINDSO | Biomass Power | Bio Power | 1.2 | 2009-02-25 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shakti Sugars Ltd. Tamil Nadu Erode 32 | PWRBIOINDSO | Biomass Power | Bio Power | 32 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shalivahana Green Energy Ltd Telangana Adilabad 6 1.12.2002 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2002-01-12 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shamanur Sugars Ltd Karnataka Davangere 22 13.08.1999 | PWRBIOINDSO | Biomass Power | Bio Power | 22 | 1999-08-13 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shiraguppi Sugar Works Ltd Karnataka Belagavi 14 01.05.2013 | PWRBIOINDSO | Biomass Power | Bio Power | 14 | 2013-01-05 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivasagar Sugar & Agro Products Ltd Karnataka Belagavi 8 30.06.2013 | PWRBIOINDSO | Biomass Power | Bio Power | 8 | 2013-06-30 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivashakthi Sugars Ltd Karnataka Belagavi 20 01.06.2013 | PWRBIOINDSO | Biomass Power | Bio Power | 20 | 2013-01-06 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Gowthamee Rice Industries (P) Limited Andhra Pradesh East Godavari 0.58 20 | PWRBIOINDSO | Biomass Power | Bio Power | 0.58 | 2014-02-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Gowthamee Rice Industries (P) Limited Andhra Pradesh East Godavari 0.88 20 | PWRBIOINDSO | Biomass Power | Bio Power | 0.88 | 2016-06-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Papers Ltd Andhra Pradesh East Godavari 4 2003-02-23 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2003-02-23 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Renuka Sugars Ltd Karnataka Belagavi 30 01.12.2012 | PWRBIOINDSO | Biomass Power | Bio Power | 30 | 2012-01-12 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Renuka Sugars Ltd Karnataka Belagavi 38 07.03.2000 | PWRBIOINDSO | Biomass Power | Bio Power | 38 | 2000-07-03 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Renuka Sugars Ltd Karnataka Belagavi 38 11.01.2012 | PWRBIOINDSO | Biomass Power | Bio Power | 38 | 2012-11-01 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Renuka Sugars Ltd Karnataka Kalaburagi 25 01.12.2009 | PWRBIOINDSO | Biomass Power | Bio Power | 25 | 2009-01-12 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Vani Sugars & Industries Ltd Andhra Pradesh Chittoor 9 2003-08-08 | PWRBIOINDSO | Biomass Power | Bio Power | 9 | 2003-08-08 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shriraam City Union Finance Ltd. Tamil Nadu Thanjavur 7.5 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shriram Investments Ltd. Tamil Nadu Dindigul 7.5 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sindhura Paper Pvt Ltd Andhra Pradesh West Godavari 3 2017-07-01 | PWRBIOINDSO | Biomass Power | Bio Power | 3 | 2017-07-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Singaraya Hills Green Power Genco (p) Ltd. Andhra Pradesh Prakasam 8 2008-07-13 | PWRBIOINDSO | Biomass Power | Bio Power | 8 | 2008-07-13 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sirius Overseas Pvt. Ltd Andhra Pradesh East Godavari 9 2009-01-04 | PWRBIOINDSO | Biomass Power | Bio Power | 9 | 2009-01-04 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Soubhagya Lakshmi Sugars Ltd Karnataka Belagavi 18 01.12.2013 | PWRBIOINDSO | Biomass Power | Bio Power | 18 | 2013-01-12 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | South India Paper Mills Ltd Karnataka Belagavi 7.8 19.05.2001 | PWRBIOINDSO | Biomass Power | Bio Power | 7.8 | 2001-05-19 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sree Godavari Kraft Paper (p) ltd Andhra Pradesh West Godavari 3 2008-11-15 | PWRBIOINDSO | Biomass Power | Bio Power | 3 | 2008-11-15 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Gowthami Rice Industries Ltd Andhra Pradesh East Godavari 0.75 2009-03-25 | PWRBIOINDSO | Biomass Power | Bio Power | 0.75 | 2009-03-25 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Kalyani Agro Products & Industries Limited Andhra Pradesh West Godavari 4 20 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2002-12-03 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Lalitha Enterprises Industries Ltd (Unit II) Andhra Pradesh East Godavari 4. | PWRBIOINDSO | Biomass Power | Bio Power | 4.7 | 2009-02-25 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Murali Mohana Para Boiled Rice Mill Andhra Pradesh East Godavari 0.65 2003-0 | PWRBIOINDSO | Biomass Power | Bio Power | 0.65 | 2003-08-26 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Ramadas Paper Boards (P) Ltd Andhra Pradesh East Godavari 4 2006-06-27 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2006-06-27 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Sarvaraya Sugars Ltd Andhra Pradesh East Godavari 19.65 2008-12-25 | PWRBIOINDSO | Biomass Power | Bio Power | 19.65 | 2008-12-25 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Satyanarayana Raw & Boiled Rice (P) Ltd Andhra Pradesh West Godavari 0.75 20 | PWRBIOINDSO | Biomass Power | Bio Power | 0.75 | 2008-03-31 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sripathi Paper & Board (P) Ltd Tamil Nadu Virudhunagar 4.95 09.03.2011 | PWRBIOINDSO | Biomass Power | Bio Power | 4.95 | 2011-09-03 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Subashri Bio Energy (P) Ltd. Tamil Nadu Namakkal 2.5 | PWRBIOINDSO | Biomass Power | Bio Power | 2.5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Subramania Siva Co-op Sugar Mills Tamil Nadu Dharmapuri 5 | PWRBIOINDSO | Biomass Power | Bio Power | 5 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Suchand Power Gen.(p) Ltd Andhra Pradesh Kurnool 6 2002-11-28 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2002-11-28 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sudha Agro Oil & Chemicals Industries Ltd Andhra Pradesh East Godavari 4 2001-12 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2001-12-27 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sudulagunta Sugars Ltd Andhra Pradesh Chittoor 8 1999-06-09 | PWRBIOINDSO | Biomass Power | Bio Power | 8 | 1999-06-09 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Surya Chandra Paper Mills Ltd Andhra Pradesh East Godavari 3 2007-11-27 | PWRBIOINDSO | Biomass Power | Bio Power | 3 | 2007-11-27 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Surya Teja Power Projects Pvt Ltd Telangana Mahabubnagar 6 31.03.2007 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2007-03-31 | Telangana | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Synergy Sakthi Renewable energy Ltd. Tamil Nadu Dharmapuri 10 | PWRBIOINDSO | Biomass Power | Bio Power | 10 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | TCP Ltd. Tamil Nadu Sivaganga 9 | PWRBIOINDSO | Biomass Power | Bio Power | 9 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Terra Energy Ltd. Tamil Nadu Cuddalore 18.68 | PWRBIOINDSO | Biomass Power | Bio Power | 18.68 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Terra Energy Ltd. Tamil Nadu Thanjavur 28.42 | PWRBIOINDSO | Biomass Power | Bio Power | 28.42 | Pre-2000 | Tamil Nadu | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | The Etikoppaka Co.op Agrl. & Industrial Society Ltd. Andhra Pradesh Visakhapatna | PWRBIOINDSO | Biomass Power | Bio Power | 4.5 | 2001-03-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ugar Sugars Works Ltd Karnataka Belagavi 44 28.05.1998 | PWRBIOINDSO | Biomass Power | Bio Power | 44 | 1998-05-28 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ugar Sugars Works Ltd Karnataka Kalaburagi 15 28.10.2010 | PWRBIOINDSO | Biomass Power | Bio Power | 15 | 2010-10-28 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vamshi Industries Ltd. Andhra Pradesh East Godavari 4 2001-04-20 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2001-04-20 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Varam Power Projects (P) Ltd Andhra Pradesh Srikakulam 6 2001-12-01 | PWRBIOINDSO | Biomass Power | Bio Power | 6 | 2001-12-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Veda Bio Fuel Pvt Ltd Andhra Pradesh Vizianagaram 3 2016-03-15 | PWRBIOINDSO | Biomass Power | Bio Power | 3 | 2016-03-15 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Veeraiah Non-Conventional Power Projects Ltd. Andhra Pradesh Krishna 4 2002-10-2 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2002-10-26 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Velagapudi Power Generation Ltd Andhra Pradesh Guntur 4 2006-11-13 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2006-11-13 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Venkatarama Oil Industries Limited. Andhra Pradesh East Godavari 1.3 2015-08-01 | PWRBIOINDSO | Biomass Power | Bio Power | 1.3 | 2015-08-01 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Venkateshwara Power Projects Ltd Karnataka Belagavi 15 03.11.2004 | PWRBIOINDSO | Biomass Power | Bio Power | 15 | 2004-03-11 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vijaya Agro Products (p) Ltd Andhra Pradesh Krishna 4 2001-12-24 | PWRBIOINDSO | Biomass Power | Bio Power | 4 | 2001-12-24 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vijaynagar Bio- Tech Ltd Andhra Pradesh Vizianagaram 1.2 2013-02-20 | PWRBIOINDSO | Biomass Power | Bio Power | 1.2 | 2013-02-20 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vijaynagar Sugars Ltd Karnataka Belagavi 35.5 04.03.2010 | PWRBIOINDSO | Biomass Power | Bio Power | 35.5 | 2010-04-03 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vishnu Vidyuth India Ltd Andhra Pradesh Visakhapatnam 7.5 2013-01-11 | PWRBIOINDSO | Biomass Power | Bio Power | 7.5 | 2013-01-11 | Andhra Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vishwanath Sugars Ltd Karnataka Belagavi 14 06.01.2006 | PWRBIOINDSO | Biomass Power | Bio Power | 14 | 2006-06-01 | Karnataka | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bellary TPS | PWRCOAINDSO | Coal Steam | Coal | 1700 | 2007-12-01 | Karnataka | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadradri TPP | PWRCOAINDSO | Coal Steam | Coal | 1080 | 2020-03-01 | Telangana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Damodaram Sanjeevaiah or Krishnapatnam TPP | PWRCOAINDSO | Coal Steam | Coal | 2400 | 2014-08-28 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | ITPCL or Cuddalore TPP | PWRCOAINDSO | Coal Steam | Coal | 1200 | 2015-09-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kakatiya TPS | PWRCOAINDSO | Coal Steam | Coal | 1100 | 2010-05-01 | Telangana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kothagudem TPS | PWRCOAINDSO | Coal Steam | Coal | 1800 | 1997-03-01 | Telangana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kudgi STPP | PWRCOAINDSO | Coal Steam | Coal | 2400 | 2016-12-25 | Karnataka | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mettur TPS | PWRCOAINDSO | Coal Steam | Coal | 1440 | 1987-01-07 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Muthiara TPP | PWRCOAINDSO | Coal Steam | Coal | 1200 | 2014-12-02 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli (EXT) TPS I | PWRCOAINDSO | Coal Steam | Coal | 420 | 2002-10-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli (EXT) TPS II | PWRCOAINDSO | Coal Steam | Coal | 500 | 2012-02-04 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli (New) TPP /Neyveli Extension | PWRCOAINDSO | Coal Steam | Coal | 1000 | 2019-12-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli TPS (Z) | PWRCOAINDSO | Coal Steam | Coal | 250 | 2002-10-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli TPS II | PWRCOAINDSO | Coal Steam | Coal | 1470 | 1986-03-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | North Chennai TPS | PWRCOAINDSO | Coal Steam | Coal | 1830 | 1994-10-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | OPG Power Generation Private Ltd. | PWRCOAINDSO | Coal Steam | Coal | 414 | 2024-01-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Raichur TPS | PWRCOAINDSO | Coal Steam | Coal | 1720 | 1985-03-01 | Karnataka | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ramagudem -B TPS | PWRCOAINDSO | Coal Steam | Coal | 62.5 | 1971-10-01 | Telangana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ramagundam STPP/Telangana Phase I | PWRCOAINDSO | Coal Steam | Coal | 1600 | 2023-09-09 | Telangana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ramagundam STPS | PWRCOAINDSO | Coal Steam | Coal | 2600 | 1983-11-01 | Telangana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rayalaseema TPS | PWRCOAINDSO | Coal Steam | Coal | 1650 | 1994-03-01 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sembcorp Gayatri Power Ltd. Power Project | PWRCOAINDSO | Coal Steam | Coal | 1320 | 2016-11-01 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Simhadri TPP | PWRCOAINDSO | Coal Steam | Coal | 2000 | 2002-02-01 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Simhapuri TPS | PWRCOAINDSO | Coal Steam | Coal | 600 | 2012-03-01 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Singareni TPP | PWRCOAINDSO | Coal Steam | Coal | 1200 | 2016-03-13 | Telangana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | TCP Limited | PWRCOAINDSO | Coal Steam | Coal | 63.5 | 2024-12-23 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Thamminapatnam TPS | PWRCOAINDSO | Coal Steam | Coal | 1000 | 2012-10-01 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Thermal Powertech Corporation Ltd/ Painampuram/Muthukur Mandal | PWRCOAINDSO | Coal Steam | Coal | 1320 | 2015-02-07 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Torangallu TPS SBU | PWRCOAINDSO | Coal Steam | Coal | 860 | 1999-05-01 | Karnataka | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin (P) TPP | PWRCOAINDSO | Coal Steam | Coal | 300 | 2013-01-31 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin Joint Venture | PWRCOAINDSO | Coal Steam | Coal | 1000 | 2015-03-10 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin TPS | PWRCOAINDSO | Coal Steam | Coal | 1050 | 1979-07-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin Thermal Power Plant | PWRCOAINDSO | Coal Steam | Coal | 525 | 2021-12-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Udupi TPP | PWRCOAINDSO | Coal Steam | Coal | 1200 | 2010-07-01 | Karnataka | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vallur TPP | PWRCOAINDSO | Coal Steam | Coal | 1500 | 2012-03-01 | Tamil Nadu | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vijayawada or Dr. Narla Tata Rao TPS | PWRCOAINDSO | Coal Steam | Coal | 2560 | 1979-11-01 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vizag or Hinduja Power TPP | PWRCOAINDSO | Coal Steam | Coal | 1040 | 2015-12-01 | Andhra Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Yadadri Thermal Power Station | PWRCOAINDSO | Coal Steam | Coal | 1600 | 2025-01-25 | Telangana | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Yermarus TPP | PWRCOAINDSO | Coal Steam | Coal | 1600 | 2016-03-29 | Karnataka | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Aliyar Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 60 | 1970-03-21 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Almatti Dam Power House | PWRHYDINDSO | Hydro | Hydro | 290 | 2004-03-26 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadra Left Bank Canal Power House | PWRHYDINDSO | Hydro | Hydro | 26 | 1965-03-29 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Kattalai Barrage I Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 30 | 2006-07-04 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Kattalai Barrage II Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 30 | 2013-08-27 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Kattalai Barrage III Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 30 | 2012-06-28 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gerusoppa (Sharavathy Tail Race) Power House | PWRHYDINDSO | Hydro | Hydro | 240 | 2001-02-20 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ghat Prabha Dam Power House | PWRHYDINDSO | Hydro | Hydro | 32 | 1992-06-14 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hampi Canal Power House | PWRHYDINDSO | Hydro | Hydro | 36 | 1958-01-02 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Idamalayar Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 75 | 1987-02-03 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Idukki Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 780 | 1976-02-12 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jog (Mahatma Gandhi) Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 139.2 | 1949-08-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kadmparai Power House | PWRHYDINDSO | Hydro | Hydro | 400 | 1987-10-17 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kadra Dam Power House | PWRHYDINDSO | Hydro | Hydro | 150 | 1997-06-02 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kakkad Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 50 | 2012-02-16 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kalinadi Nagjhari Power House | PWRHYDINDSO | Hydro | Hydro | 900 | 1979-08-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kalinadi Nagjhari Supa Dam Power House | PWRHYDINDSO | Hydro | Hydro | 100 | 1985-08-23 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kodasali Dam Power House | PWRHYDINDSO | Hydro | Hydro | 120 | 1998-06-20 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kodayar I & II Power House | PWRHYDINDSO | Hydro | Hydro | 100 | 1970-12-09 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kundah I to V Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 555 | 1960-07-08 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kuttiyadi Hydroelectric Old, Additional & Extension Power House | PWRHYDINDSO | Hydro | Hydro | 225 | 1972-09-11 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lingnamakki Dam Power House | PWRHYDINDSO | Hydro | Hydro | 55 | 1979-08-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Jurala Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 240 | 2015-09-30 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Mettur I to IV Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 120 | 1988-01-04 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Periyar Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 180 | 1997-09-27 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Sileru Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 460 | 1976-03-28 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mettur Dam Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 50 | 1937-06-13 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mettur Tunnel | PWRHYDINDSO | Hydro | Hydro | 200 | 1965-08-16 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Moyar Power House | PWRHYDINDSO | Hydro | Hydro | 40 | 1952-04-10 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Munirabad Power House | PWRHYDINDSO | Hydro | Hydro | 28 | 1962-01-19 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Sagar (N.J.Sagar) Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 815.6 | 1978-03-07 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Sagar Left Bank Canal Power House (N.J.Sagar LBC) | PWRHYDINDSO | Hydro | Hydro | 60 | 1983-06-05 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Sagar Right Bank Canal Power House (N.J.Sagar RBC) | PWRHYDINDSO | Hydro | Hydro | 90 | 1983-02-24 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Sagar Tail Pond Dam (N.J.Sagar TPD) | PWRHYDINDSO | Hydro | Hydro | 50 | 2017-01-28 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Neriamangalam Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 52.65 | 1961-01-27 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pallivasal Hydro Power Project | PWRHYDINDSO | Hydro | Hydro | 60 | 2025-03-01 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pallivasal Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 37.5 | 1948-02-02 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Panniar Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 30 | 1963-12-29 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Papanasam Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 32 | 1944-07-08 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Parson's Valley Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 30 | 2000-06-22 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 168 | 1958-10-12 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pinnapuram (Standalone Pumped Storage ) Hydro Power Project | PWRHYDINDSO | Hydro | Hydro | 1680 | 2025-06-01 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pochampad (Sriram Sagar Project) Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 36 | 1987-02-20 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Poringalkuthu Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 36 | 1957-03-06 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Priyadarshni Jurala Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 234 | 2008-03-28 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pulichinthala Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 120 | 2016-09-25 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pykara Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 59.2 | 1932-06-09 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pykara Ultimate Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 150 | 2005-09-06 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sabarigiri Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 340 | 1960-04-18 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sarkarpathy Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 30 | 1966-08-14 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sengulam Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 48 | 1954-05-01 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sharavathi Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 1035 | 1964-08-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivasamudram Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 42 | 1902-08-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sholayar Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 54 | 1956-05-09 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sholayar I Power House | PWRHYDINDSO | Hydro | Hydro | 84 | 1971-04-22 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Srisailam Left Bank Power House | PWRHYDINDSO | Hydro | Hydro | 900 | 2001-04-26 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Srisailam Right Bank (RB) Power House | PWRHYDINDSO | Hydro | Hydro | 770 | 1982-08-30 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Suruliyar Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 35 | 1978-08-27 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | T B Dam/Tungabhadra Dam Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 36 | 1957-01-26 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Thottiyar Hydro Power Project | PWRHYDINDSO | Hydro | Hydro | 40 | 2024-10-01 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Upper Sileru I & II Hydroelectric Power Project | PWRHYDINDSO | Hydro | Hydro | 240 | 1967-10-14 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Varahi Power House | PWRHYDINDSO | Hydro | Hydro | 460 | 2009-01-11 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kaiga Generating Station | PWRURNINDSO | Nuclear | Nuclear | 880 | 2000-03-16 | Karnataka | 0.85 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kudankulam Atomic Power Project | PWRURNINDSO | Nuclear | Nuclear | 2000 | 2014-12-31 | Tamil Nadu | 0.85 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Madras Atomic Power Station | PWRURNINDSO | Nuclear | Nuclear | 440 | 1984-01-27 | Tamil Nadu | 0.85 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Basin Bridge Gas Turbine Power Station | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 120 | 1996-02-12 | Tamil Nadu | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | GMR Rajahmundry Energy Ltd. | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 768 | 2015-07-04 | Andhra Pradesh | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | GMR Vemagiri Combined Cycle Power Plant | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 370 | 2006-01-13 | Andhra Pradesh | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | GVK Jegurupadu Gas Combined Cycle Gas Turbine | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 235.4 | 1996-07-04 | Andhra Pradesh | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Karaikal Gas Power Plant | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 32.5 | 1999-10-01 | Puducherry | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kayamkulam (Rajiv Gandhi) Gas Combined Cycle Power Plant | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 359.58 | 1998-11-02 | Kerala | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kovilkalappal (Thirumakotai) Gas Combined Cycle Gas Turbine Power Station | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 107.88 | 2001-02-05 | Tamil Nadu | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kuttalam Gas Turbine Power Station | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 100 | 2003-11-27 | Tamil Nadu | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lanco Kondapalli Combined Cycle Gas Turbine Power Plant Phase II | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 366 | 2009-12-05 | Andhra Pradesh | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pillaiperumalnallur (PPN) Power Plant Phase I | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 330.5 | 2001-04-26 | Tamil Nadu | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Valuthur Gas Turbine Power Station | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 186.2 | 2002-12-24 | Tamil Nadu | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Yelahanka Combined Cycle Power Plant | PWRNGSINDSO | Natural Gas CC | Oil & Gas | 370.05 | 2025-02-01 | Karnataka | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | APICTO Ltd. Small Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 13 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Abletech Electro Engineers Pvt. Ltd. Small Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 4.8 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Adyanpara Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 3.5 | 2015-03-09 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Agradalli Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 0.75 | 2008-10-24 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Agrahara Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 1.26 | 2012-09-24 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Akkihebbal Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 4.5 | 2007-09-03 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Aliyar Mini Hydel Project | PWRHYDINDSO | Hydro | Small Hydro | 2.5 | 2002-09-23 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Amaravathi Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2006-09-21 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Aniyooru Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 24 | 2019-11-21 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Aniyur Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 9 | 2009-08-13 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Anweri Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 1.5 | 1997-05-04 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Aremadanahalli Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 1.5 | 2013-09-02 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Attigala Small Hydro Power Station | PWRHYDINDSO | Hydro | Small Hydro | 0.35 | 1998-07-03 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Auromira Energy Group Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 18 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Baje Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 3.8 | 2015-07-10 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Barapole Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 15 | 2013-12-04 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Basavanna(Aidab havi) Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 24.75 | 2013-02-05 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Beedalli Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 3 | 2016-06-13 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bellamkonda Branch Canal Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 0.55 | 2004-11-17 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bellamkonda Branch canal Hydro Power Project Scheme II | PWRHYDINDSO | Hydro | Small Hydro | 0.55 | 1999-08-28 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadra Left Bank Canal Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 1.5 | 2018-04-05 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadra Right Bank Canal Power Station | PWRHYDINDSO | Hydro | Small Hydro | 0.4 | 2005-01-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadra Right Bank Canal Powerhouse | PWRHYDINDSO | Hydro | Small Hydro | 13.2 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Barrage I Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 10 | 2009-07-01 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Barrage II Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 10 | Pre-2000 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 1.4 | 2000-04-28 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhima-I (Sonna) Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 10.5 | 2010-08-04 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhoruka Power Corporation Hydro Project 1 | PWRHYDINDSO | Hydro | Small Hydro | 6.25 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhoruka Power Corporation Hydro Project 2 | PWRHYDINDSO | Hydro | Small Hydro | 24 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Bonal Tank Mini Hydel Project | PWRHYDINDSO | Hydro | Small Hydro | 1.25 | 2011-08-12 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Brindavan Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 12 | 2006-06-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Burgugadda Tank Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 1.2 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Charmadi Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 4.5 | 2008-07-05 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chayadevi Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 24 | 2007-06-22 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chembukadavu-I Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 2.7 | 2003-08-19 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chembukadavu-II Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 3.75 | 2003-09-04 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chettipeta Mini Hydel | PWRHYDINDSO | Hydro | Small Hydro | 1 | Pre-2000 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chilakaluripet Major Block Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 1 | 2000-07-13 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chimmony Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 2.5 | 2015-05-22 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chunchanakatte Small Hydro Power Station | PWRHYDINDSO | Hydro | Small Hydro | 18 | 1997-10-13 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Chunchidoddi Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 10.25 | 2004-12-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Deccan Cement Ltd. Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 3.7 | 1996-02-28 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dhanalakshmi Cotton & Rice Mills Limited Small Hydro Project 1 | PWRHYDINDSO | Hydro | Small Hydro | 1.59 | 1997-12-23 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dhanalakshmi Cotton & Rice Mills Limited Small Hydro Project 2 | PWRHYDINDSO | Hydro | Small Hydro | 2.61 | 1997-07-23 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Doddatappale Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 3 | 2011-01-22 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dondela Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 13 | 2009-07-19 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Donkarayi Canal Hydroelectric Power Plant | PWRHYDINDSO | Hydro | Small Hydro | 25 | Pre-2000 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Dummagudem Hydel Project | PWRHYDINDSO | Hydro | Small Hydro | 24 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Duphadal Small Hydro Electric Power Station | PWRHYDINDSO | Hydro | Small Hydro | 2.8 | 1997-04-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Energy Development Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 7 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Espar Pak Limited Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 1.3 | 2000-04-08 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Flovel Small Hydro Project 1 | PWRHYDINDSO | Hydro | Small Hydro | 4.5 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Flovel Small Hydro Project 2 | PWRHYDINDSO | Hydro | Small Hydro | 4.8 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gajanur Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 0.65 | 2014-06-06 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ganekal Mini Hydel Scheme | PWRHYDINDSO | Hydro | Small Hydro | 0.35 | 1993-12-24 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ganganahal Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 2 | 2013-07-30 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gayatri Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 2.2 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gilada Group Small Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 6 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gokak Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 10.8 | 1997-04-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gonal 2 Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 2 | 2019-08-27 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gonal 3 Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 5 | 2011-11-04 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Gugal Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 10 | 2007-09-19 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hanumanthapura Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 0.5 | 2002-09-19 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Harangi Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 15 | 1999-07-19 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hebbakavadi Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 1.75 | 2002-04-03 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hemagir Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2005-06-28 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hemavathi Left Bank Canal Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 16 | 2001-04-20 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hemavathi Right Bank Canal Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 3 | 2000-07-10 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hemavathi River Bed Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 8 | 2007-04-28 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hongadalla Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 24 | 2019-05-08 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hosmath Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 4.8 | 2011-08-12 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Hullahhalla Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 12 | 2009-04-07 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Iggalur Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 1.5 | 2015-01-23 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Iruttukanam Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 4.5 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Jyothi Jalashakthi Pvt. Ltd. Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 0.3 | 2005-11-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | KCP Limited Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 8.25 | 1998-03-24 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | KRS Dam Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2009-11-02 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kabini Dam Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 20 | 2003-06-24 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kabini RBC Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 5 | 2002-12-31 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kadamane I Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 9 | 2007-04-30 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kadamane II Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 15 | 2010-08-04 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kallada Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 15 | 1994-01-05 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kallam Spinning Mill Limited Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2002-01-01 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kalmala Mini Hydel Scheme | PWRHYDINDSO | Hydro | Small Hydro | 0.4 | 1990-01-24 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kare Power Resource Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 24.75 | 2015-09-16 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kare Power Resources Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 24 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Karikkayam Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 15 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Karnataka Power Corporation Limited (KPCL) Hydro Project 1 | PWRHYDINDSO | Hydro | Small Hydro | 17.2 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Karnataka Power Corporation Limited (KPCL) Hydro Project 2 | PWRHYDINDSO | Hydro | Small Hydro | 9 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kattepura Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 5 | 2013-09-05 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kemphole Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 18 | 2005-01-10 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kenchanagudam Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 6 | 2007-05-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kilara Small Hydro Electric Power Station | PWRHYDINDSO | Hydro | Small Hydro | 2 | 2000-03-31 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kodagu Hydel Project | PWRHYDINDSO | Hydro | Small Hydro | 3 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Kuttiady Tailrace Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 4.5 | 2008-06-19 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | L.K. Power Corporation Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 2 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Link Canal Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 1.5 | 2003-07-17 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Bhavani Micro Hydel Project | PWRHYDINDSO | Hydro | Small Hydro | 8 | 1990-04-03 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Bhavani Right Bank Canal Project | PWRHYDINDSO | Hydro | Small Hydro | 8 | 1998-02-10 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Meenmutty Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 3.5 | 2006-05-02 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | MGHE Tail Race Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 22 | 2007-12-06 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Machagundal Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 0.5 | 2017-05-31 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Maddur Branch Canal Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 2 | 2011-01-22 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Madhavamantri Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 3 | 2001-07-09 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Madupetty Small Hydro Electric Station | PWRHYDINDSO | Hydro | Small Hydro | 2 | 1997-12-01 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mahadevapura-II Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 6 | 2014-03-28 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Malampuzha Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 2.5 | 2001-11-26 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Malankara Small Hydro Electric Station | PWRHYDINDSO | Hydro | Small Hydro | 10.5 | 2005-08-06 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mallapur Mini Hydro Power Station Project | PWRHYDINDSO | Hydro | Small Hydro | 9 | 1993-11-19 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Malligere Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 0.75 | 2007-09-27 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mandagere Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 3.5 | 2004-09-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mani Dam Power House | PWRHYDINDSO | Hydro | Small Hydro | 9 | 1993-03-29 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Maniyar Small Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 12 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Manjanadka Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 10 | 2009-06-27 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mankulam Micro Hydroelectric Power Plant | PWRHYDINDSO | Hydro | Small Hydro | 0.11 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mannapitlu Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 15 | 2009-09-17 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Maravakandy Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 0.75 | 1992-10-14 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Meenvallam Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 3 | 2014-12-01 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mouneshwara Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 24.75 | 2013-08-14 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mukurthy Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 0.7 | 2001-06-27 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Mulibettu Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 10.5 | 2015-06-27 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | NATL Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 4.01 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | NCL Energy Limited Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 7.5 | 2000-09-28 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Narayanapura LBC Small Hydro Electric Power Station | PWRHYDINDSO | Hydro | Small Hydro | 11.6 | 1999-07-14 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Neerukatte Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 15 | 2009-09-09 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Neria Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 18 | 2006-04-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nippulavagu Small Hydro Project Phase I | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2002-02-06 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nippulavagu Small Hydro Project Phase II | PWRHYDINDSO | Hydro | Small Hydro | 3.3 | 2002-11-07 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nippulavagu Small Hydro Project Phase III | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2003-11-21 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nizam Sagar Hydroelectric Power Plant | PWRHYDINDSO | Hydro | Small Hydro | 10 | 1954-02-23 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Nugu Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 3 | 2002-12-31 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Palair Hydro Electric Station | PWRHYDINDSO | Hydro | Small Hydro | 2 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Paschim Hydro Energy Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 9 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pathankayam Small Hydro Electric Plant | PWRHYDINDSO | Hydro | Small Hydro | 8 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pedda Vagu Mini Hydel Project | PWRHYDINDSO | Hydro | Small Hydro | 1.2 | 2011-04-15 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Peddapalli Mini Hydro Station | PWRHYDINDSO | Hydro | Small Hydro | 9.16 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Peechi Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 1.25 | 2013-01-07 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pendanandipadu Branch Canal Mini Hydel Scheme | PWRHYDINDSO | Hydro | Small Hydro | 0.65 | 2001-05-17 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Penna Ahobilam Hydroelectric Power Plant (PABH HES) | PWRHYDINDSO | Hydro | Small Hydro | 20 | Pre-2000 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Peppara Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 3 | 1996-06-15 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Vaigai Mini I Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2010-10-02 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Vaigai Mini II Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 2.5 | 2011-01-21 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Vaigai Mini III Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 4 | Pre-2000 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Vaigai Mini IV Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 2.5 | Pre-2000 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Perla Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 24 | 2009-09-12 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Perunchani Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 1.3 | 2005-12-21 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Perunthenaruvi Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 6 | 2017-10-22 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pioneer Power Corporation Ltd. Small Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 24.75 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ponmudi Small Hydro Electric Station | PWRHYDINDSO | Hydro | Small Hydro | 32.4 | 1963-12-29 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Poozhithode Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 4.8 | 2011-06-25 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Poringalkuthu Left Bank Extension Project | PWRHYDINDSO | Hydro | Small Hydro | 16 | 1999-03-20 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Poringalkuthu small hydroelectric project | PWRHYDINDSO | Hydro | Small Hydro | 24 | 2022-05-04 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Prassana Power Ltd. Small Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 6 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Punachi Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 2 | 1992-11-12 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Pykara Micro Power House | PWRHYDINDSO | Hydro | Small Hydro | 2 | 1989-10-09 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | RNS Infrastructures Small Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 11.4 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajankollur Small Hydro Power Station | PWRHYDINDSO | Hydro | Small Hydro | 2 | 1999-08-06 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ranganatha Swami Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 24.75 | 2007-07-29 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ranni Perinad Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2012-02-16 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rayabasavanna Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 1.4 | 2013-08-31 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Rayalaseema Power Projects Limited Small Hydro Plant | PWRHYDINDSO | Hydro | Small Hydro | 3 | 1998-11-21 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | SKJ Power Limited Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 1.5 | 1999-01-27 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | SPML Infra Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 20 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sagar Power Limited Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 4.3 | 1997-11-27 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sagar Power Limited Small Hydro Project II | PWRHYDINDSO | Hydro | Small Hydro | 4 | 1998-09-07 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Saraswati Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 2 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sardar Power Ltd. Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 2 | 2008-12-01 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sathanur Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 7.5 | 1999-03-10 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sattegala Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 6.25 | 2006-09-14 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Servalar Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 20 | 1986-03-23 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shahapur Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 13.2 | 1997-03-18 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shamburi Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 24 | 2009-09-28 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shamili Hydel Power Project | PWRHYDINDSO | Hydro | Small Hydro | 12 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shanmukhasubramanya Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 10 | 2016-12-12 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sheshadri Iyer Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 6.6 | 2001-08-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shimsha Hydro Electric Power Station | PWRHYDINDSO | Hydro | Small Hydro | 17.2 | 1940-04-18 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shimsha Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 24 | 2001-10-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shiva Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 3 | 1998-09-10 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivani Power Spinners Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 0.75 | 2000-03-11 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivapur TLBC Hydro Electric Power Station | PWRHYDINDSO | Hydro | Small Hydro | 18 | 1992-11-29 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sholayar II Power House | PWRHYDINDSO | Hydro | Small Hydro | 25 | 1971-03-29 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Shri Dhanalaxmi Group Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 2 | 1997-11-24 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Siddapura Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 12 | 2009-06-21 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sindhanooru Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 0.8 | 2011-12-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Singatalur Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 18 | 2012-08-30 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Singur Hydro Electric Station | PWRHYDINDSO | Hydro | Small Hydro | 15 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sirwar Mini Hydro Power Station Project | PWRHYDINDSO | Hydro | Small Hydro | 1 | 1992-11-26 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sneha Renewable Energies Hydrel Project | PWRHYDINDSO | Hydro | Small Hydro | 0.9 | Pre-2000 | Telangana | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Soham Phalguni Power Project 1 | PWRHYDINDSO | Hydro | Small Hydro | 22 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Soham Phalguni Power Project 2 | PWRHYDINDSO | Hydro | Small Hydro | 22 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Soham Phalguni Power Project 3 | PWRHYDINDSO | Hydro | Small Hydro | 15 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Somanamaradi Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 13.8 | 2009-01-19 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Somasila Reservoir Left Flank Mini Hydel Scheme | PWRHYDINDSO | Hydro | Small Hydro | 10 | 2005-11-01 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Somasila Reservoir Left Flank Mini Hydel Scheme II | PWRHYDINDSO | Hydro | Small Hydro | 2 | 2008-10-01 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Somavathi Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 6 | 2011-10-24 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Someshwara Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 24.75 | 2005-07-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sonathi Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 13.5 | 2011-12-25 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Jayalakshmi Power Corporation Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 4 | 2000-01-19 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Maruthi Power-gen (India) Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 6 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sriramadevarakatte Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 1.5 | 2001-10-01 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Sugur Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 4.5 | 2004-04-03 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Suvarnamukhi Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 2 | 2014-10-26 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Thirumala Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 2.4 | 2000-02-02 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Thirumurthy Mini Hydel Project | PWRHYDINDSO | Hydro | Small Hydro | 1.95 | 2000-03-20 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Trident Addanki Branch Canal Small Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 3 | 2001-02-28 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Trident Power Corporation Mini Hydro Project | PWRHYDINDSO | Hydro | Small Hydro | 4 | Pre-2000 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Trident Power Corporation Scheme I | PWRHYDINDSO | Hydro | Small Hydro | 2 | 1999-10-13 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Trident Power Corporation Scheme II | PWRHYDINDSO | Hydro | Small Hydro | 2 | 1999-08-26 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Tunga Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 24 | 2014-06-13 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Tungabhadra Steel Products Ltd. | PWRHYDINDSO | Hydro | Small Hydro | 2.4 | 1999-09-17 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Ullunkal Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 7 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Upper Kallar Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 2 | Pre-2000 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Urumi - I Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 3.75 | 2004-01-25 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Urumi - II Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 2.4 | 2004-01-25 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vaigai Hydro Power Project | PWRHYDINDSO | Hydro | Small Hydro | 6 | 1990-03-04 | Tamil Nadu | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Varahi Tail Race - I Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 22.5 | 2005-06-29 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Varahi Tail Race - II Mini Hydel Power Station | PWRHYDINDSO | Hydro | Small Hydro | 15 | 2009-04-17 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vellathooval Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 3.6 | 2026-08-21 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Vilangad Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 7.5 | 2014-09-01 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Yeleru Reservoir Project Gap 2 Phase I | PWRHYDINDSO | Hydro | Small Hydro | 3 | 2000-01-17 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Yeleru Reservoir Project Gap 2 Phase II | PWRHYDINDSO | Hydro | Small Hydro | 1.5 | 2011-04-06 | Andhra Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | Yennehole -I Mini Hydel Station | PWRHYDINDSO | Hydro | Small Hydro | 15 | 2014-10-16 | Karnataka | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_S | kuthungal Small Hydro Electric Project | PWRHYDINDSO | Hydro | Small Hydro | 21 | 2001-06-01 | Kerala | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | A P I Agro Madhya Pradesh Raisen 1.1 | PWRBIOINDWE | Biomass Power | Bio Power | 1.1 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | A. A. Energy Maharashtra Gadchiroli 10 30.04.2010 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2010-04-30 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | ASN Industries Pvt Ltd Madhya Pradesh Ratlam 7.5 | PWRBIOINDWE | Biomass Power | Bio Power | 7.5 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Abellon Clean Energy Ltd Gujarat Ahmedabad 9.9 | PWRBIOINDWE | Biomass Power | Bio Power | 9.9 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Aditya Food Madhya Pradesh Bhopal 0.3 | PWRBIOINDWE | Biomass Power | Bio Power | 0.3 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Agrawal Vidut Ltd. Chhattisgarh Raipur 8.5 | PWRBIOINDWE | Biomass Power | Bio Power | 8.5 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ambika Solvex Pvt Ltd Madhya Pradesh Ratlam 1.2 | PWRBIOINDWE | Biomass Power | Bio Power | 1.2 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ambika Solvex Pvt Ltd Madhya Pradesh Ujjain 3 | PWRBIOINDWE | Biomass Power | Bio Power | 3 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Amreli Power Projects Pvt Ltd Gujarat Amreli 10 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Anant Urja Pvt Ltd Madhya Pradesh Narsimhapur 1.2 | PWRBIOINDWE | Biomass Power | Bio Power | 1.2 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ankur Scientific Energy Technologies Pvt Ltd Gujarat Vadodara 1.2 | PWRBIOINDWE | Biomass Power | Bio Power | 1.2 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Armstrong Energy Pvt. Ltd. Maharashtra Nashik 6 29.03.2008 | PWRBIOINDWE | Biomass Power | Bio Power | 6 | 2008-03-29 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Arya Energy Ltd Madhya Pradesh Bhopal 12 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Aryan Sugar Ltd. Maharashtra Solapur 10 2015-01-11 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2015-01-11 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ashok SSKL Maharashtra Ahilyanagar 15 2013-11-12 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2013-11-12 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Babanroji Shinde Sugar and allied ind Maharashtra Solapur 25 2015-02-21 | PWRBIOINDWE | Biomass Power | Bio Power | 25 | 2015-02-21 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bajrang Agro Industries Pvt Ltd Madhya Pradesh Dhar 1.2 | PWRBIOINDWE | Biomass Power | Bio Power | 1.2 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Baliraja Sakhar Karkhana Ltd. Maharashtra Parbhani 15 2015-06-17 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2015-06-17 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Baramati Agro Ltd Maharashtra Chhatrapati Sambhajinagar 14.75 2013-11-20 | PWRBIOINDWE | Biomass Power | Bio Power | 14.75 | 2013-11-20 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Baramati Agro Ltd. Maharashtra Pune 22 2010-04-24 | PWRBIOINDWE | Biomass Power | Bio Power | 22 | 2010-04-24 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhairavnath Sugar Works Ltd. Maharashtra Dharashiv 14.5 2012-05-02 | PWRBIOINDWE | Biomass Power | Bio Power | 14.5 | 2012-05-02 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhairavnath Sugar Works Ltd. Maharashtra Solapur 12 2012-02-28 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2012-02-28 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhairavnath Sugar Works Ltd. Maharashtra Solapur 12.5 2015-03-26 | PWRBIOINDWE | Biomass Power | Bio Power | 12.5 | 2015-03-26 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhairavnath Sugar Works Ltd. Maharashtra Solapur 14.5 2014-11-29 | PWRBIOINDWE | Biomass Power | Bio Power | 14.5 | 2014-11-29 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhavnagar Biomass Power Projects Pvt Ltd Gujarat Bhavnagar 10 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhima SSKL Maharashtra Pune 19.5 2012-12-02 | PWRBIOINDWE | Biomass Power | Bio Power | 19.5 | 2012-12-02 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhima Sahakari Sakhar Karkhana Ltd. Maharashtra Solapur 25 2018-03-10 | PWRBIOINDWE | Biomass Power | Bio Power | 25 | 2018-03-10 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhimashankar SSKL Maharashtra Pune 19 2013-11-04 | PWRBIOINDWE | Biomass Power | Bio Power | 19 | 2013-11-04 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Chhatrapati Sambhaji Raje Sakhar Udyog Ltd. Maharashtra Chhatrapati Sambhajinaga | PWRBIOINDWE | Biomass Power | Bio Power | 6 | 2013-01-02 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Chopada SSKL Maharashtra Jalgaon 1.5 1996-05-28 | PWRBIOINDWE | Biomass Power | Bio Power | 1.5 | 1996-05-28 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Claris Lifesciences Ltd Gujarat Ahmedabad 4.2 | PWRBIOINDWE | Biomass Power | Bio Power | 4.2 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Daund Sugar Ltd. Maharashtra Pune 18 2009-12-27 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2009-12-27 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Deepak Spinners Ltd Madhya Pradesh Guna 3 | PWRBIOINDWE | Biomass Power | Bio Power | 3 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dnyaneshwar SSK Maharashtra Ahilyanagar 12 2007-07-31 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2007-07-31 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dnyaneshwar Sahakari Sakhar Karkhana Ltd Maharashtra Ahilyanagar 19.5 2017-12-06 | PWRBIOINDWE | Biomass Power | Bio Power | 19.5 | 2017-12-06 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dr B. Ambedkar SSKL Maharashtra Dharashiv 16 2007-05-25 | PWRBIOINDWE | Biomass Power | Bio Power | 16 | 2007-05-25 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dudhaganga-Vedganga SSKL Maharashtra Kolhapur 20 2012-02-19 | PWRBIOINDWE | Biomass Power | Bio Power | 20 | 2012-02-19 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dwarkadhish Sakhar Karkhana Ltd. Maharashtra Nashik 13 2010-12-27 | PWRBIOINDWE | Biomass Power | Bio Power | 13 | 2010-12-27 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ecofren Power Project Ltd. Chhattisgarh Durg 8 | PWRBIOINDWE | Biomass Power | Bio Power | 8 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | G M T Mining & Power Pvt.Ltd. Maharashtra Nagpur 10 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | Pre-2000 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | GAPS Power & Infrastructure (P) Ltd. Maharashtra Chhatrapati Sambhajinagar 13 30 | PWRBIOINDWE | Biomass Power | Bio Power | 13 | 2008-11-30 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gangakhed Sugars Energy Ltd. Maharashtra Parbhani 30 2011-10-01 | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2011-10-01 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gangamai Industries & Constru Ltd Maharashtra Ahilyanagar 31 2011-12-05 | PWRBIOINDWE | Biomass Power | Bio Power | 31 | 2011-12-05 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Garg Casteels Pvt Ltd Gujarat Bhavnagar 2.2 | PWRBIOINDWE | Biomass Power | Bio Power | 2.2 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gokul Mauli Sugars Ltd. Maharashtra Solapur 14.85 2018-03-01 | PWRBIOINDWE | Biomass Power | Bio Power | 14.85 | 2018-03-01 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Green Power Sugars Ltd. Maharashtra Satara 15 2015-04-03 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2015-04-03 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Greta Energy Pvt. Ltd. Maharashtra Chandrapur 15 10.08.2012 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2012-10-08 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gujarat Energy Development Agency Gujarat Vadodara 0.5 | PWRBIOINDWE | Biomass Power | Bio Power | 0.5 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | H. R. Johnsons Madhya Pradesh Dewas 3.5 | PWRBIOINDWE | Biomass Power | Bio Power | 3.5 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | I.S.A. Power Pvt Ltd Chhattisgarh Dhamtari 8 | PWRBIOINDWE | Biomass Power | Bio Power | 8 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ind-Barath Energies (Maharashtra) Ltd. Maharashtra Nanded 20 08.01.2009 | PWRBIOINDWE | Biomass Power | Bio Power | 20 | 2009-08-01 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Indreshwar Sugar Mills Ltd. Maharashtra Solapur 12 2011-12-19 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2011-12-19 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jagruti Sugar & Allied Industries Ltd Maharashtra Latur 13 2011-12-14 | PWRBIOINDWE | Biomass Power | Bio Power | 13 | 2011-12-14 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jai Hind Sugar Pvt. Ltd. Maharashtra Solapur 14.5 2015-12-18 | PWRBIOINDWE | Biomass Power | Bio Power | 14.5 | 2015-12-18 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jaishriram Sugar & Agro Products Ltd. Maharashtra Ahilyanagar 5 2014-12-20 | PWRBIOINDWE | Biomass Power | Bio Power | 5 | 2014-12-20 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jakraya Sugars Maharashtra Solapur 11 2011-07-01 | PWRBIOINDWE | Biomass Power | Bio Power | 11 | 2011-07-01 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jarandeshwar Sugar Mills Pvt. Ltd. Maharashtra Satara 30 2018-04-03 | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2018-04-03 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Javandnia Sugar Madhya Pradesh Narsimhapur 0.7 | PWRBIOINDWE | Biomass Power | Bio Power | 0.7 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jawahar SSKL,Kolhapur Maharashtra Kolhapur 24 2001-11-23 | PWRBIOINDWE | Biomass Power | Bio Power | 24 | 2001-11-23 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jawahar SSSK Maharashtra Kolhapur 3 2007-12-10 | PWRBIOINDWE | Biomass Power | Bio Power | 3 | 2007-12-10 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jaymahesh Sugar Ltd Maharashtra Beed 30 2013-01-07 | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2013-01-07 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jaywant Sugars Ltd. Maharashtra Satara 10 2015-04-22 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2015-04-22 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Junagadh Power Projects Pvt Ltd Gujarat Junagadh 10 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | KVK Bio-Energy Pvt Ltd. Chhattisgarh Janjgir-Champa 15 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kalchuri Trading and Investment Corporation Madhya Pradesh Jabalpur 1 | PWRBIOINDWE | Biomass Power | Bio Power | 1 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kalindi Power and Steel Ltd Chhattisgarh Mahasamund 8 | PWRBIOINDWE | Biomass Power | Bio Power | 8 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kancheshwar Sugar Ltd. Maharashtra Dharashiv 15 2015-02-11 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2015-02-11 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Karmayogi Shankarraoji Patil SSKL Maharashtra Pune 15 2013-11-13 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2013-11-13 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kashap Sweetner Madhya Pradesh Ratlam 0.4 | PWRBIOINDWE | Biomass Power | Bio Power | 0.4 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khandala Taluka Shetkari Sahakari Sakhar Karkhana Ltd. Maharashtra Satara 9.5 20 | PWRBIOINDWE | Biomass Power | Bio Power | 9.5 | 2018-04-04 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khetan Chemicles Madhya Pradesh Dhar 2.1 | PWRBIOINDWE | Biomass Power | Bio Power | 2.1 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kisanveer Satara SSKL Maharashtra Satara 22 2012-02-14 | PWRBIOINDWE | Biomass Power | Bio Power | 22 | 2012-02-14 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kranti SSKL Maharashtra Sangli 19.7 2010-02-16 | PWRBIOINDWE | Biomass Power | Bio Power | 19.7 | 2010-02-16 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Krishna Protiens Madhya Pradesh Jabalpur 0.7 | PWRBIOINDWE | Biomass Power | Bio Power | 0.7 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kukadi SSKL Maharashtra Ahilyanagar 12 2013-12-06 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2013-12-06 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kumbhi Kasari SSKL Maharashtra Kolhapur 17.5 2014-01-08 | PWRBIOINDWE | Biomass Power | Bio Power | 17.5 | 2014-01-08 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kundan Namkeen Madhya Pradesh Bhopal 0.3 | PWRBIOINDWE | Biomass Power | Bio Power | 0.3 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Lanxess India Pvt Ltd Madhya Pradesh Jabalpur 3.9 | PWRBIOINDWE | Biomass Power | Bio Power | 3.9 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Logod Insulation Madhya Pradesh Dhar 0.6 | PWRBIOINDWE | Biomass Power | Bio Power | 0.6 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Lokmangal Mauli Maharashtra Dharashiv 30 2013-11-28 | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2013-11-28 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Lokmangal Sugar Ethanol & Cogen. Ind. Ltd. Maharashtra Solapur 31.5 2012-07-02 | PWRBIOINDWE | Biomass Power | Bio Power | 31.5 | 2012-07-02 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Loknete Baburao Patil Agro Industries Ltd. Maharashtra Solapur 19.5 2014-07-03 | PWRBIOINDWE | Biomass Power | Bio Power | 19.5 | 2014-07-03 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | M S M Energy Maharashtra Parbhani 10 15.11.2010 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2010-11-15 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Maharashtra Shetkari Sugar Ltd. Maharashtra Parbhani 20 2014-02-16 | PWRBIOINDWE | Biomass Power | Bio Power | 20 | 2014-02-16 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Maharashtra Vidyut Nigam Ltd. Maharashtra Wardha 10 20.05.2013 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2013-05-20 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Mahavir Energy and Coal Benefication Ltd. Chhattisgarh Raigarh 12 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Majalgaon SSKL Maharashtra Beed 22 2013-11-23 | PWRBIOINDWE | Biomass Power | Bio Power | 22 | 2013-11-23 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Malegaon SSKL Maharashtra Pune 21 2009-12-14 | PWRBIOINDWE | Biomass Power | Bio Power | 21 | 2009-12-14 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Manas Agro ind and infra Maharashtra Wardha 15 2013-11-28 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2013-11-28 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Manjara SSKL Maharashtra Latur 18 2013-11-12 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2013-11-12 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Matoshri Laxmi Sugar Co-Generation Industries Ltd. Maharashtra Solapur 12 2014-0 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2014-03-12 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Mula SSK,Ahemadnagar Maharashtra Ahilyanagar 30 2006-12-11 | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2006-12-11 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Narmada Sugar Madhya Pradesh Barwani 3 | PWRBIOINDWE | Biomass Power | Bio Power | 3 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Natural Sugar & Allied Industries Ltd Maharashtra Dharashiv 13 2014-01-11 | PWRBIOINDWE | Biomass Power | Bio Power | 13 | 2014-01-11 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Neeraj Power Pvt Ltd. Chhattisgarh Raipur 7.5 | PWRBIOINDWE | Biomass Power | Bio Power | 7.5 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Nira Bhima SSKL Maharashtra Pune 18 2014-04-11 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2014-04-11 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Olam Agro India Ltd. previously M/s Hemarus Technologies Ltd. Maharashtra Kolhap | PWRBIOINDWE | Biomass Power | Bio Power | 20 | 2010-11-23 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Orient Green Power (M/s. Padmasri Dr.D.Y.Patil Sahakari Sakhar Karkahna) Maharas | PWRBIOINDWE | Biomass Power | Bio Power | 20 | 2015-02-09 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Orient Green Power Ltd. Madhya Pradesh Jabalpur 10 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) (Waste to Energy) Goa N.A. 1.9400000000000002 | PWRBIOINDWE | Biomass Power | Bio Power | 1.94 | Pre-2000 | Goa | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) (Waste to Energy) Gujarat N.A. 7.5 | PWRBIOINDWE | Biomass Power | Bio Power | 7.5 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) (Waste to Energy) Madhya Pradesh N.A. 15.4 | PWRBIOINDWE | Biomass Power | Bio Power | 15.4 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) (Waste to Energy) Maharashtra N.A. 12.59 | PWRBIOINDWE | Biomass Power | Bio Power | 12.59 | Pre-2000 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Biomass & bagasse based cogen.] Chhattisgarh N | PWRBIOINDWE | Biomass Power | Bio Power | 144.89 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Biomass & bagasse based cogen.] Gujarat N.A. 1 | PWRBIOINDWE | Biomass Power | Bio Power | 17.3 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Biomass & bagasse based cogen.] Madhya Pradesh | PWRBIOINDWE | Biomass Power | Bio Power | 24.7 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Biomass & bagasse based cogen.] Maharashtra N. | PWRBIOINDWE | Biomass Power | Bio Power | 536.2 | Pre-2000 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Non-Bagasse based cogen.] Chhattisgarh N.A. 2. | PWRBIOINDWE | Biomass Power | Bio Power | 2.5 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Non-Bagasse based cogen.] Gujarat N.A. 12 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Non-Bagasse based cogen.] Madhya Pradesh N.A. | PWRBIOINDWE | Biomass Power | Bio Power | 14.85 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Non-Bagasse based cogen.] Maharashtra N.A. 16. | PWRBIOINDWE | Biomass Power | Bio Power | 16.4 | Pre-2000 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Waste to Energy (Off-grid)] Chhattisgarh N.A. | PWRBIOINDWE | Biomass Power | Bio Power | 10.83 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Waste to Energy (Off-grid)] Gujarat N.A. 455 | PWRBIOINDWE | Biomass Power | Bio Power | 45.05 | Pre-2000 | Gujarat | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Waste to Energy (Off-grid)] Madhya Pradesh N.A | PWRBIOINDWE | Biomass Power | Bio Power | 32.71 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Waste to Energy (Off-grid)] Maharashtra N.A. 6 | PWRBIOINDWE | Biomass Power | Bio Power | 62.01 | Pre-2000 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Pandurang SSK (Phase I) Maharashtra Solapur 9 2006-06-22 | PWRBIOINDWE | Biomass Power | Bio Power | 9 | 2006-06-22 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Piyush Sugar And Power Pvt. Ltd. Maharashtra Ahilyanagar 6 2018-01-31 | PWRBIOINDWE | Biomass Power | Bio Power | 6 | 2018-01-31 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Pragya Energy Pvt Ltd Madhya Pradesh Katni 1.2 | PWRBIOINDWE | Biomass Power | Bio Power | 1.2 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Pravara Renewable Energy Ltd (Boot-M/s. Padmashri Vikhe Patil SSKL) Maharashtra | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2015-11-05 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Prigya Bekari Madhya Pradesh Ujjain 0.2 | PWRBIOINDWE | Biomass Power | Bio Power | 0.2 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Purna SSKL Maharashtra Hingoli 18 2011-06-27 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2011-06-27 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Purti Sakhar Karkh. Ltd. Maharashtra Nagpur 22 2007-03-18 | PWRBIOINDWE | Biomass Power | Bio Power | 22 | 2007-03-18 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | R. R. Energy Ltd. Chhattisgarh Raigarh 15 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | R.K. Namkeen Madhya Pradesh Shajapur 0.3 | PWRBIOINDWE | Biomass Power | Bio Power | 0.3 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Rajarambapu Patil SSKL Maharashtra Sangli 28 2016-12-26 | PWRBIOINDWE | Biomass Power | Bio Power | 28 | 2016-12-26 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Rajarambapu Patil SSKL(W) Maharashtra Sangli 12 2006-11-11 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2006-11-11 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Rake power Ltd Maharashtra Nagpur 10 25.07.2008 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2008-07-25 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ramkrishna Solvex Pvt Ltd Madhya Pradesh Anuppur 3 | PWRBIOINDWE | Biomass Power | Bio Power | 3 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ramnik Power & Alloys Pvt Ltd Madhya Pradesh Balaghat 6 | PWRBIOINDWE | Biomass Power | Bio Power | 6 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Raosahebdada Pawar Ghodganga Sahakari Sakhar Karkhana Ltd Maharashtra Pune 20.5 | PWRBIOINDWE | Biomass Power | Bio Power | 20.5 | 2018-08-16 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Real (N.R.I.) Power Pvt Ltd Chhattisgarh Bilaspur 7.5 | PWRBIOINDWE | Biomass Power | Bio Power | 7.5 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Rena Sahakari Sakhar Karkhana Ltd. Maharashtra Latur 12 2018-03-21 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2018-03-21 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Rukmini Power and Steel Ltd. Chhattisgarh Raigarh 10 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | S. M. Shankarrao Mohite- Patil SSKL Maharashtra Solapur 33 2011-03-06 | PWRBIOINDWE | Biomass Power | Bio Power | 33 | 2011-03-06 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sadashivrao Mandlik Maharashtra Kolhapur 12 2012-02-09 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2012-02-09 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sadguru Sri Sri Sakhar Karkhana Maharashtra Sangli 12 2014-03-21 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2014-03-21 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sahakar Shiromani Vasantrao Kale SSKL Maharashtra Solapur 18 2016-01-16 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2016-01-16 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sahakarmaharshi Bhausaheb Thorat SSKL Maharashtra Ahilyanagar 30 2016-03-28 | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2016-03-28 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Saikrupa SSKL Maharashtra Ahilyanagar 5.5 2010-10-22 | PWRBIOINDWE | Biomass Power | Bio Power | 5.5 | 2010-10-22 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Saikrupa Sakhar Karkhana Maharashtra Ahilyanagar 40 2011-03-31 | PWRBIOINDWE | Biomass Power | Bio Power | 40 | 2011-03-31 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Saisa Biscuits Madhya Pradesh Bhopal 0.4 | PWRBIOINDWE | Biomass Power | Bio Power | 0.4 | Pre-2000 | Madhya Pradesh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Samarth SSKL Maharashtra Jalna 18 2011-01-07 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2011-01-07 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Samrudhi Sugars Ltd Maharashtra Jalna 12 2014-04-03 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2014-04-03 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sanjivni(T) SSKL Maharashtra Ahilyanagar 12 2011-12-03 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2011-12-03 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sant Muktai Sugar & Energy Ltd. Maharashtra Jalgaon 12 2017-01-21 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2017-01-21 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sant Tukaram SSKL Maharashtra Pune 15 2016-06-13 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2016-06-13 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sar Senapati Santaji Ghorpade Sugar Factory Ltd. Maharashtra Kolhapur 22 2014-12 | PWRBIOINDWE | Biomass Power | Bio Power | 22 | 2014-12-24 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Saradambika Power Plant Pvt. Ltd. Maharashtra Chandrapur 10 30.06.2008 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2008-06-30 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sh. Chhatrapati Shahu Maharashtra Kolhapur 21.5 2008-03-15 | PWRBIOINDWE | Biomass Power | Bio Power | 21.5 | 2008-03-15 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shalivahana Projects Ltd. Maharashtra Yavatmal 10 17.01.2008 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2008-01-17 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sharad SSKL Maharashtra Kolhapur 13 2018-01-20 | PWRBIOINDWE | Biomass Power | Bio Power | 13 | 2018-01-20 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sharad SSKL Maharashtra Kolhapur 2 2008-01-15 | PWRBIOINDWE | Biomass Power | Bio Power | 2 | 2008-01-15 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sharayu Agro Industries Ltd. Maharashtra Satara 30 2016-10-27 | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2016-10-27 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shivratna Udyog Ltd Maharashtra Solapur 12.5 2015-02-21 | PWRBIOINDWE | Biomass Power | Bio Power | 12.5 | 2015-02-21 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shraddha Energy & Infraprojects Pvt. Ltd. Maharashtra Jalna 12 2015-06-15 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2015-06-15 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shree Renuka Sugars Ltd. (Boot- M/s Ajinkyatara SSKL) Maharashtra Satara 24 2012 | PWRBIOINDWE | Biomass Power | Bio Power | 24 | 2012-11-02 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shree Renuka Sugars Ltd. (Boot- M/s DBRK SSKL) Maharashtra Kolhapur 30 2011-06-0 | PWRBIOINDWE | Biomass Power | Bio Power | 30 | 2011-06-07 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shree Renuka Sugars Ltd. (Boot- M/s Mohanrao Shinde SSKL) Maharashtra Sangli 15 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2010-03-17 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shree Siddheshwar Sahakari Sakhar Karkhana Ltd. Maharashtra Solapur 38 2017-12-2 | PWRBIOINDWE | Biomass Power | Bio Power | 38 | 2017-12-29 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shreenath Mhaskoba SSKL Maharashtra Pune 10 2012-01-20 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2012-01-20 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Ambalika Sugars Pvt. Ltd. Maharashtra Ahilyanagar 38 2012-11-29 | PWRBIOINDWE | Biomass Power | Bio Power | 38 | 2012-11-29 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Chhatrapati Sahakari Sakhar Karkhana Ltd. Maharashtra Pune 18 2017-12-12 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2017-12-12 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Datta Sakhar Karkhana (A unit of Dalmia Bharat Sugar and Ind. Ltd Maharasht | PWRBIOINDWE | Biomass Power | Bio Power | 23 | 2014-03-16 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Gurudatt Sugars Ltd. Maharashtra Kolhapur 15 2013-11-22 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2013-11-22 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Pandurang SSKL (Phase II) Maharashtra Solapur 10 2012-02-22 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2012-02-22 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Shankar SSKL Maharashtra Solapur 20 2011-03-23 | PWRBIOINDWE | Biomass Power | Bio Power | 20 | 2011-03-23 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Vithal SSKL Maharashtra Solapur 29.8 2010-05-27 | PWRBIOINDWE | Biomass Power | Bio Power | 29.8 | 2010-05-27 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shriram Jawahar Shetkari Sahakari Sakhar Udyog Maharashtra Satara 1.5 2010-05-09 | PWRBIOINDWE | Biomass Power | Bio Power | 1.5 | 2010-05-09 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shudha Agro Oil and Chemical Industries Ltd Chhattisgarh Bilaspur 9.9 | PWRBIOINDWE | Biomass Power | Bio Power | 9.9 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Siddhanath Sugar Mills Ltd. Maharashtra Solapur 26 2010-12-15 | PWRBIOINDWE | Biomass Power | Bio Power | 26 | 2010-12-15 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sinewave Power Ltd. Maharashtra Sangli 10 23.01.2014 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2014-01-23 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sitaram Maharaj S K Maharashtra Solapur 10 2013-12-11 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2013-12-11 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Someshwar SSKL Maharashtra Pune 18 2010-05-21 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2010-05-21 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sonhira SSKL Maharashtra Sangli 22 2011-04-29 | PWRBIOINDWE | Biomass Power | Bio Power | 22 | 2011-04-29 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | South Asian Agro Industries Ltd Chhattisgarh Raipur 9.8 | PWRBIOINDWE | Biomass Power | Bio Power | 9.8 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Spark Green Energy (Ahmednagar) P. Ltd Maharashtra Ahilyanagar 25 | PWRBIOINDWE | Biomass Power | Bio Power | 25 | Pre-2000 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sri Guruprabha Power Ltd Maharashtra Jalgaon 10 30.11.2009 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2009-11-30 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sri Panchjanya Power Pvt. Ltd. Maharashtra Hingoli 10 09.09.2010 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2010-09-09 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Swaraj India Agro Ltd. Maharashtra Satara 19.5 2015-11-21 | PWRBIOINDWE | Biomass Power | Bio Power | 19.5 | 2015-11-21 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Team Ferro Alloys Pvt. Ltd. Maharashtra Gondia 8 30.12.2005 | PWRBIOINDWE | Biomass Power | Bio Power | 8 | 2005-12-30 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | The Saswad Mali Sugar Factory Ltd Maharashtra Solapur 14.8 2013-12-19 | PWRBIOINDWE | Biomass Power | Bio Power | 14.8 | 2013-12-19 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Udagiri Sugar & Power Ltd. Maharashtra Sangli 14 2013-03-03 | PWRBIOINDWE | Biomass Power | Bio Power | 14 | 2013-03-03 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Urjankur Shree Datta Co.Ltd Maharashtra Kolhapur 36 2013-04-01 | PWRBIOINDWE | Biomass Power | Bio Power | 36 | 2013-04-01 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Urjankur Shree Tatyasaheb Kore Power Maharashtra Kolhapur 44 2013-04-01 | PWRBIOINDWE | Biomass Power | Bio Power | 44 | 2013-04-01 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Utech Sugar Ltd. Maharashtra Ahilyanagar 14.9 2017-12-28 | PWRBIOINDWE | Biomass Power | Bio Power | 14.9 | 2017-12-28 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Utopian Sugars Ltd. Maharashtra Solapur 14.8 2014-12-02 | PWRBIOINDWE | Biomass Power | Bio Power | 14.8 | 2014-12-02 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | VARAM Bio-Energy Pvt. Ltd. Maharashtra Bhandara 10 18.02.2009 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2009-02-18 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vaidhyanath SSKL Maharashtra Beed 21 2013-02-08 | PWRBIOINDWE | Biomass Power | Bio Power | 21 | 2013-02-08 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vandana Vidhyt Ltd Chhattisgarh Bilaspur 8 | PWRBIOINDWE | Biomass Power | Bio Power | 8 | Pre-2000 | Chhattisgarh | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vasantraodada Patil SSKL Maharashtra Nashik 17 2012-02-18 | PWRBIOINDWE | Biomass Power | Bio Power | 17 | 2012-02-18 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vayunandana Power Ltd. Maharashtra Gadchiroli 10 09.12.2010 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2010-09-12 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vighnahar SSK,Pune Maharashtra Pune 18 2005-12-23 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2005-12-23 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vikas SSKL Maharashtra Latur 18 2011-02-15 | PWRBIOINDWE | Biomass Power | Bio Power | 18 | 2011-02-15 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vishwasrao Naik SSKL Maharashtra Sangli 15 2012-12-28 | PWRBIOINDWE | Biomass Power | Bio Power | 15 | 2012-12-28 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vitthal Refined Sugars Ltd. Maharashtra Solapur 26 2017-12-01 | PWRBIOINDWE | Biomass Power | Bio Power | 26 | 2017-12-01 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vitthal Sugars Manufacturing Limited Maharashtra Solapur 12 2011-03-21 | PWRBIOINDWE | Biomass Power | Bio Power | 12 | 2011-03-21 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vitthalrao Shinde SSKL Maharashtra Solapur 38 2011-03-11 | PWRBIOINDWE | Biomass Power | Bio Power | 38 | 2011-03-11 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Yash Agro Energy Ltd. Maharashtra Chandrapur 8 | PWRBIOINDWE | Biomass Power | Bio Power | 8 | Pre-2000 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Yashwantrao Mohite Krishna SSKL Maharashtra Satara 16 2010-12-14 | PWRBIOINDWE | Biomass Power | Bio Power | 16 | 2010-12-14 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Yedeshwari Agro Products Ltd Maharashtra Beed 10 2014-01-17 | PWRBIOINDWE | Biomass Power | Bio Power | 10 | 2014-01-17 | Maharashtra | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Akaltara TPS | PWRCOAINDWE | Coal Steam | Coal | 1800 | 2013-08-13 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Akrimota TPS | PWRCOAINDWE | Coal Steam | Coal | 250 | 2005-03-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Amaravati TPS | PWRCOAINDWE | Coal Steam | Coal | 1350 | 2013-03-25 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Amarkantak TPS | PWRCOAINDWE | Coal Steam | Coal | 210 | 2008-06-01 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Anuppur TPP | PWRCOAINDWE | Coal Steam | Coal | 1250 | 2015-04-01 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Avantha Bhandar TPS | PWRCOAINDWE | Coal Steam | Coal | 600 | 2014-03-31 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Balco Korba TPP | PWRCOAINDWE | Coal Steam | Coal | 600 | 2015-07-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bandakhar TPP | PWRCOAINDWE | Coal Steam | Coal | 300 | 2015-06-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Baradarha TPS | PWRCOAINDWE | Coal Steam | Coal | 1200 | 2014-02-23 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bela TPS | PWRCOAINDWE | Coal Steam | Coal | 270 | 2013-03-20 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhavnagar TPP | PWRCOAINDWE | Coal Steam | Coal | 500 | 2016-05-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhilai TPS | PWRCOAINDWE | Coal Steam | Coal | 500 | 2008-04-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhusawal TPS | PWRCOAINDWE | Coal Steam | Coal | 1870 | 1982-09-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bina TPS | PWRCOAINDWE | Coal Steam | Coal | 500 | 2012-08-01 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Binjkote TPP | PWRCOAINDWE | Coal Steam | Coal | 600 | 2017-04-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Butibori TPP | PWRCOAINDWE | Coal Steam | Coal | 600 | 2012-08-17 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Chakabura TPP | PWRCOAINDWE | Coal Steam | Coal | 30 | 2014-03-28 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Chandrapur (Maharashtra) STPS | PWRCOAINDWE | Coal Steam | Coal | 2920 | 1985-05-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dahanu TPS | PWRCOAINDWE | Coal Steam | Coal | 500 | 1995-01-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dhariwal TPP | PWRCOAINDWE | Coal Steam | Coal | 600 | 2013-11-03 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dr. Shyama Prasad Mukherjee TPS | PWRCOAINDWE | Coal Steam | Coal | 500 | 2007-03-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | EMCO Energy Warora TPS/ GMR Warora | PWRCOAINDWE | Coal Steam | Coal | 600 | 2013-02-07 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gadarwara STPS | PWRCOAINDWE | Coal Steam | Coal | 1600 | 2019-03-01 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gandhi Nagar TPS | PWRCOAINDWE | Coal Steam | Coal | 630 | 1990-03-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gupta Energy or GEPL TPP | PWRCOAINDWE | Coal Steam | Coal | 120 | 2012-05-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | JSW Ratnagiri TPP | PWRCOAINDWE | Coal Steam | Coal | 300 | 2010-08-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jaypee Nigrie STPP | PWRCOAINDWE | Coal Steam | Coal | 1320 | 2014-08-29 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kasaipalli TPP | PWRCOAINDWE | Coal Steam | Coal | 270 | 2011-12-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khaparkheda TPS | PWRCOAINDWE | Coal Steam | Coal | 1340 | 1989-03-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khargone Super Critical Power Plant | PWRCOAINDWE | Coal Steam | Coal | 1320 | 2019-09-01 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Koradi TPS | PWRCOAINDWE | Coal Steam | Coal | 2190 | 1982-03-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Korba STPS | PWRCOAINDWE | Coal Steam | Coal | 2600 | 1983-03-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Korba West or Hasdeo TPS | PWRCOAINDWE | Coal Steam | Coal | 1340 | 1983-03-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kutchh Lignite TPS | PWRCOAINDWE | Coal Steam | Coal | 150 | 1997-03-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Lara STPS | PWRCOAINDWE | Coal Steam | Coal | 1600 | 2018-03-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Mahan TPP | PWRCOAINDWE | Coal Steam | Coal | 1200 | 2013-02-24 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Marwa TPS | PWRCOAINDWE | Coal Steam | Coal | 1000 | 2014-03-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Mauda TPS | PWRCOAINDWE | Coal Steam | Coal | 2320 | 2012-04-19 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Mihan TPS | PWRCOAINDWE | Coal Steam | Coal | 246 | 2012-02-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Mundra TPS | PWRCOAINDWE | Coal Steam | Coal | 4620 | 2009-08-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Mundra UMTPP | PWRCOAINDWE | Coal Steam | Coal | 4000 | 2012-02-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Nasik TPS | PWRCOAINDWE | Coal Steam | Coal | 630 | 1979-03-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Nawapara TPP | PWRCOAINDWE | Coal Steam | Coal | 600 | 2016-08-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Niwari TPP | PWRCOAINDWE | Coal Steam | Coal | 90 | 2013-12-10 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | O.P. Jindal or Tamnar I TPS/ Raigarh TPP | PWRCOAINDWE | Coal Steam | Coal | 1000 | 2007-12-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Paras TPS | PWRCOAINDWE | Coal Steam | Coal | 500 | 2007-03-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Parli TPS | PWRCOAINDWE | Coal Steam | Coal | 750 | 2007-02-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Pathadi TPP | PWRCOAINDWE | Coal Steam | Coal | 600 | 2009-06-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Raikheda TPP | PWRCOAINDWE | Coal Steam | Coal | 1370 | 2015-03-02 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ratija TPS | PWRCOAINDWE | Coal Steam | Coal | 100 | 2013-02-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | SVPL TPP | PWRCOAINDWE | Coal Steam | Coal | 63 | 2011-12-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sabarmati (D-F Stations) TPP | PWRCOAINDWE | Coal Steam | Coal | 362 | 1978-10-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Salaya TPP/Essar Power Gujarat | PWRCOAINDWE | Coal Steam | Coal | 1200 | 2012-02-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sanjay Gandhi TPS | PWRCOAINDWE | Coal Steam | Coal | 1340 | 1993-03-01 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sasan UMTPP | PWRCOAINDWE | Coal Steam | Coal | 3960 | 2013-05-30 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Satpura TPS | PWRCOAINDWE | Coal Steam | Coal | 500 | 2013-03-22 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Seioni TPP or Jhabua Power Seoni TPP | PWRCOAINDWE | Coal Steam | Coal | 600 | 2016-03-22 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shirpur TPP | PWRCOAINDWE | Coal Steam | Coal | 300 | 2018-09-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Singhaji or Malwa TPP | PWRCOAINDWE | Coal Steam | Coal | 2520 | 2013-10-18 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sikka TPS | PWRCOAINDWE | Coal Steam | Coal | 500 | 2015-03-29 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Singhitarai TPP | PWRCOAINDWE | Coal Steam | Coal | 600 | 2025-07-19 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sipat STPS | PWRCOAINDWE | Coal Steam | Coal | 2980 | 2007-05-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Solapur Super critical Thermal Power Plant | PWRCOAINDWE | Coal Steam | Coal | 1320 | 2017-04-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Surat (Lignite) TPS | PWRCOAINDWE | Coal Steam | Coal | 500 | 1999-11-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Tamnar TPP | PWRCOAINDWE | Coal Steam | Coal | 2400 | 2014-03-10 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Tirora TPS | PWRCOAINDWE | Coal Steam | Coal | 3300 | 2012-09-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Trombay TPS | PWRCOAINDWE | Coal Steam | Coal | 750 | 1984-01-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Uchpinda TPP | PWRCOAINDWE | Coal Steam | Coal | 1440 | 2015-11-01 | Chhattisgarh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ukai TPS | PWRCOAINDWE | Coal Steam | Coal | 1110 | 1979-01-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vindhyachal STPS | PWRCOAINDWE | Coal Steam | Coal | 4760 | 1987-10-01 | Madhya Pradesh | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Wanakbori TPS | PWRCOAINDWE | Coal Steam | Coal | 2270 | 1982-03-01 | Gujarat | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Wardha Warora TPP | PWRCOAINDWE | Coal Steam | Coal | 540 | 2010-06-01 | Maharashtra | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bansagar Tons I Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 315 | 1991-09-27 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bansagar Tons II Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 30 | 2002-02-01 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bansagar Tons III Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 60 | 2000-07-18 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bargi Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 90 | 1988-06-03 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhandardhara II Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 34 | 1999-05-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhira Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 150 | 1927-08-10 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhira PSS (Pump Storage Scheme) Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 150 | 1927-06-17 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhira Tail Race Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 80 | 1987-09-13 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhivpuri Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 75 | 1997-03-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gandhi Sagar Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 115 | 1960-11-19 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ghatgarh Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 250 | 2008-01-07 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Hasdeobango Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 120 | 1994-03-21 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Indira Sagar Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 1000 | 2004-01-01 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kadana Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 240 | 1990-01-09 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khopoli Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 72 | 2001-08-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Koyna Dam Power House | PWRHYDINDWE | Hydro | Hydro | 36 | 1980-10-03 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Koyna I,II,III & IV Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 1920 | 1962-05-16 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Madhikheda Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 60 | 2006-08-28 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Omkareshwar Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 520 | 2007-11-01 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Pench Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 160 | 1986-09-09 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Rajghat Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 45 | 1999-09-29 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sardar Sarovar Canal Head Power House (CHPH) | PWRHYDINDWE | Hydro | Hydro | 250 | 2004-05-03 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sardar Sarovar River Bed Power House (RBPH) | PWRHYDINDWE | Hydro | Hydro | 1200 | 2005-02-01 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Tillari Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 60 | 1986-10-10 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ukai Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 300 | 1974-07-08 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vaitarna Hydroelectric Power Project | PWRHYDINDWE | Hydro | Hydro | 60 | 1976-06-26 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kakrapar Atomic Power Station | PWRURNINDWE | Nuclear | Nuclear | 1840 | 1993-05-06 | Gujarat | 0.85 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Tarapur Atomic Power Station | PWRURNINDWE | Nuclear | Nuclear | 1400 | 1969-10-28 | Maharashtra | 0.85 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | DGEN Mega Combined Cycle Gas Turbine Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 1200 | 2014-11-26 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dhuvaran Gas Based Combined Cycle Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 594.72 | 2004-01-28 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Essar Hazira Combined Cycle Gas Turbine Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 515 | 1997-10-02 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Hazira GSEG Gas Combined Cycle Gas Turbine Power Plant Ext. | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 351 | 2012-02-18 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jhanor-Gandhar Gas Combined Cycle Gas Turbine Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 657.39 | 1994-03-17 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kawas Gas Combined Cycle Gas Turbine Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 656.2 | 1992-03-22 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Pipavav Combined Cycle Gas Turbine Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 702 | 2013-03-22 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ratnagiri Gas and Power Private Ltd. | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 1967.08 | 1998-11-12 | Maharashtra | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | SUGEN Combined Cycle Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 1147.5 | 2009-02-04 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Trombay Unit 7 Gas Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 180 | 1993-07-29 | Maharashtra | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | UNOSUGEN Combined Cycle Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 382.5 | 2013-01-20 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Uran Gas Combined Cycle Gas Turbine | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 672 | 1985-06-17 | Maharashtra | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Utran Gas Based Power Station Combined Cycle Power Plant | PWRNGSINDWE | Natural Gas CC | Oil & Gas | 374 | 2009-07-10 | Gujarat | 0.55 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ambai Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 4 | 2012-06-30 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Amhata Hydro Energy Project | PWRHYDINDWE | Hydro | Small Hydro | 3.8 | Pre-2000 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ascent Hydro Projects | PWRHYDINDWE | Hydro | Small Hydro | 2.2 | Pre-2000 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bansagar Hydel Power Station Phase IV | PWRHYDINDWE | Hydro | Small Hydro | 20 | 2006-08-20 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhandardara Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 12 | 2001-08-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhatghar Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 16 | 1977-08-02 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhatsa Hydro Electric Plant (Bhatsa HEP) | PWRHYDINDWE | Hydro | Small Hydro | 15 | 1991-09-28 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhivpuri Mini Hydel Project | PWRHYDINDWE | Hydro | Small Hydro | 3 | 1997-03-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Birsinghpur Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 20 | 1991-11-01 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Chhattisgarh Small Hydro project Bunched | PWRHYDINDWE | Hydro | Small Hydro | 24.9 | 2025-09-30 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Chitri Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 2 | 2010-12-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | DLZ Group Hydro Project (Maharashtra) | PWRHYDINDWE | Hydro | Small Hydro | 4.9 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Daman Ganga I & II Small Hydro Power Project | PWRHYDINDWE | Hydro | Small Hydro | 5.6 | Pre-2000 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Darana Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 4.9 | 2010-12-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Deoghar Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 1.5 | 2010-04-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dhom Balkawadi Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 4 | 2010-06-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dhom Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 2 | 1992-03-31 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dimbhe Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 5 | 1998-10-17 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dolvahal Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 2 | 2007-12-02 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Dudhganga Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 24 | 2000-02-27 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gangrel Mini Hydel Project | PWRHYDINDWE | Hydro | Small Hydro | 1.2 | Pre-2000 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gangrel Hydro Electric Power Station | PWRHYDINDWE | Hydro | Small Hydro | 10 | 2004-04-02 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gautami Godavari Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 1.2 | 2013-03-12 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ghatprabha Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 8 | 2013-04-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Govt. of Maharashtra Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 3 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gujarat Electricity Board (GEB) Project 1 | PWRHYDINDWE | Hydro | Small Hydro | 5 | Pre-2000 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gujarat Electricity Board (GEB) Project 2 | PWRHYDINDWE | Hydro | Small Hydro | 3 | Pre-2000 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Gullu Small Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 24 | Pre-2000 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Indira Sagar Project | PWRHYDINDWE | Hydro | Small Hydro | 15 | Pre-2000 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Jatashankari Hydro Power Project | PWRHYDINDWE | Hydro | Small Hydro | 7 | Pre-2000 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kachchh Branch Canal Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 6.66 | 2020-02-01 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kadvi Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 1.5 | 2011-03-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kanher Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 4 | 1991-08-18 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Karanjwan Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 3 | 2001-10-26 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kasari Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 2.5 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khadakvasla Dam Foot Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 0.7 | 2012-06-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khadakwasla Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 8 | 1991-03-31 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khadakwasla II Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 8 | 1991-08-21 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Khodshi Power Projects HEP | PWRHYDINDWE | Hydro | Small Hydro | 4.9 | 2013-12-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Konal Hydro Power Project | PWRHYDINDWE | Hydro | Small Hydro | 10 | 2010-03-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Korba Mini Hydel Power Plant | PWRHYDINDWE | Hydro | Small Hydro | 1.7 | 2003-01-12 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Kumbhi Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 2.5 | 2011-02-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 1 | PWRHYDINDWE | Hydro | Small Hydro | 4 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 2 | PWRHYDINDWE | Hydro | Small Hydro | 16 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 3 | PWRHYDINDWE | Hydro | Small Hydro | 9 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 4 | PWRHYDINDWE | Hydro | Small Hydro | 4 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 5 | PWRHYDINDWE | Hydro | Small Hydro | 2 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Mahan III Hydro Power Project | PWRHYDINDWE | Hydro | Small Hydro | 24.75 | Pre-2000 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Majalgaon Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 1.5 | 2008-01-17 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Majalgaon Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 0.75 | 2007-12-21 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Manikdoh Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 6 | 1995-11-22 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Miyagam Branch Canal Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 1.5 | 2018-05-15 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Nilwande Low Level Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 7 | 2012-06-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Nira Deoghar Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 6 | 2009-11-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Nira Deoghar Hydro Electric Project II | PWRHYDINDWE | Hydro | Small Hydro | 10 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | OREVA Energy Pvt. Ltd. Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 1 | Pre-2000 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Paithan Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 12 | 1984-11-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Panam Canal Small Hydro Power Project | PWRHYDINDWE | Hydro | Small Hydro | 2 | 1994-03-24 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Patgaon Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 2.5 | 2011-03-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Pawana Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 10 | 1988-06-11 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Pench Kamathi Khari LBC Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 4.4 | 2011-12-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Radhanagari HEP | PWRHYDINDWE | Hydro | Small Hydro | 4.8 | 1952-12-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Rani Avanti Bai Sagar Project | PWRHYDINDWE | Hydro | Small Hydro | 10 | Pre-2000 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | SAS Hydel Power Projects | PWRHYDINDWE | Hydro | Small Hydro | 9.75 | Pre-2000 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sabarmati Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 4 | Pre-2000 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Saurashtra Branch Canal Small Hydro Project I | PWRHYDINDWE | Hydro | Small Hydro | 15 | 2018-12-01 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Saurashtra Branch Canal Small Hydro Project II | PWRHYDINDWE | Hydro | Small Hydro | 15 | 2019-02-27 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Shivaji Mohite Group Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 3.5 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sikasar Hydel Power Station | PWRHYDINDWE | Hydro | Small Hydro | 7 | 2006-09-03 | Chhattisgarh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sirmour Small Hydro Power Project | PWRHYDINDWE | Hydro | Small Hydro | 24 | Pre-2000 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sonawade Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 4 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Sterling & Wilson Group Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 2.5 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Surya Hydro Electric Plant (Surya HEP) | PWRHYDINDWE | Hydro | Small Hydro | 6 | 1999-01-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Surya Left Bank Canal Hydro Electric Plant (Surya LBC HEP) | PWRHYDINDWE | Hydro | Small Hydro | 0.75 | 1998-06-04 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Tawa Hydro Electric Generation Power Plant | PWRHYDINDWE | Hydro | Small Hydro | 13.5 | 1997-01-21 | Madhya Pradesh | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Tembhu Barej Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 4.5 | 2010-12-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Terwanmedhe Hydro Electric Plant (Terwanmedhe HEP) | PWRHYDINDWE | Hydro | Small Hydro | 0.2 | 1998-03-31 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Ujjani Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 12 | 1994-05-02 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vadodara Branch Canal Small Hydro Project I | PWRHYDINDWE | Hydro | Small Hydro | 1.05 | 2019-06-20 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vadodara Branch Canal Small Hydro Project II | PWRHYDINDWE | Hydro | Small Hydro | 0.7 | 2019-02-19 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vadodara Branch Canal Small Hydro Project III | PWRHYDINDWE | Hydro | Small Hydro | 0.4 | 2018-12-21 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vadodara Branch Canal Small Hydro Project IV | PWRHYDINDWE | Hydro | Small Hydro | 0.4 | 2018-12-24 | Gujarat | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vaitarna Dam Foot Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 1.5 | 1987-09-21 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vajra Fall Hydro Electric Project | PWRHYDINDWE | Hydro | Small Hydro | 3 | 2002-12-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vajra Fall Hydro Electric Project II | PWRHYDINDWE | Hydro | Small Hydro | 3 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Veer Nira LBC Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 4.8 | 2012-03-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Vir Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 9 | 1975-02-17 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Wan Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 1.5 | 2007-12-21 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Warana Group Small Hydro Project 1 | PWRHYDINDWE | Hydro | Small Hydro | 2 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Warana Group Small Hydro Project 2 | PWRHYDINDWE | Hydro | Small Hydro | 2.5 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Warana Group Small Hydro Project 3 | PWRHYDINDWE | Hydro | Small Hydro | 2.5 | Pre-2000 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Warana Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 16 | 1999-09-01 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Yeldari Small Hydro Project | PWRHYDINDWE | Hydro | Small Hydro | 22.5 | 1968-05-10 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
India | IN_W | Yewateshwar Hydro Electric Plant | PWRHYDINDWE | Hydro | Small Hydro | 0.07 | 1998-09-02 | Maharashtra | 0.45 | Operational | India_Electricity_Infrastructure.xlsx

## Planned_Generation
Country | Node | Project_Name | Technology_Code | Technology_Name | Fuel | Capacity_MW | Expected_COD | Status | Developer | Source
Bangladesh | BD | Rooppur Nuclear Power Plant Unit-1 | PWRURNBGDXX | Nuclear Power Plant | Nuclear | 1200 | 2024 | Under Construction / Test | NPCBL / Rosatom (Russia) | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rooppur Nuclear Power Plant Unit-2 | PWRURNBGDXX | Nuclear Power Plant | Nuclear | 1200 | 2025 | Under Construction | NPCBL / Rosatom (Russia) | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Patuakhali 1320 MW Coal PP (RNPL) | PWRCOABGDXX | Coal Power Plant | Coal | 1320 | 2025 | Test Run | RPCL | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rupsha 800 MW CCPP | PWRNGSBGDXX | Natural Gas CC/OC | Gas/HSD | 800 | 2025 | Test Run | NWPGCL | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sonagazi 75 MW Solar Plant (EGCB) | PWRSPVBGDXX | Solar PV | Solar | 75 | 2025 | Test Run / Commissioning | EGCB | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Moulvibazar 10 MW Solar Power Plant | PWRSPVBGDXX | Solar PV | Solar | 10 | 2025 | Under Development | IPP | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Additional LNG-based Gas Power (Multiple) | PWRNGSBGDXX | Natural Gas CC/OC | Gas/LNG | 5000 | 2025 | Committed Pipeline | Various IPP/PDB | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Large-scale Solar Expansion | PWRSPVBGDXX | Solar PV | Solar | 3000 | 2025 | Planning/Committed | Various IPP | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Offshore Wind (Pilot) | PWRWONBGDXX | Wind Power | Wind | 200 | 2035 | Pre-Feasibility | TBD | Bangladesh_Power_Sector.xlsx
Bhutan | BT | Punatsangchhu-II HP (PHP-II) — Full Commissioning | PWRHYDBTNXX | Hydropower | Hydro | 1020 | 2025 | Partially Operational – Ramp Up | DGPC / PHPA-II | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Kholongchhu Hydropower Project | PWRHYDBTNXX | Hydropower | Hydro | 600 | 2027 | Under Construction | DGPC / Kholongchhu Hydro Energy Ltd. (JV with Satluj Jal Vidyut Nigam) | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Bunakha Reservoir Hydropower Project | PWRHYDBTNXX | Hydropower | Hydro | 2400 | 2030 | Feasibility / Planning | DGPC / Government of Bhutan | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Chamkharchhu I Hydropower Project | PWRHYDBTNXX | Hydropower | Hydro | 670 | 2028 | Pre-Construction / DPR | DGPC / Chamkharchhu Hydropower Ltd. | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Dorjilung Hydropower Project | PWRHYDBTNXX | Hydropower | Hydro | 1125 | 2030 | Feasibility Complete | DGPC / JV (India partner TBD) | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Nikachhu HP — Full Output Stabilization | PWRHYDBTNXX | Hydropower | Hydro | 118 | 2025 | Operational (stabilizing) | DGPC | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Rooftop Solar Program (National) | PWRSPVBTNXX | Solar PV | Solar | 50 | 2030 | Rolling / Ongoing | Private / Households / BPC | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Mini/Micro Hydel Expansion | PWRHYDBTNXX | Hydropower | Hydro | 20 |  | Rolling | Local Communities / BPC | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Shakti Hydropower Project (proposed) | PWRHYDBTNXX | Hydropower | Hydro | 2585 | 2035 | Feasibility | Government of Bhutan / India JV | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Amochhu Reservoir Project | PWRHYDBTNXX | Hydropower | Hydro | 620 | 2030 | Feasibility | Government of Bhutan | Bhutan_Power_Infrastructure.xlsx
India | IN_E | Hiranmaye TPP | PWRCOAINDEA | Coal Power Plant | Coal | 150 | 2035 | Pipeline | Hiranmaye Energy Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_E | Kandarei TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1050 | 2035 | Pipeline | KVK Nilanchal Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_E | Kodarma TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1600 | 2028 | Pipeline | Damodar Valley Corporation(DVC) | India_Electricity_Infrastructure.xlsx
India | IN_E | Lanco Babandh TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1320 | 2035 | Pipeline | LBP Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_E | Malibrahmani Power Station | PWRCOAINDEA | Coal Power Plant | Coal | 1050 | 2013 | Pipeline | Jindal Power Ltd. (JPL) | India_Electricity_Infrastructure.xlsx
India | IN_E | Matrishri Usha Jayaswal TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1080 | 2035 | Pipeline | Corporate Power Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_E | New NabiNagar TPP (Majhiyan) | PWRCOAINDEA | Coal Power Plant | Coal | 2400 | 2029 | Pipeline | NTPC Ltd. & BSPGCL (NPGCL) | India_Electricity_Infrastructure.xlsx
India | IN_E | Patratu TPS | PWRCOAINDEA | Coal Power Plant | Coal | 1600 | 2026 | Pipeline | Patratu Vidyut Utpadan Nigam Limited | India_Electricity_Infrastructure.xlsx
India | IN_E | Raghunathpur TPS | PWRCOAINDEA | Coal Power Plant | Coal | 1320 | 2028 | Pipeline | Damodar Valley Corporation(DVC) | India_Electricity_Infrastructure.xlsx
India | IN_E | Sagardighi TPS | PWRCOAINDEA | Coal Power Plant | Coal | 660 | 2025 | Pipeline | West Bengal Power Development Corp. Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_E | Siriya TPS or Banka Power Project | PWRCOAINDEA | Coal Power Plant | Coal | 2640 | 2035 | Pipeline | Jas Infrastructure and Power | India_Electricity_Infrastructure.xlsx
India | IN_E | Super Critical Buxar Thermal Power Plant | PWRCOAINDEA | Coal Power Plant | Coal | 660 | 2026 | Pipeline | Satlaj Jal Vidhut Nigam Limited (SJVN Ltd) | India_Electricity_Infrastructure.xlsx
India | IN_E | Talabira TPP | PWRCOAINDEA | Coal Power Plant | Coal | 2400 | 2030 | Pipeline | NLC India Limited (formerly Neyveli Lignite Corp. Ltd.) | India_Electricity_Infrastructure.xlsx
India | IN_E | Talcher or Kaniha Talcher STPS | PWRCOAINDEA | Coal Power Plant | Coal | 1320 | 2027 | Pipeline | NTPC Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_E | Tori TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1800 | 2035 | Pipeline | Essar Power Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_E | Bhasmey Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 51 | 2035 | Pipeline | Gati Infrastructure Pvt. Limited (GIPL) | India_Electricity_Infrastructure.xlsx
India | IN_E | Panan Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 300 | 2035 | Pipeline | Himgiri Hydro Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_E | Rammam III Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 120 | 2029 | Pipeline | National Thermal Power Corporation Limited (NTPC) | India_Electricity_Infrastructure.xlsx
India | IN_E | Rangit-II Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 66 | 2025 | Pipeline | Sikkim Hydro Power Limited | India_Electricity_Infrastructure.xlsx
India | IN_E | Rangit-IV Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 120 | 2026 | Pipeline | Jal Power Corporation Limited | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta- VI Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 500 | 2027 | Pipeline | National Hydroelectric Power Corporation (NHPC) | India_Electricity_Infrastructure.xlsx
India | IN_E | Damodar Valley Corporation (DVC) Jharkhand 10.0 | PWRSPVINDEA | Solar PV | Solar | 10 | 2026 | Pipeline | Damodar Valley Corporation (DVC) | India_Electricity_Infrastructure.xlsx
India | IN_E | GVREL Jharkhand 155.0 | PWRSPVINDEA | Solar PV | Solar | 155 | 2025 | Pipeline | GVREL | India_Electricity_Infrastructure.xlsx
India | IN_E | GVREL Jharkhand 80.0 | PWRSPVINDEA | Solar PV | Solar | 80 | 2025 | Pipeline | GVREL | India_Electricity_Infrastructure.xlsx
India | IN_E | GVREL West Bengal 75.0 | PWRSPVINDEA | Solar PV | Solar | 75 | 2025 | Pipeline | GVREL | India_Electricity_Infrastructure.xlsx
India | IN_E | NHPC Limited Odisha 40.0 | PWRSPVINDEA | Solar PV | Solar | 40 | 2025 | Pipeline | NHPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_E | SECI Jharkhand 100.0 | PWRSPVINDEA | Solar PV | Solar | 100 | 2027 | Pipeline | SECI | India_Electricity_Infrastructure.xlsx
India | IN_E | SJVN GREEN ENERGY LIMITED Bihar 75.0 | PWRSPVINDEA | Solar PV | Solar | 75 | 2023 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_E | SPD Jharkhand 8.0 | PWRSPVINDEA | Solar PV | Solar | 8 | 2025 | Pipeline | SPD | India_Electricity_Infrastructure.xlsx
India | IN_E | SPD West Bengal 10.0 | PWRSPVINDEA | Solar PV | Solar | 10 | 2024 | Pipeline | SPD | India_Electricity_Infrastructure.xlsx
India | IN_E | SPD West Bengal 14.0 | PWRSPVINDEA | Solar PV | Solar | 14 | 2024 | Pipeline | SPD | India_Electricity_Infrastructure.xlsx
India | IN_NE | Dibang Hydro Power Project | PWRHYDINDNE | Hydropower | Hydro | 2880 | 2032 | Pipeline | National Hydroelectric Power Corporation (NHPC) | India_Electricity_Infrastructure.xlsx
India | IN_NE | HEO Hydro Electric Project | PWRHYDINDNE | Hydropower | Hydro | 240 | 2029 | Pipeline | North Eastern Electric Power Corporation Ltd.(NEEPCO) and Government of Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lower Kopili Hydro Power Project | PWRHYDINDNE | Hydropower | Hydro | 120 | 2026 | Pipeline | Assam Power Generation Corporation Limited (APGCL) | India_Electricity_Infrastructure.xlsx
India | IN_NE | Subansiri Lower Hydro Power Project | PWRHYDINDNE | Hydropower | Hydro | 1750 | 2026 | Pipeline | National Hydroelectric Power Corporation (NHPC) | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tato-I Hydro Electric Project | PWRHYDINDNE | Hydropower | Hydro | 186 | 2029 | Pipeline | North Eastern Electric Power Corporation Ltd.(NEEPCO) and Government of Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | SJVN GREEN ENERGY LIMITED Assam 50.0 | PWRSPVINDNE | Solar PV | Solar | 50 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_NE | SJVN GREEN ENERGY LIMITED Assam 70.0 | PWRSPVINDNE | Solar PV | Solar | 70 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_N | Barsingar Lignite TPP | PWRCOAINDNO | Coal Power Plant | Coal | 250 | 2035 | Pipeline | NLC India Limited (formerly Neyveli Lignite Corp. Ltd.) | India_Electricity_Infrastructure.xlsx
India | IN_N | Bithnok TPP | PWRCOAINDNO | Coal Power Plant | Coal | 250 | 2035 | Pipeline | Rajasthan Rajya Vidyut Utpadan Nigam Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghatampur TPP | PWRCOAINDNO | Coal Power Plant | Coal | 660 | 2026 | Pipeline | NLC & UPRVUNL | India_Electricity_Infrastructure.xlsx
India | IN_N | Singrauli STPS | PWRCOAINDNO | Coal Power Plant | Coal | 1600 | 2029 | Pipeline | NTPC Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_N | Yamuna Nagar or Deenbandhu Chotu Ram TPS | PWRCOAINDNO | Coal Power Plant | Coal | 800 | 2029 | Pipeline | Haryana Power Generation Corp. Ltd.(HPGCL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Chanju-III Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 48 | 2027 | Pipeline | Himachal Pradesh Power Corporation Limited (HPPCL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhaulasidh Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 66 | 2027 | Pipeline | Satluj Jal Vidyut Nigam Limited (SJVNL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Kiru Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 624 | 2026 | Pipeline | Chenab Valley Power Projects Private Limited (CVPPL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Kwar Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 540 | 2028 | Pipeline | Chenab Valley Power Projects Private Limited (CVPPL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Lakhwar Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 300 | 2031 | Pipeline | Uttarakhand Jal Vidyut Nigam Limited (UJVNL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Lata Tapovan Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 171 | 2035 | Pipeline | National Thermal Power Corporation Limited (NTPC) | India_Electricity_Infrastructure.xlsx
India | IN_N | Lower Kalnai Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 48 | 2035 | Pipeline | J&K State Power Development Corporation Limited (JKSPDC) | India_Electricity_Infrastructure.xlsx
India | IN_N | Luhri Stage-I Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 210 | 2030 | Pipeline | Satluj Jal Vidyut Nigam Limited (SJVNL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Pakal Dul Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 1000 | 2026 | Pipeline | Chenab Valley Power Projects Private Limited (CVPPL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Parnai Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 37.5 | 2027 | Pipeline | J&K State Power Development Corporation Limited (JKSPDC) | India_Electricity_Infrastructure.xlsx
India | IN_N | Phata Byung Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 76 | 2035 | Pipeline | Lanco Mandakini Hydro Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Ratle Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 850 | 2028 | Pipeline | Ratle Hydro Electric Project Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Shahpurkandi Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 206 | 2027 | Pipeline | Punjab State Power Corporation Limited (PSPCL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Shongtong Karcham Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 450 | 2028 | Pipeline | Himachal Pradesh Power Corporation Limited (HPPCL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunni Dam Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 382 | 2029 | Pipeline | Satluj Jal Vidyut Nigam Limited (SJVNL) | India_Electricity_Infrastructure.xlsx
India | IN_N | Tangnu Romai- I Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 44 | 2035 | Pipeline | Tangu Romai Power Generation | India_Electricity_Infrastructure.xlsx
India | IN_N | Tapovan Vishnugad Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 520 | 2029 | Pipeline | National Thermal Power Corporation Limited (NTPC) | India_Electricity_Infrastructure.xlsx
India | IN_N | Tehri Pumped Storage Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 250 | 2026 | Pipeline | Tehri Hydro Development Corporation (THDC) | India_Electricity_Infrastructure.xlsx
India | IN_N | Tidong-I Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 150 | 2026 | Pipeline | Statkraft India Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Vishnugad Pipalkoti Hydro Power Project | PWRHYDINDNO | Hydropower | Hydro | 444 | 2027 | Pipeline | Tehri Hydro Development Corporation (THDC) | India_Electricity_Infrastructure.xlsx
India | IN_N | Gorakhpur Haryana Anu Vidyut Pariyojana | PWRURNINDNO | Nuclear Power Plant | Nuclear | 1400 | 2029 | Pipeline | Nuclear Power Corporation of India | India_Electricity_Infrastructure.xlsx
India | IN_N | Rajasthan Atomic Power Station | PWRURNINDNO | Nuclear Power Plant | Nuclear | 700 | 2026 | Pipeline | Nuclear Power Corporation of India | India_Electricity_Infrastructure.xlsx
India | IN_N | BETA Combined Cycle Power Plant Module I | PWRNGSINDNO | Natural Gas CC/OC | Oil & Gas | 225 | 2035 | Pipeline | Beta Infratech Pvt. Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_N | ABC RENEWABLE ENERGY RJ-01 Private Limited Rajasthan 400.0 | PWRSPVINDNO | Solar PV | Solar | 400 | 2024 | Pipeline | ABC RENEWABLE ENERGY RJ-01 Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ABC RJ LAND 01 Private Limited Rajasthan 380.0 | PWRSPVINDNO | Solar PV | Solar | 380 | 2024 | Pipeline | ABC RJ LAND 01 Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ABU RENEWABLES INDIA PRIVATE LIMITED Rajasthan 340.0 | PWRSPVINDNO | Solar PV | Solar | 340 | 2026 | Pipeline | ABU RENEWABLES INDIA PRIVATE LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_N | ACME Sun Power Private Limited Rajasthan 320.0 | PWRSPVINDNO | Solar PV | Solar | 320 | 2026 | Pipeline | ACME Sun Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ACME Surya Power Private Limited Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2026 | Pipeline | ACME Surya Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ACME Venus Urja Private Limited Rajasthan 400.0 | PWRSPVINDNO | Solar PV | Solar | 400 | 2026 | Pipeline | ACME Venus Urja Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | AM Green Energy Private Limited, Bikaner Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | AM Green Energy Private Limited, Bikaner | India_Electricity_Infrastructure.xlsx
India | IN_N | Acme Renewtech Fifth Private Limited Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2027 | Pipeline | Acme Renewtech Fifth Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Eighteen Limited (AREH18L) Rajasthan 50.0 | PWRSPVINDNO | Solar PV | Solar | 50 | 2027 | Pipeline | Adani Renewable Energy Holding Eighteen Limited (AREH18L) | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2028 | Pipeline | Adani Renewable Energy Holding Four Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 284.0 | PWRSPVINDNO | Solar PV | Solar | 284 | 2030 | Pipeline | Adani Renewable Energy Holding Four Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 500.0 | PWRSPVINDNO | Solar PV | Solar | 1500 | 2025 | Pipeline | Adani Renewable Energy Holding Four Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 717.0 | PWRSPVINDNO | Solar PV | Solar | 717 | 2029 | Pipeline | Adani Renewable Energy Holding Four Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 765.0 | PWRSPVINDNO | Solar PV | Solar | 765 | 2030 | Pipeline | Adani Renewable Energy Holding Four Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Seventeen Private Limited Rajasthan 600.0 | PWRSPVINDNO | Solar PV | Solar | 600 | 2025 | Pipeline | Adani Renewable Energy Holding Seventeen Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Park Rajasthan Limited Rajasthan 1000.0 | PWRSPVINDNO | Solar PV | Solar | 2000 | 2030 | Pipeline | Adani Renewable Energy Park Rajasthan Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Park Rajasthan Limited – AREPRL – a JV of State Govt. & Adani Renewable Energy Park Limited Rajasthan 266.0 | PWRSPVINDNO | Solar PV | Solar | 266 | 2025 | Pipeline | Adani Renewable Energy Park Rajasthan Limited – AREPRL – a JV of State Govt. & Adani Renewable Energy Park Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Solar Energy AP Three Limited Rajasthan 150.0 | PWRSPVINDNO | Solar PV | Solar | 150 | 2026 | Pipeline | Adani Solar Energy AP Three Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Amplus Tungabhadra Private Limited Uttar Pradesh 50.0 | PWRSPVINDNO | Solar PV | Solar | 50 | 2025 | Pipeline | Amplus Tungabhadra Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Apraava Energy Private Limited Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2026 | Pipeline | Apraava Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Apraava Energy Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Apraava Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Apraava Energy Private Limited Rajasthan 50.0 | PWRSPVINDNO | Solar PV | Solar | 50 | 2026 | Pipeline | Apraava Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Auxo Sunlight Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 600 | 2026 | Pipeline | Auxo Sunlight Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Avaada RJSustainable Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2028 | Pipeline | Avaada RJSustainable Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Avaada RJSustainable Private Limited Rajasthan 700.0 | PWRSPVINDNO | Solar PV | Solar | 700 | 2030 | Pipeline | Avaada RJSustainable Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Avaada Surya Power Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Avaada Surya Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Avaada Suryaenergy Private Limited Rajasthan 1100.0 | PWRSPVINDNO | Solar PV | Solar | 1100 | 2030 | Pipeline | Avaada Suryaenergy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | CESC Limited (Developer Company) Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2027 | Pipeline | CESC Limited (Developer Company) | India_Electricity_Infrastructure.xlsx
India | IN_N | EG Mega Urja Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | EG Mega Urja Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | EG Saur Urja Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | EG Saur Urja Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Energizent Power Private Limited Rajasthan 205.0 | PWRSPVINDNO | Solar PV | Solar | 205 | 2035 | Pipeline | Energizent Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Enfinity Global Surya Kiran Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Enfinity Global Surya Kiran Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Frugal Energy Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Frugal Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Furies Solren Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Furies Solren Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Furies Solren Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Furies Solren | India_Electricity_Infrastructure.xlsx
India | IN_N | Hazel Hybren Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Hazel Hybren Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Helia Energy Park Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Helia Energy Park Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | IB Vogt Solar Seven Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 600 | 2025 | Pipeline | IB Vogt Solar Seven Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Inox Wind Energy Limited Rajasthan 500.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | Inox Wind Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Izhma Solar Private Limited Rajasthan 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2028 | Pipeline | Izhma Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | JGRJ One Solar Private Limited Rajasthan 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2026 | Pipeline | JGRJ One Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | JGRJ One Solar Private Limited Rajasthan 50.0 | PWRSPVINDNO | Solar PV | Solar | 50 | 2026 | Pipeline | JGRJ One Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | JGRJ Two Solar Private Limited Rajasthan 400.0 | PWRSPVINDNO | Solar PV | Solar | 400 | 2026 | Pipeline | JGRJ Two Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Beta Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Juniper Green Beta Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Cosmic Private Limited Rajasthan 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2025 | Pipeline | Juniper Green Cosmic Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Cosmic Private Limited Rajasthan 150.0 | PWRSPVINDNO | Solar PV | Solar | 150 | 2026 | Pipeline | Juniper Green Cosmic Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Energy Private Limited Rajasthan 130.0 | PWRSPVINDNO | Solar PV | Solar | 130 | 2030 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Energy Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2027 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Energy Private Limited Rajasthan 50.0 | PWRSPVINDNO | Solar PV | Solar | 50 | 2027 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green India Six Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2028 | Pipeline | Juniper Green India Six Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Stellar Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Juniper Green Stellar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Nirjara Energy Private Limited Rajasthan 50.0 | PWRSPVINDNO | Solar PV | Solar | 50 | 2025 | Pipeline | Juniper Nirjara Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Khidrat Renewable Energy Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2025 | Pipeline | Khidrat Renewable Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | M/s Hinduja Renewables Energy Private Limited (LoA has been cancelled) Uttar Pradesh 600.0 | PWRSPVINDNO | Solar PV | Solar | 600 | 2026 | Pipeline | M/s Hinduja Renewables Energy Private Limited (LoA has been cancelled) | India_Electricity_Infrastructure.xlsx
India | IN_N | M/s. Essel Surya Urja Company of Rajasthan Limited -ESUCRL- A JV of Rajasthan State Govt. and Essel Infraprojects Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2027 | Pipeline | M/s. Essel Surya Urja Company of Rajasthan Limited -ESUCRL- A JV of Rajasthan State Govt. and Essel Infraprojects Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Martial Solren Private Limited Rajasthan 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2025 | Pipeline | Martial Solren Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | NEEPCO Limited (SPD) Rajasthan 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2025 | Pipeline | NEEPCO Limited (SPD) | India_Electricity_Infrastructure.xlsx
India | IN_N | NEEPCO Limited (SPD) Rajasthan 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2025 | Pipeline | NEEPCO Limited (SPD) | India_Electricity_Infrastructure.xlsx
India | IN_N | NHPC Limited Rajasthan 192.86 | PWRSPVINDNO | Solar PV | Solar | 192.86 | 2023 | Pipeline | NHPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Limited Rajasthan 78.0 | PWRSPVINDNO | Solar PV | Solar | 78 | 2025 | Pipeline | NTPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Limited Uttar Pradesh 20.0 | PWRSPVINDNO | Solar PV | Solar | 20 | 2025 | Pipeline | NTPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC REL Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2026 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC REL Rajasthan 325.0 | PWRSPVINDNO | Solar PV | Solar | 650 | 2026 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC REL Rajasthan 500.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2025 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Renewables Energy Limited Uttar Pradesh 600.0 | PWRSPVINDNO | Solar PV | Solar | 600 | 2026 | Pipeline | NTPC Renewables Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Renewables Energy Limited Uttar Pradesh 800.0 | PWRSPVINDNO | Solar PV | Solar | 800 | 2026 | Pipeline | NTPC Renewables Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Others Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 600 | 2027 | Pipeline | Others | India_Electricity_Infrastructure.xlsx
India | IN_N | Proteus Energy Private Limited Rajasthan 217.0 | PWRSPVINDNO | Solar PV | Solar | 217 | 2026 | Pipeline | Proteus Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Purvah Green Power Private Limited (Developer Company) Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 900 | 2027 | Pipeline | Purvah Green Power Private Limited (Developer Company) | India_Electricity_Infrastructure.xlsx
India | IN_N | Radiant Star Solar Park Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Radiant Star Solar Park Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Dinkar Jyoti Private Limited Rajasthan 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2025 | Pipeline | ReNew Dinkar Jyoti Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Dinkar Urja Private Limited Rajasthan 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2024 | Pipeline | ReNew Dinkar Urja Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Samir Shakti Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2025 | Pipeline | ReNew Samir Shakti Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar (Shakti Five) Private Limited Rajasthan 400.0 | PWRSPVINDNO | Solar PV | Solar | 400 | 2025 | Pipeline | ReNew Solar (Shakti Five) Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar (Shakti Six) Private Limited (400+400) Rajasthan 400.0 | PWRSPVINDNO | Solar PV | Solar | 800 | 2029 | Pipeline | ReNew Solar (Shakti Six) Private Limited (400+400) | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar (Shakti Six) Private Limited Rajasthan 1000.0 | PWRSPVINDNO | Solar PV | Solar | 1000 | 2026 | Pipeline | ReNew Solar (Shakti Six) Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar (Shakti Three) Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2025 | Pipeline | ReNew Solar (Shakti Three) Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power P. Limited Rajasthan 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2030 | Pipeline | ReNew Solar Power P. Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power P. Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 600 | 2030 | Pipeline | ReNew Solar Power P. Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power P. Limited Rajasthan 400.0 | PWRSPVINDNO | Solar PV | Solar | 400 | 2027 | Pipeline | ReNew Solar Power P. Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited (2 x 300) Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 600 | 2026 | Pipeline | ReNew Solar Power Private Limited (2 x 300) | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 100.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2030 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 150.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2027 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 200.0 | PWRSPVINDNO | Solar PV | Solar | 1000 | 2030 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2030 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 3600 | 2027 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 400.0 | PWRSPVINDNO | Solar PV | Solar | 400 | 2030 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 70.0 | PWRSPVINDNO | Solar PV | Solar | 140 | 2027 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Surya Jyoti Private Limited Rajasthan 210.0 | PWRSPVINDNO | Solar PV | Solar | 210 | 2025 | Pipeline | ReNew Surya Jyoti Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Surya Pratap Private Limited Rajasthan 210.0 | PWRSPVINDNO | Solar PV | Solar | 210 | 2025 | Pipeline | ReNew Surya Pratap Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Renew Sun Power Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Renew Sun Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Resco Global Wind Services Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2027 | Pipeline | Resco Global Wind Services Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Resco Global Wind Services Private Limited Rajasthan 76.0 | PWRSPVINDNO | Solar PV | Solar | 76 | 2035 | Pipeline | Resco Global Wind Services Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Himachal Pradesh 15.0 | PWRSPVINDNO | Solar PV | Solar | 15 | 2024 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Punjab 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Rajasthan 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Rajasthan 370.1 | PWRSPVINDNO | Solar PV | Solar | 370.1 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_N | SPV - Deshraj Solar Energy Private Limited Rajasthan 150.0 | PWRSPVINDNO | Solar PV | Solar | 150 | 2027 | Pipeline | SPV - Deshraj Solar Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | SPV - HRP Green Power Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | SPV - HRP Green Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | SRIPL5, SRIPL8, SRIPL9 Rajasthan 200.0 | PWRSPVINDNO | Solar PV | Solar | 800 | 2026 | Pipeline | SRIPL5, SRIPL8, SRIPL9 | India_Electricity_Infrastructure.xlsx
India | IN_N | SRIPL5, SRIPL8, SRIPL9 Rajasthan 50.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2026 | Pipeline | SRIPL5, SRIPL8, SRIPL9 | India_Electricity_Infrastructure.xlsx
India | IN_N | Saimaa Solar Private Limited Rajasthan 150.0 | PWRSPVINDNO | Solar PV | Solar | 150 | 2026 | Pipeline | Saimaa Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Shikhar Surya (One) Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2025 | Pipeline | Shikhar Surya (One) Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Sone Solar Private Limited Punjab 40.0 | PWRSPVINDNO | Solar PV | Solar | 40 | 2025 | Pipeline | Sone Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Sourya Manthan Renewable Energy Private Limited Rajasthan 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2026 | Pipeline | Sourya Manthan Renewable Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Sprng Power Private Limited Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2026 | Pipeline | Sprng Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunbreeze Renewables Nine Private Limited Rajasthan 1000.0 | PWRSPVINDNO | Solar PV | Solar | 1000 | 2026 | Pipeline | Sunbreeze Renewables Nine Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunbreeze Renewables Nine Private Limited Rajasthan 400.0 | PWRSPVINDNO | Solar PV | Solar | 400 | 2026 | Pipeline | Sunbreeze Renewables Nine Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | TEQ Green Power XIII Private Limited Rajasthan 120.0 | PWRSPVINDNO | Solar PV | Solar | 120 | 2035 | Pipeline | TEQ Green Power XIII Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | TEQ Green Power XVI Private Limited Rajasthan 50.0 | PWRSPVINDNO | Solar PV | Solar | 50 | 2035 | Pipeline | TEQ Green Power XVI Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | TP SAURYA LIMITED Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2024 | Pipeline | TP SAURYA LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_N | Tejorupa Renewables India Project Private Limited Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2026 | Pipeline | Tejorupa Renewables India Project Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Tepsol Sun Sparkle Private Limited Rajasthan 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Tepsol Sun Sparkle Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Acme Renewtech Sixth Private Limited Gujarat, Andhra Pradesh & Rajasthan 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2035 | Pipeline | Acme Renewtech Sixth Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five A Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | Adani Green Energy Twenty Five A Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five B Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 1000 | 2035 | Pipeline | Adani Green Energy Twenty Five B Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five B Limited N.A. 83.0 | PWRSPVINDNO | Solar PV | Solar | 83 | 2026 | Pipeline | Adani Green Energy Twenty Five B Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five C Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2025 | Pipeline | Adani Green Energy Twenty Five C Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | Adani Green Energy Twenty Five Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Four A Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | Adani Green Energy Twenty Four A Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Four B Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | Adani Green Energy Twenty Four B Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Four Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | Adani Green Energy Twenty Four Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Seven A Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2026 | Pipeline | Adani Green Energy Twenty Seven A Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six A Limited N.A. 167.0 | PWRSPVINDNO | Solar PV | Solar | 167 | 2025 | Pipeline | Adani Green Energy Twenty Six A Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six A Limited N.A. 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2025 | Pipeline | Adani Green Energy Twenty Six A Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six A Limited N.A. 234.0 | PWRSPVINDNO | Solar PV | Solar | 234 | 2035 | Pipeline | Adani Green Energy Twenty Six A Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six A Limited N.A. 50.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2025 | Pipeline | Adani Green Energy Twenty Six A Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six B Limited N.A. 134.0 | PWRSPVINDNO | Solar PV | Solar | 134 | 2026 | Pipeline | Adani Green Energy Twenty Six B Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six B Limited N.A. 150.0 | PWRSPVINDNO | Solar PV | Solar | 150 | 2026 | Pipeline | Adani Green Energy Twenty Six B Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six B Limited N.A. 167.0 | PWRSPVINDNO | Solar PV | Solar | 167 | 2026 | Pipeline | Adani Green Energy Twenty Six B Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six B Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2025 | Pipeline | Adani Green Energy Twenty Six B Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Five Limited N.A. 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2035 | Pipeline | Adani Renewable Energy Fifty Five Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Five Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2035 | Pipeline | Adani Renewable Energy Fifty Five Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Five Limited N.A. 67.0 | PWRSPVINDNO | Solar PV | Solar | 67 | 2035 | Pipeline | Adani Renewable Energy Fifty Five Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Five Limited N.A. 99.0 | PWRSPVINDNO | Solar PV | Solar | 99 | 2035 | Pipeline | Adani Renewable Energy Fifty Five Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Seven Limited N.A. 100.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2035 | Pipeline | Adani Renewable Energy Fifty Seven Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Seven Limited N.A. 150.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2035 | Pipeline | Adani Renewable Energy Fifty Seven Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Seven Limited N.A. 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2035 | Pipeline | Adani Renewable Energy Fifty Seven Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Seven Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | Adani Renewable Energy Fifty Seven Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Six Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | Adani Renewable Energy Fifty Six Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Azure Power Fifty One Private Limited N.A. 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2027 | Pipeline | Azure Power Fifty One Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Azure Power Fifty One Private Limited N.A. 50.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2027 | Pipeline | Azure Power Fifty One Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Azure Power Fifty Two Private Limited N.A. 167.0 | PWRSPVINDNO | Solar PV | Solar | 167 | 2027 | Pipeline | Azure Power Fifty Two Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Azure Power Fifty Two Private Limited N.A. 333.0 | PWRSPVINDNO | Solar PV | Solar | 333 | 2027 | Pipeline | Azure Power Fifty Two Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Damodar Valley Corporation (DVC) Jharkand & West Bengal 10.0 | PWRSPVINDNO | Solar PV | Solar | 10 | 2026 | Pipeline | Damodar Valley Corporation (DVC) | India_Electricity_Infrastructure.xlsx
India | IN_N | Eden Renewable Bercy Private Limited N.A. 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2027 | Pipeline | Eden Renewable Bercy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Gorbea Solar Private Limited N.A. 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2025 | Pipeline | Gorbea Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Green Infra Renewable Projects Limited N.A. 298.0 | PWRSPVINDNO | Solar PV | Solar | 298 | 2027 | Pipeline | Green Infra Renewable Projects Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Green Valley Renewable Energy GVREL - A JV of DVC & NTPC Green Energy Limited Jharkand & West Bengal 310.0 | PWRSPVINDNO | Solar PV | Solar | 310 | 2025 | Pipeline | Green Valley Renewable Energy GVREL - A JV of DVC & NTPC Green Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | JSW Renew Energy Eleven Limited N.A. 700.0 | PWRSPVINDNO | Solar PV | Solar | 700 | 2026 | Pipeline | JSW Renew Energy Eleven Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Jakson Limited N.A. 50.0 | PWRSPVINDNO | Solar PV | Solar | 50 | 2027 | Pipeline | Jakson Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Energy Private Limited N.A. 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2028 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | MRS Green Energy Private Limited N.A. 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2026 | Pipeline | MRS Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Renewable Energy Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2027 | Pipeline | NTPC Renewable Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Renewable Energy Limited N.A. 500.0 | PWRSPVINDNO | Solar PV | Solar | 500 | 2035 | Pipeline | NTPC Renewable Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Pace Digitek Private Limited N.A. 100.0 | PWRSPVINDNO | Solar PV | Solar | 100 | 2026 | Pipeline | Pace Digitek Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Pavni (Raj) Solar Private Limited (erstwhile: AEW India North One Private Limited) N.A. 200.0 | PWRSPVINDNO | Solar PV | Solar | 200 | 2027 | Pipeline | Pavni (Raj) Solar Private Limited (erstwhile: AEW India North One Private Limited) | India_Electricity_Infrastructure.xlsx
India | IN_N | Project Nine Renewable Power Private Limited Rajasthan, Karnataka & Andhra Pradesh 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2026 | Pipeline | Project Nine Renewable Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Reliance NU Suntech Private Limited N.A. 930.0 | PWRSPVINDNO | Solar PV | Solar | 930 | 2027 | Pipeline | Reliance NU Suntech Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | SAEL Industries Limited N.A. 250.0 | PWRSPVINDNO | Solar PV | Solar | 250 | 2027 | Pipeline | SAEL Industries Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | SAEL SOLAR MHP1 Private Limited N.A. 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2025 | Pipeline | SAEL SOLAR MHP1 Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | SAEL SOLAR MHP2 Private Limited N.A. 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2025 | Pipeline | SAEL SOLAR MHP2 Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Punjab & Himachal Pradesh 18.0 | PWRSPVINDNO | Solar PV | Solar | 18 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_N | Sembcorp Green Infra Private Limited N.A. 150.0 | PWRSPVINDNO | Solar PV | Solar | 150 | 2027 | Pipeline | Sembcorp Green Infra Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunsure Solarpark Fourteen Private Limited N.A. 300.0 | PWRSPVINDNO | Solar PV | Solar | 300 | 2027 | Pipeline | Sunsure Solarpark Fourteen Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_N | The Singareni Collieries Company Limited N.A. 76.0 | PWRSPVINDNO | Solar PV | Solar | 76 | 2027 | Pipeline | The Singareni Collieries Company Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavanapadu Thermal Power Plant Phase I | PWRCOAINDSO | Coal Power Plant | Coal | 1320 | 2035 | Pipeline | East Coast Energy Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_S | Ennore SEZ Expansion SCTPP | PWRCOAINDSO | Coal Power Plant | Coal | 1320 | 2026 | Pipeline | Tamil Nadu Generation & Distribution Corp. Ltd. (TANGEDCO) | India_Electricity_Infrastructure.xlsx
India | IN_S | North Chennai TPS | PWRCOAINDSO | Coal Power Plant | Coal | 800 | 2025 | Pipeline | Tamil Nadu Generation & Distribution Corp. Ltd. (TANGEDCO) | India_Electricity_Infrastructure.xlsx
India | IN_S | Singareni TPP | PWRCOAINDSO | Coal Power Plant | Coal | 800 | 2028 | Pipeline | The Singareni Collieries Co. Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin (P) TPP | PWRCOAINDSO | Coal Power Plant | Coal | 660 | 2035 | Pipeline | Ind Barath Power Infra Limited (IBPIL) | India_Electricity_Infrastructure.xlsx
India | IN_S | Udangudi Power Station | PWRCOAINDSO | Coal Power Plant | Coal | 1320 | 2026 | Pipeline | Tamil Nadu Generation & Distribution Corp. Ltd. (TANGEDCO) | India_Electricity_Infrastructure.xlsx
India | IN_S | Yadadri Thermal Power Station | PWRCOAINDSO | Coal Power Plant | Coal | 2400 | 2025 | Pipeline | Telangana State Power Generation Corp. Ltd. (TSGENCO) | India_Electricity_Infrastructure.xlsx
India | IN_S | Chitravathi Pumped Storage Project | PWRHYDINDSO | Hydropower | Hydro | 500 | 2026 | Pipeline | Adani Renewable Energy Forty-Two Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Gandikota Pumped Storage Project | PWRHYDINDSO | Hydropower | Hydro | 1000 | 2029 | Pipeline | Adani Renewable Energy Fifty-One Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Kundah Pumped Storage Phase-I, II & III | PWRHYDINDSO | Hydropower | Hydro | 500 | 2026 | Pipeline | Tamil Nadu Generation & Distribution Co. Limited (TANGEDCO) | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Sileru (Extension) Hydroelectric Power Project | PWRHYDINDSO | Hydropower | Hydro | 230 | 2026 | Pipeline | Andhra Pradesh Power Generation Corporation Limited (APGENCO) | India_Electricity_Infrastructure.xlsx
India | IN_S | Mankulam Hydro Power Project | PWRHYDINDSO | Hydropower | Hydro | 40 | 2027 | Pipeline | Kerala State Electricity Board (KSEB) | India_Electricity_Infrastructure.xlsx
India | IN_S | Polavaram Hydro Power Project | PWRHYDINDSO | Hydropower | Hydro | 960 | 2028 | Pipeline | Andhra Pradesh Power Generation Corporation Limited (APGENCO) | India_Electricity_Infrastructure.xlsx
India | IN_S | Saundatti Pumped Storage Project | PWRHYDINDSO | Hydropower | Hydro | 1600 | 2027 | Pipeline | Greenko KA01 IREP Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Sharavathy Pumped Storage Project | PWRHYDINDSO | Hydropower | Hydro | 2000 | 2029 | Pipeline | Karnataka Power Corporation Limited (KPCL) | India_Electricity_Infrastructure.xlsx
India | IN_S | Upper Sileru Pumped Storage Project | PWRHYDINDSO | Hydropower | Hydro | 1350 | 2029 | Pipeline | Andhra Pradesh Power Generation Corporation Limited (APGENCO) | India_Electricity_Infrastructure.xlsx
India | IN_S | BHAVINI PFBR Atomic Power Station | PWRURNINDSO | Nuclear Power Plant | Nuclear | 500 | 2024 | Pipeline | Bharatiya Nabhikiya Vidyut Nigam Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Kudankulam Atomic Power Project | PWRURNINDSO | Nuclear Power Plant | Nuclear | 4000 | 2025 | Pipeline | Nuclear Power Corporation of India | India_Electricity_Infrastructure.xlsx
India | IN_S | ACME Hybrid Urja Private Limited Karnataka 280.0 | PWRSPVINDSO | Solar PV | Solar | 280 | 2027 | Pipeline | ACME Hybrid Urja Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | ACME Omega Urja Private Limited Karnataka 300.0 | PWRSPVINDSO | Solar PV | Solar | 300 | 2035 | Pipeline | ACME Omega Urja Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | ACME Platinum Urja Private Limited Karnataka 350.0 | PWRSPVINDSO | Solar PV | Solar | 350 | 2027 | Pipeline | ACME Platinum Urja Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | APSPCL - a JV of NREDCAP, APGENCO & SECI Andhra Pradesh 100.0 | PWRSPVINDSO | Solar PV | Solar | 100 | 2025 | Pipeline | APSPCL - a JV of NREDCAP, APGENCO & SECI | India_Electricity_Infrastructure.xlsx
India | IN_S | APSPCL - a JV of NREDCAP, APGENCO & SECI Andhra Pradesh 750.0 | PWRSPVINDSO | Solar PV | Solar | 750 | 2026 | Pipeline | APSPCL - a JV of NREDCAP, APGENCO & SECI | India_Electricity_Infrastructure.xlsx
India | IN_S | Ayana Kadapa Renewable Power Private Limited Andhra Pradesh 250.0 | PWRSPVINDSO | Solar PV | Solar | 250 | 2026 | Pipeline | Ayana Kadapa Renewable Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Clean Renewable Energy Hybrid Eight Private Limited (SPV of Hero Solar Energy Private Limited) Karnataka 250.0 | PWRSPVINDSO | Solar PV | Solar | 250 | 2026 | Pipeline | Clean Renewable Energy Hybrid Eight Private Limited (SPV of Hero Solar Energy Private Limited) | India_Electricity_Infrastructure.xlsx
India | IN_S | INGEL Tamil Nadu 200.0 | PWRSPVINDSO | Solar PV | Solar | 200 | 2027 | Pipeline | INGEL | India_Electricity_Infrastructure.xlsx
India | IN_S | IRCON RENEWABLE POWER LIMITED Karnataka 100.0 | PWRSPVINDSO | Solar PV | Solar | 100 | 2026 | Pipeline | IRCON RENEWABLE POWER LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_S | NHPC Limited Andhra Pradesh 100.0 | PWRSPVINDSO | Solar PV | Solar | 100 | 2023 | Pipeline | NHPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | NHPC Limited Kerala 50.0 | PWRSPVINDSO | Solar PV | Solar | 50 | 2026 | Pipeline | NHPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | NTPC Limited Telangana 176.0 | PWRSPVINDSO | Solar PV | Solar | 176 | 2025 | Pipeline | NTPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Purvah Green Power Private Limited (Developer Company) Andhra Pradesh 300.0 | PWRSPVINDSO | Solar PV | Solar | 900 | 2035 | Pipeline | Purvah Green Power Private Limited (Developer Company) | India_Electricity_Infrastructure.xlsx
India | IN_S | Purvah Green Power Private Limited (Developer Company) Karnataka 300.0 | PWRSPVINDSO | Solar PV | Solar | 300 | 2028 | Pipeline | Purvah Green Power Private Limited (Developer Company) | India_Electricity_Infrastructure.xlsx
India | IN_S | Reliance Jio Infocomm Limited Karnataka 25.0 | PWRSPVINDSO | Solar PV | Solar | 25 | 2025 | Pipeline | Reliance Jio Infocomm Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | SECI Andhra Pradesh 300.0 | PWRSPVINDSO | Solar PV | Solar | 300 | 2026 | Pipeline | SECI | India_Electricity_Infrastructure.xlsx
India | IN_S | Sprng Soura Kiran Private Limited Andhra Pradesh 250.0 | PWRSPVINDSO | Solar PV | Solar | 250 | 2020 | Pipeline | Sprng Soura Kiran Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | TEQ Green Power XVI Private Limited Karnataka 70.0 | PWRSPVINDSO | Solar PV | Solar | 70 | 2035 | Pipeline | TEQ Green Power XVI Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 170.0 | PWRSPVINDSO | Solar PV | Solar | 170 | 2024 | Pipeline | Tata Power Renewable Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 200.0 | PWRSPVINDSO | Solar PV | Solar | 200 | 2026 | Pipeline | Tata Power Renewable Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 202.5 | PWRSPVINDSO | Solar PV | Solar | 202.5 | 2025 | Pipeline | Tata Power Renewable Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 300.0 | PWRSPVINDSO | Solar PV | Solar | 300 | 2025 | Pipeline | Tata Power Renewable Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 400.0 | PWRSPVINDSO | Solar PV | Solar | 400 | 2025 | Pipeline | Tata Power Renewable Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Akaltara TPS | PWRCOAINDWE | Coal Power Plant | Coal | 1800 | 2013 | Pipeline | JSW Energy Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Amaravati TPS | PWRCOAINDWE | Coal Power Plant | Coal | 1350 | 2035 | Pipeline | Indiabulls Realtech Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Avantha Bhandar TPS | PWRCOAINDWE | Coal Power Plant | Coal | 1600 | 2028 | Pipeline | Adani Power Co. Ltd. (APL) | India_Electricity_Infrastructure.xlsx
India | IN_W | Bijora Ghanmukh TPP | PWRCOAINDWE | Coal Power Plant | Coal | 600 | 2035 | Pipeline | Jinbhuvish Power Generation Pvt. Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Binjkote TPP | PWRCOAINDWE | Coal Power Plant | Coal | 600 | 2014 | Pipeline | SKS Power Generation Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Deveri TPP/ Visa Thermal Power Plant | PWRCOAINDWE | Coal Power Plant | Coal | 600 | 2035 | Pipeline | Visa Power Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Gadarwara STPS | PWRCOAINDWE | Coal Power Plant | Coal | 1600 | 2025 | Pipeline | NTPC Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Gorgi Thermal Power Project | PWRCOAINDWE | Coal Power Plant | Coal | 660 | 2035 | Pipeline | DB Power Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Koradi TPS | PWRCOAINDWE | Coal Power Plant | Coal | 1320 | 2029 | Pipeline | Maharashtra State Power Generation Co. Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Korba West or Hasdeo TPS | PWRCOAINDWE | Coal Power Plant | Coal | 1320 | 2029 | Pipeline | Chhattisgarh State Power Generation Co. Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Lanco Vidarbha TPP | PWRCOAINDWE | Coal Power Plant | Coal | 1320 | 2035 | Pipeline | LVP Pvt. Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Lara STPS | PWRCOAINDWE | Coal Power Plant | Coal | 1600 | 2027 | Pipeline | NTPC Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Mahan TPP | PWRCOAINDWE | Coal Power Plant | Coal | 3200 | 2026 | Pipeline | Essar Power M.P. Limited (ESSARPMPL) | India_Electricity_Infrastructure.xlsx
India | IN_W | Nasik RattanIndia or Nasik (P) TPS | PWRCOAINDWE | Coal Power Plant | Coal | 1350 | 2035 | Pipeline | Rattanindia Power Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Pathadi TPP | PWRCOAINDWE | Coal Power Plant | Coal | 1320 | 2012 | Pipeline | Adani Power Co. Ltd. (APL) | India_Electricity_Infrastructure.xlsx
India | IN_W | Raikheda TPP | PWRCOAINDWE | Coal Power Plant | Coal | 1600 | 2028 | Pipeline | Adani Power Co. Ltd. (APL) | India_Electricity_Infrastructure.xlsx
India | IN_W | Salora TPP | PWRCOAINDWE | Coal Power Plant | Coal | 135 | 2035 | Pipeline | Vandana Vidyut Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Singhitarai TPP | PWRCOAINDWE | Coal Power Plant | Coal | 600 | 2015 | Pipeline | Vedanta Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Sipat STPS | PWRCOAINDWE | Coal Power Plant | Coal | 800 | 2029 | Pipeline | NTPC Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Ukai TPS | PWRCOAINDWE | Coal Power Plant | Coal | 800 | 2029 | Pipeline | Gujarat State Energy Corp. Ltd. | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhavali Pumped Storage Project | PWRHYDINDWE | Hydropower | Hydro | 1500 | 2028 | Pipeline | JSW Energy PSP Two Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhivpuri Pumped Storage Project | PWRHYDINDWE | Hydropower | Hydro | 1000 | 2028 | Pipeline | Tata Power Company Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Koyna Left Bank PSS Hydro Power Project | PWRHYDINDWE | Hydropower | Hydro | 80 | 2035 | Pipeline | Water Resource Department, Government of Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MP30 Gandhi Sagar Pumped Storage Project | PWRHYDINDWE | Hydropower | Hydro | 1920 | 2026 | Pipeline | Greenko MP01 IREP Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Maheshwar Hydro Power Project | PWRHYDINDWE | Hydropower | Hydro | 400 | 2035 | Pipeline | Shree Maheshwar Hydel Power Corporation Limited (SMHPCL) | India_Electricity_Infrastructure.xlsx
India | IN_W | ADANI RENEWABLE ENERGY EIGHT LIMITED Gujarat 115.0 | PWRSPVINDWE | Solar PV | Solar | 115 | 2026 | Pipeline | ADANI RENEWABLE ENERGY EIGHT LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_W | Adani Renewable Energy Holding Four Limited Gujarat 500.0 | PWRSPVINDWE | Solar PV | Solar | 500 | 2024 | Pipeline | Adani Renewable Energy Holding Four Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Adani Renewable Energy Holding Four Limited Gujarat 750.0 | PWRSPVINDWE | Solar PV | Solar | 750 | 2026 | Pipeline | Adani Renewable Energy Holding Four Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Amplus Kaveri Solar Private Limited Maharashtra 100.0 | PWRSPVINDWE | Solar PV | Solar | 100 | 2025 | Pipeline | Amplus Kaveri Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Asnen Solar Private Limited Madhya Pradesh 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2027 | Pipeline | Asnen Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada GJGreen Private Limited Gujarat 300.0 | PWRSPVINDWE | Solar PV | Solar | 300 | 2026 | Pipeline | Avaada GJGreen Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada GJSolar Private Limited Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2026 | Pipeline | Avaada GJSolar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada GJSustainable Private Limited [Lakadiya-SECI] Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2025 | Pipeline | Avaada GJSustainable Private Limited [Lakadiya-SECI] | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada InClean Private Limited Gujarat 300.0 | PWRSPVINDWE | Solar PV | Solar | 300 | 2025 | Pipeline | Avaada InClean Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada KNClean Private Limited Madhya Pradesh 700.0 | PWRSPVINDWE | Solar PV | Solar | 700 | 2027 | Pipeline | Avaada KNClean Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada KNClean Private Limited Madhya Pradesh 900.0 | PWRSPVINDWE | Solar PV | Solar | 900 | 2027 | Pipeline | Avaada KNClean Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada MHRenewable1 Private Limited Maharashtra 500.0 | PWRSPVINDWE | Solar PV | Solar | 500 | 2026 | Pipeline | Avaada MHRenewable1 Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada MPSolar Private Limited Madhya Pradesh 500.0 | PWRSPVINDWE | Solar PV | Solar | 500 | 2027 | Pipeline | Avaada MPSolar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada MPSustainable Private Limited Madhya Pradesh 750.0 | PWRSPVINDWE | Solar PV | Solar | 750 | 2026 | Pipeline | Avaada MPSustainable Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada SunEnergy Private Limited Maharashtra 400.0 | PWRSPVINDWE | Solar PV | Solar | 400 | 2026 | Pipeline | Avaada SunEnergy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada Sustainable Urja Private Limited Maharashtra 73.0 | PWRSPVINDWE | Solar PV | Solar | 73 | 2026 | Pipeline | Avaada Sustainable Urja Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Clean Renewable Energy Hybrid Eleven Private Limited(SPV of Hero Solar Energy Private Limited) Gujarat 270.0 | PWRSPVINDWE | Solar PV | Solar | 270 | 2027 | Pipeline | Clean Renewable Energy Hybrid Eleven Private Limited(SPV of Hero Solar Energy Private Limited) | India_Electricity_Infrastructure.xlsx
India | IN_W | Ctrls Datacenters Limited Maharashtra 50.0 | PWRSPVINDWE | Solar PV | Solar | 50 | 2025 | Pipeline | Ctrls Datacenters Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Femund Solar Private Limited Gujarat 150.0 | PWRSPVINDWE | Solar PV | Solar | 150 | 2027 | Pipeline | Femund Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | GSECL Gujarat 1200.0 | PWRSPVINDWE | Solar PV | Solar | 1200 | 2025 | Pipeline | GSECL | India_Electricity_Infrastructure.xlsx
India | IN_W | GSECL Gujarat 3325.0 | PWRSPVINDWE | Solar PV | Solar | 3325 | 2026 | Pipeline | GSECL | India_Electricity_Infrastructure.xlsx
India | IN_W | GSECL Gujarat 600.0 | PWRSPVINDWE | Solar PV | Solar | 600 | 2025 | Pipeline | GSECL | India_Electricity_Infrastructure.xlsx
India | IN_W | GSECL Gujarat 700.0 | PWRSPVINDWE | Solar PV | Solar | 700 | 2027 | Pipeline | GSECL | India_Electricity_Infrastructure.xlsx
India | IN_W | HR Sabarmati Private Limited Gujarat 158.0 | PWRSPVINDWE | Solar PV | Solar | 158 | 2023 | Pipeline | HR Sabarmati Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | HR Sabarmati Private Limited Gujarat 52.0 | PWRSPVINDWE | Solar PV | Solar | 52 | 2022 | Pipeline | HR Sabarmati Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | INGEL Gujarat 600.0 | PWRSPVINDWE | Solar PV | Solar | 600 | 2025 | Pipeline | INGEL | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Gujarat 150.0 | PWRSPVINDWE | Solar PV | Solar | 150 | 2028 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2029 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Gujarat 600.0 | PWRSPVINDWE | Solar PV | Solar | 600 | 2028 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Maharashtra 350.0 | PWRSPVINDWE | Solar PV | Solar | 350 | 2028 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Maharashtra 50.0 | PWRSPVINDWE | Solar PV | Solar | 50 | 2028 | Pipeline | Juniper Green Energy Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Gem Private Limited Maharashtra 100.0 | PWRSPVINDWE | Solar PV | Solar | 100 | 2028 | Pipeline | Juniper Green Gem Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Gem Private Limited Maharashtra 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2028 | Pipeline | Juniper Green Gem Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY Eleventh Solar Private Limited Maharashtra 183.0 | PWRSPVINDWE | Solar PV | Solar | 183 | 2025 | Pipeline | MSKVY Eleventh Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY Fifth Solar Private Limited Maharashtra 103.0 | PWRSPVINDWE | Solar PV | Solar | 103 | 2025 | Pipeline | MSKVY Fifth Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY First Kusum Private Limited Maharashtra 185.0 | PWRSPVINDWE | Solar PV | Solar | 185 | 2025 | Pipeline | MSKVY First Kusum Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY Tenth Solar Private Limited Maharashtra 154.0 | PWRSPVINDWE | Solar PV | Solar | 154 | 2025 | Pipeline | MSKVY Tenth Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY Twentieth Solar Private Limited Maharashtra 129.0 | PWRSPVINDWE | Solar PV | Solar | 129 | 2025 | Pipeline | MSKVY Twentieth Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Maharashtra State Electricity Generating Co. Limited - MAHAGENCO Maharashtra 250.0 | PWRSPVINDWE | Solar PV | Solar | 250 | 2026 | Pipeline | Maharashtra State Electricity Generating Co. Limited - MAHAGENCO | India_Electricity_Infrastructure.xlsx
India | IN_W | Malaren Solar Private Limited Gujarat 150.0 | PWRSPVINDWE | Solar PV | Solar | 150 | 2026 | Pipeline | Malaren Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | NHPC Limited Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 400 | 2025 | Pipeline | NHPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | NHPC Limited Gujarat 600.0 | PWRSPVINDWE | Solar PV | Solar | 600 | 2026 | Pipeline | NHPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC Limited Chhattisgarh 26.0 | PWRSPVINDWE | Solar PV | Solar | 26 | 2025 | Pipeline | NTPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC Limited Madhya Pradesh 20.0 | PWRSPVINDWE | Solar PV | Solar | 20 | 2026 | Pipeline | NTPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC Limited Maharashtra 13.0 | PWRSPVINDWE | Solar PV | Solar | 13 | 2025 | Pipeline | NTPC Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 1200.0 | PWRSPVINDWE | Solar PV | Solar | 2400 | 2024 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 137.0 | PWRSPVINDWE | Solar PV | Solar | 137 | 2022 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2025 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 225.0 | PWRSPVINDWE | Solar PV | Solar | 225 | 2026 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 245.0 | PWRSPVINDWE | Solar PV | Solar | 245 | 2026 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 275.0 | PWRSPVINDWE | Solar PV | Solar | 550 | 2026 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 721.0 | PWRSPVINDWE | Solar PV | Solar | 721 | 2024 | Pipeline | NTPC REL | India_Electricity_Infrastructure.xlsx
India | IN_W | Ortusun Renewables Maharashtra 20.0 | PWRSPVINDWE | Solar PV | Solar | 20 | 2025 | Pipeline | Ortusun Renewables | India_Electricity_Infrastructure.xlsx
India | IN_W | Purvah Green Power Private Limited(Developer Company) Gujarat 300.0 | PWRSPVINDWE | Solar PV | Solar | 300 | 2028 | Pipeline | Purvah Green Power Private Limited(Developer Company) | India_Electricity_Infrastructure.xlsx
India | IN_W | RDS Solar Park Private Limited Gujarat 350.0 | PWRSPVINDWE | Solar PV | Solar | 350 | 2026 | Pipeline | RDS Solar Park Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar (Shakti Eight) Private Limited Gujarat 100.0 | PWRSPVINDWE | Solar PV | Solar | 100 | 2026 | Pipeline | ReNew Solar (Shakti Eight) Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar (Shakti Eight) Private Limited Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2026 | Pipeline | ReNew Solar (Shakti Eight) Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Gujarat 100.0 | PWRSPVINDWE | Solar PV | Solar | 400 | 2028 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 400 | 2028 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Gujarat 300.0 | PWRSPVINDWE | Solar PV | Solar | 1200 | 2027 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Madhya Pradesh 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2027 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Maharashtra 100.0 | PWRSPVINDWE | Solar PV | Solar | 100 | 2025 | Pipeline | ReNew Solar Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Reliance New Energy Maharashtra 93.0 | PWRSPVINDWE | Solar PV | Solar | 93 | 2035 | Pipeline | Reliance New Energy | India_Electricity_Infrastructure.xlsx
India | IN_W | Resco Global Wind Services Private Limited Gujarat 100.0 | PWRSPVINDWE | Solar PV | Solar | 100 | 2027 | Pipeline | Resco Global Wind Services Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Resco Global Wind Services Private Limited Gujarat 500.0 | PWRSPVINDWE | Solar PV | Solar | 500 | 2027 | Pipeline | Resco Global Wind Services Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Resco Global Wind Services Private Limited Madhya Pradesh 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2026 | Pipeline | Resco Global Wind Services Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Resco Global Wind Services Private Limited Madhya Pradesh 240.0 | PWRSPVINDWE | Solar PV | Solar | 240 | 2035 | Pipeline | Resco Global Wind Services Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Rewa Ultra Mega Solar Limited RUMSL- a JV of MPUVN and SECI Madhya Pradesh 170.0 | PWRSPVINDWE | Solar PV | Solar | 170 | 2025 | Pipeline | Rewa Ultra Mega Solar Limited RUMSL- a JV of MPUVN and SECI | India_Electricity_Infrastructure.xlsx
India | IN_W | SJVN GREEN ENERGY LIMITED Gujarat 100.0 | PWRSPVINDWE | Solar PV | Solar | 100 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_W | SJVN GREEN ENERGY LIMITED Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_W | SJVN GREEN ENERGY LIMITED Gujarat 260.0 | PWRSPVINDWE | Solar PV | Solar | 260 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_W | SJVN GREEN ENERGY LIMITED Gujarat 70.0 | PWRSPVINDWE | Solar PV | Solar | 70 | 2025 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
India | IN_W | SPV Maharashtra 1.3 | PWRSPVINDWE | Solar PV | Solar | 1.3 | 2022 | Pipeline | SPV | India_Electricity_Infrastructure.xlsx
India | IN_W | Skadar Solar Private Limited Maharashtra 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2026 | Pipeline | Skadar Solar Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Sprng Green Power Private Limited Gujarat 300.0 | PWRSPVINDWE | Solar PV | Solar | 300 | 2024 | Pipeline | Sprng Green Power Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Sprng Power Earth Private Limited Gujarat 250.0 | PWRSPVINDWE | Solar PV | Solar | 250 | 2026 | Pipeline | Sprng Power Earth Private Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Tata Power Renewable Energy Limited Maharashtra 270.0 | PWRSPVINDWE | Solar PV | Solar | 270 | 2024 | Pipeline | Tata Power Renewable Energy Limited | India_Electricity_Infrastructure.xlsx
India | IN_W | Teq Green Power Private Limited Gujarat 200.0 | PWRSPVINDWE | Solar PV | Solar | 200 | 2035 | Pipeline | Teq Green Power Private Limited | India_Electricity_Infrastructure.xlsx
Nepal | NP | Middle Bhotekoshi HEP | PWRHYDNPLXX | Hydropower | Hydro | 102 | 2025 | Under Construction / Ready for operation | Middle Bhotekoshi Jalbidhyut Company Ltd. (NEA sub.) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Trishuli 3B HEP | PWRHYDNPLXX | Hydropower | Hydro | 37 | 2025 | Under Construction | Trishuli Jal Vidhyut Company Ltd. (NEA sub.) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tanahun HEP | PWRHYDNPLXX | Hydropower | Hydro | 140 | 2025 | Under Construction | Tanahun Hydropower Ltd. (NEA sub.) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rahughat HEP | PWRHYDNPLXX | Hydropower | Hydro | 40 | 2025 | Under Construction | Raghuganga Hydropower Ltd. (NEA sub.) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tamakoshi-V HEP | PWRHYDNPLXX | Hydropower | Hydro | 94.8 | 2025 | Under Construction | Tamakoshi Jalvidyut Company Ltd. (NEA sub.) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Modi 'A' HEP | PWRHYDNPLXX | Hydropower | Hydro | 42 | 2026 | Under Construction | Modi Jalvidhyut Company Ltd. (NEA sub.) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Modi HEP | PWRHYDNPLXX | Hydropower | Hydro | 18.2 | 2026 | Under Construction | Modi Jalvidhyut Company Ltd. (NEA sub.) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Kulekhani III HEP | PWRHYDNPLXX | Hydropower | Hydro | 14 | 2020 | Operational (completed ~2020) | NEA | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Trishuli 3A HEP | PWRHYDNPLXX | Hydropower | Hydro | 60 | 2019 | Operational | NEA | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Budi Gandaki HEP | PWRHYDNPLXX | Hydropower | Hydro | 1 |  | NEA / GoN | Storage (dam) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Chainpur HEP | PWRHYDNPLXX | Hydropower | Hydro | 210 |  | Under development | CSJVCL (Chilime subsidiary) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rolwaling HEP | PWRHYDNPLXX | Hydropower | Hydro | 22 | 2025 | Under Construction | IPP | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tamakoshi V HEP (Tamkoshi Khola) | PWRHYDNPLXX | Hydropower | Hydro | 99.8 | 2025 | Under Construction | Tamakoshi Jal Vidhyut Company Ltd. (TJVCL) | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Modi (UMAHEP) | PWRHYDNPLXX | Hydropower | Hydro | 42 | 2026 | Under Construction | NEA subsidiary | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Modi (UMHEP) | PWRHYDNPLXX | Hydropower | Hydro | 18.2 | 2026 | Under Construction | NEA subsidiary | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Solar Plants (63 projects via competitive bidding) | PWRSPVNPLXX | Solar PV | Solar PV | 960 | 2025 | Awarded/Under development | Various IPPs | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rahughat HEP | PWRHYDNPLXX | Hydropower | Hydro | 40 | 2024 | Under Construction | NEA/Subsidiary | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Trishuli 3A | PWRHYDNPLXX | Hydropower | Hydro | 60 | 2019 | Under Construction (2019) → Operational | NEA | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khani Khola-1 HEP | PWRHYDNPLXX | Hydropower | Hydro | 40 |  | Under Construction | Greenlife Energy Pvt. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Baleph A HEP | PWRHYDNPLXX | Hydropower | Hydro | 22.14 |  | Under Construction | Moonlight Hydropower Pvt. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khani Khola (Dolakha) HEP | PWRHYDNPLXX | Hydropower | Hydro | 30 |  | Under Construction | Sasha Engineering Hydropower (P) Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Lower Irkhuwa HEP | PWRHYDNPLXX | Hydropower | Hydro | 13.04 |  | Under Construction | Lower Irkhuwa Hydropower Co. Pvt. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Badi Gad HEP | PWRHYDNPLXX | Hydropower | Hydro | 6.6 |  | Under Construction | Water and Energy Nepal Pvt. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rawa Khola HEP | PWRHYDNPLXX | Hydropower | Hydro | 6.5 |  | Under Construction | Dudhkoshi Power Company Pvt. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Phalankhu Khola HEP | PWRHYDNPLXX | Hydropower | Hydro | 13.7 |  | Under Construction | Betrawoti Hydropower Company (P) Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Tadi HEP | PWRHYDNPLXX | Hydropower | Hydro | 11 |  | Under Construction | Suryakunda Hydroelectric Pvt. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Mailung A HEP | PWRHYDNPLXX | Hydropower | Hydro | 6.42 |  | Under Construction | Energy Engineering Pvt. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tadi Khola HEP | PWRHYDNPLXX | Hydropower | Hydro | 5 |  | Under Construction | Hira Ratna Hydropower P. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Middle Midim HEP | PWRHYDNPLXX | Hydropower | Hydro | 4.8 |  | Under Construction | Madhya Midim Jalbidhyut Company P. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khorounga Khola HEP | PWRHYDNPLXX | Hydropower | Hydro | 4.8 |  | Under Construction | Reliable Hydropower Co. Pvt. Ltd. | Nepal_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sobadhanavi NG Combined Cycle (1st CCY GT) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas | 235 | 2025 | Under construction / advanced | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale, various zones) | PWRSPVLKAXX | Solar PV | Solar | 200 | 2025 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 10 | 2025 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro (various) | PWRHYDLKAXX | Hydropower | Mini Hydro | 10 | 2025 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass (various) | PWRBIOLKAXX | Biomass Power | Biomass | 10 | 2025 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (Kollonawa, 1st utility-scale) | PWRSDSLKAXX |  | Storage (BESS) | 5 | 2025 | Funding secured | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sobadhanavi NG CCY Steam Turbine (1st CCY ST) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas | 115 | 2026 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | 2nd NG CCY GT | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas | 235 | 2026 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 370 | 2026 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 90 | 2026 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro (various) | PWRHYDLKAXX | Hydropower | Mini Hydro | 10 | 2026 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass (various) | PWRBIOLKAXX | Biomass Power | Biomass | 15 | 2026 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS Kollonawa (100 MW / 100 MWh) | PWRSDSLKAXX |  | Storage (BESS) | 100 | 2026 | Funding secured | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda A extension (life ext.) | PWROILLKAXX | Oil/Diesel Power | Oil | 68 | 2026 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda B extension | PWROILLKAXX | Oil/Diesel Power | Oil | 72 | 2026 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Barge Plant extension | PWROILLKAXX | Oil/Diesel Power | Oil | 62 | 2026 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa GT-07 RETIREMENT | PWROILLKAXX | Oil/Diesel Power | Oil (RETIREMENT) | -115 | 2026 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | 2nd NG CCY Steam Turbine | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas | 115 | 2027 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 400 | 2027 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 260 | 2027 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | PWRHYDLKAXX | Hydropower | Mini Hydro | 10 | 2027 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | PWRBIOLKAXX | Biomass Power | Biomass | 20 | 2027 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG Internal Combustion Engine (200 MW) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas | 200 | 2028 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 450 | 2028 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 200 | 2028 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | PWRHYDLKAXX | Hydropower | Mini Hydro | 20 | 2028 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | PWRBIOLKAXX | Biomass Power | Biomass | 20 | 2028 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS Southern Region (100 MW / 400 MWh) | PWRSDSLKAXX |  | Storage (BESS) | 100 | 2028 | Financial arrangement needed | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 450 | 2029 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 150 | 2029 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | PWRHYDLKAXX | Hydropower | Mini Hydro | 20 | 2029 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | PWRBIOLKAXX | Biomass Power | Biomass | 20 | 2029 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (100 MW / 400 MWh, 3rd unit) | PWRSDSLKAXX |  | Storage (BESS) | 100 | 2029 | Financial arrangement needed | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa New GT (gas turbine) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas | 130 | 2030 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 450 | 2030 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 150 | 2030 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | PWRHYDLKAXX | Hydropower | Mini Hydro | 20 | 2030 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | PWRBIOLKAXX | Biomass Power | Biomass | 20 | 2030 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS Western (50 MW / 50 MWh) | PWRSDSLKAXX |  | Storage (BESS) | 50 | 2030 | Financial arrangement needed | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG Gas Turbine (100 MW) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas | 100 | 2031 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 350 | 2031 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 100 | 2031 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | PWRHYDLKAXX | Hydropower | Mini Hydro | 20 | 2031 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | PWRBIOLKAXX | Biomass Power | Biomass | 20 | 2031 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (100 MW / 400 MWh, 5th unit) | PWRSDSLKAXX |  | Storage (BESS) | 100 | 2031 | Financial arrangement needed | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda A RETIREMENT | PWROILLKAXX | Oil/Diesel Power | Oil (RETIREMENT) | -68 | 2031 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda B RETIREMENT | PWROILLKAXX | Oil/Diesel Power | Oil (RETIREMENT) | -72 | 2031 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Barge Plant RETIREMENT | PWROILLKAXX | Oil/Diesel Power | Oil (RETIREMENT) | -62 | 2031 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 350 | 2032 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 100 | 2032 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (200 MW / 800 MWh) | PWRSDSLKAXX |  | Storage (BESS) | 200 | 2032 | Financial arrangement needed | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | KCCP1 (Kelanitissa CCY-1) RETIREMENT | PWROILLKAXX | Oil/Diesel Power | Oil (RETIREMENT) | -165 | 2033 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | KCCP2 (Kelanitissa CCY-2) RETIREMENT | PWROILLKAXX | Oil/Diesel Power | Oil (RETIREMENT) | -163 | 2033 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Uthuru Janani RETIREMENT | PWROILLKAXX | Oil/Diesel Power | Oil (RETIREMENT) | -26.7 | 2033 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Maha Oya Pumped Storage Power Plant (PSPP) | PWRHYDLKAXX | Hydropower | Pumped Hydro Storage | 600 | 2034 | NPD approval & EIA submitted | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 350 | 2034 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 100 | 2034 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 Gas Turbine (300 MW) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas / Hydrogen | 300 | 2035 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | PWRSPVLKAXX | Solar PV | Solar | 350 | 2035 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | PWRWONLKAXX | Wind Power | Wind | 100 | 2035 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Westcoast CCY RETIREMENT | PWRNGSLKAXX | Natural Gas CC/OC | Oil/Gas (RETIREMENT) | -300 | 2035 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT additions (2036) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas / Hydrogen | 200 | 2036 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT (2037) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas / Hydrogen | 200 | 2037 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV 2036–2037 | PWRSPVLKAXX | Solar PV | Solar | 350 | 2036 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 IC Engine (200 MW, 2038) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas / Hydrogen | 200 | 2038 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV 2038 | PWRSPVLKAXX | Solar PV | Solar | 400 | 2038 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind 2038 | PWRWONLKAXX | Wind Power | Wind | 100 | 2038 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | India–Sri Lanka HVDC Interconnection (500 MW) | TRNINDSOLKAXX |  | Import (India) | 500 | 2039 | Under study | CEB / India (Govt-to-Govt) | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT (200 MW, 2039) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas / Hydrogen | 200 | 2039 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV 2039–2043 | PWRSPVLKAXX | Solar PV | Solar | 400 | 2039 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind 2039–2042 | PWRWONLKAXX | Wind Power | Wind | 100 | 2039 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT additions 2040–2043 | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas / Hydrogen | 200 | 2040 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Offshore Wind (500 MW) | PWRWONLKAXX | Wind Power | Wind (Offshore) | 500 | 2043 | Planned | IPP / CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Nuclear Power Plant (600 MW) | PWRURNLKAXX | Nuclear Power Plant | Nuclear | 600 | 2044 | Long-term plan | CEB / State | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT (200 MW, 2044) | PWRNGSLKAXX | Natural Gas CC/OC | Natural Gas / Hydrogen | 200 | 2044 | Planned | CEB / IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV 2044 | PWRSPVLKAXX | Solar PV | Solar | 450 | 2044 | Planned | IPPs | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (50 MW / 200 MWh, 2044) | PWRSDSLKAXX |  | Storage (BESS) | 50 | 2044 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Lakvijaya Units 2 & 3 RETIREMENT | PWRCOALKAXX | Coal Power Plant | Coal (RETIREMENT) | -600 | 2044 | Planned | CEB | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Siyambalanduwa Solar (100 MW) | PWRSPVLKAXX | Solar PV | Solar | 100 | 2026 | Planned / tender | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Ridiyagama Solar (100 MW, floating/ground) | PWRSPVLKAXX | Solar PV | Solar (floating/ground) | 100 | 2029 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Valaichenai Solar (100 MW) | PWRSPVLKAXX | Solar PV | Solar | 100 | 2027 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sampur Phase I (50 MW) | PWRSPVLKAXX | Solar PV | Solar | 50 | 2028 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sampur Phase II (70 MW) | PWRSPVLKAXX | Solar PV | Solar | 70 | 2029 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Trincomalee Solar I (100 MW) | PWRSPVLKAXX | Solar PV | Solar | 100 | 2029 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Trincomalee Solar II (100 MW) | PWRSPVLKAXX | Solar PV | Solar | 100 | 2029 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kilinochchi Solar I (50 MW) | PWRSPVLKAXX | Solar PV | Solar | 50 | 2029 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kilinochchi Solar II (100 MW) | PWRSPVLKAXX | Solar PV | Solar | 100 | 2031 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mannar Extension Wind (50 MW) | PWRWONLKAXX | Wind Power | Wind | 50 | 2026 | Cabinet approval stage | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mannar Phase II Wind (250 MW) | PWRWONLKAXX | Wind Power | Wind | 250 | 2027 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mullikulam Wind (100 MW) | PWRWONLKAXX | Wind Power | Wind | 100 | 2027 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kalpitiya Wind (120 MW) | PWRWONLKAXX | Wind Power | Wind | 120 | 2027 | Various stages | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Pooneryn Wind (234 MW) | PWRWONLKAXX | Wind Power | Wind | 234 | 2030 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Veravil Wind (200 MW) | PWRWONLKAXX | Wind Power | Wind | 200 | 2031 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Karachchi Wind (120 MW) | PWRWONLKAXX | Wind Power | Wind | 120 | 2032 | Planned | IPP | SriLanka_Electricity_Infrastructure.xlsx
Maldives | MV | POISED — Remaining Solar PV + BESS (126 outer islands) | PWRSPVMDVXX | Solar PV | Solar PV + BESS | 28 | 2025 | Under construction / Near completion | ADB (Asian Development Bank) — Government of Maldives | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ASPIRE — Existing PPA installations | PWRSPVMDVXX | Solar PV | Solar PV | 7.1 | 2024 | Operational | World Bank — ASPIRE project | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ARISE — Solar PV + BESS (hybridization + floating Addu) | PWRSPVMDVXX | Solar PV | Solar PV + BESS | 36 | 2026 | Planned / Under development | World Bank — ARISE project | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ASSURE — BESS + EMS + Solar IPPs (20 outer islands) | PWRSPVMDVXX | Solar PV | Solar PV + BESS | 20 | 2028 | Under development | ADB — ASSURE project | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Rooftop PV — Greater Male' Households (net-metering) | PWRSPVMDVXX | Solar PV | Solar PV | 9 | 2028 | Ongoing rollout | Private / ASSURE-supported | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Rooftop PV — Addu City and Other Islands (net-metering) | PWRSPVMDVXX | Solar PV | Solar PV | 8 | 2028 | Planned | Private (government-supported) | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | WTE Plant — K. Thilafushi | PWRWASMDVXX | Waste-to-Energy | Waste-to-Energy | 12 | 2024 | Planned (target operational end 2024) | Government of Maldives / Private PPA | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | WTE Plant — Addu City | PWRWASMDVXX | Waste-to-Energy | Waste-to-Energy | 1.5 | 2024 | Planned (target operational end 2024) | Government / Private | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | WTE Plant — R. Vandhoo | PWRWASMDVXX | Waste-to-Energy | Waste-to-Energy | 0.5 | 2024 | Planned (target operational end 2024) | Government / Private | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Rooftop PV — Gulhifalhu/Thilafushi Commercial Buildings (PPA) | PWRSPVMDVXX | Solar PV | Solar PV | 25 | 2028 | Potential initiative | Private sector (PPA) | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Wind Turbines — Gulhifalhu / Thilafushi | PWRWONMDVXX | Wind Power | Wind | 2 | 2028 | Potential initiative | Private PPA | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Floating Solar PV + BESS — Greater Male' Region | PWRSPVMDVXX | Solar PV | Solar PV (Floating) | 100 | 2028 | Potential initiative | Private PPA (large infrastructure) | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Solar PV Hybrid Plants — Outer Inhabited Islands (additional) | PWRSPVMDVXX | Solar PV | Solar PV + BESS | 35 | 2028 | Potential initiative | Public sector and utilities | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Solar PV — Resort and Industrial Islands | PWRSPVMDVXX | Solar PV | Solar PV | 75 | 2028 | Potential initiative | Private sector (resort operators) | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | LNG Power Plant — Gulhifalhu (feasibility study recommended) | PWRNGSMDVXX | Natural Gas CC/OC | Natural Gas (LNG) | 140 |  | Feasibility study recommended | To be determined (feasibility study first) | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Rooftop PV under ASSURE — Greater Male' (Magey Solar Program) | PWRSPVMDVXX | Solar PV | Solar PV | 4 | 2025 | Under development | ADB ASSURE project — Government Magey Solar Program | Maldives_Energy_Infrastructure.xlsx
Bhutan | BT | Gelephu Solar Power Plant | PWRSPVBTNXX | Solar PV | Solar |  | 2027 | Planning | TBD / Private IPP | Bhutan_Power_Infrastructure.xlsx ¦ Capacity TBD (target 200-500 MW); part of Gelephu Mindfulness City
Bhutan | BT | DSP Solar Expansion | PWRSPVBTNXX | Solar PV | Solar |  | 2026 | Under Study | DGPC | Bhutan_Power_Infrastructure.xlsx ¦ Capacity TBD; expansion of existing DSP Solar (3.23 MU in 2024)
Maldives | MV | ASSURE — Pilot Wind Power (Noonu Manadhoo) | PWRWONMDVXX | Onshore Wind | Wind |  |  | Planned pilot | ADB — ASSURE project | Maldives_Energy_Infrastructure.xlsx ¦ Pilot wind turbine; capacity TBD
Maldives | MV | ASSURE — Pilot Ocean Energy | PWRWAVMDVXX | Ocean / Marine RE | Ocean |  |  | Planned pilot | ADB — ASSURE project | Maldives_Energy_Infrastructure.xlsx ¦ Pilot ocean/marine RE; island TBD; capacity TBD
Maldives | MV | Marine Renewable Energy Road Map + Pilots | PWRWAVMDVXX | Ocean / Marine RE | Ocean |  |  | Planning / Study phase | ASSURE + International TA | Maldives_Energy_Infrastructure.xlsx ¦ Marine RE Road Map H1 2025; tidal 28-106 MW potential; pilots TBD
Maldives | MV | Solar PV — Solar Street Lights + Island Councils Program (expanded) | PWRSPVMDVXX | Solar PV | Solar |  |  | Planned expansion | Government (revolving fund proposed) | Maldives_Energy_Infrastructure.xlsx ¦ Expanded to all Island Councils; capacity TBD

## Technology_Costs
Technology_Code | Technology_Name | Parameter | Unit | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Source | Notes
PWRSPV | Solar PV (utility-scale) | CAPEX | USD/kW | 560 | 536 | 474 | 413 | 379 | 345 | 311 | IN(base)=$560/kW ¦ BD=$840(×1.5) ¦ LK=$849(×1.5) ¦ NP=$896(×1.6) ¦ BT=$1008(×1.8) ¦ MV=$1680(×3.0) Anchor refs: IRENA 2024; ADB PADs; CEB LTGEP BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
PWRSPV | Solar PV (utility-scale) | Fixed O&M | USD/kW/yr | 8 | 8 | 7 | 6 | 6 | 5 | 5 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
PWRSPV | Solar PV (utility-scale) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
PWRSPV | Solar PV (utility-scale) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRSPV | Solar PV (utility-scale) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRSPV | Solar PV (utility-scale) | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
PWRSPR | Solar PV (rooftop/distributed) | CAPEX | USD/kW | 850 | 813 | 720 | 627 | 576 | 524 | 472 | IN(base)=$850/kW ¦ BD=$1275(×1.5) ¦ LK=$982(×1.2) ¦ NP=$1360(×1.6) ¦ BT=$1530(×1.8) ¦ MV=$2550(×3.0) Anchor refs: CERC; CEB LTGEP BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
PWRSPR | Solar PV (rooftop/distributed) | Fixed O&M | USD/kW/yr | 9 | 9 | 8 | 7 | 7 | 6 | 6 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
PWRSPR | Solar PV (rooftop/distributed) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
PWRSPR | Solar PV (rooftop/distributed) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRSPR | Solar PV (rooftop/distributed) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRSPR | Solar PV (rooftop/distributed) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
PWRCSP | Concentrated Solar Power | CAPEX | USD/kW | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
PWRCSP | Concentrated Solar Power | Fixed O&M | USD/kW/yr | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
PWRCSP | Concentrated Solar Power | Variable O&M | USD/MWh | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
PWRCSP | Concentrated Solar Power | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRCSP | Concentrated Solar Power | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRCSP | Concentrated Solar Power | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
PWRWON | Onshore Wind | CAPEX | USD/kW | 761 | 687 | 663 | 640 | 617 | 594 | 570 | IN(base)=$761/kW ¦ BD=$1218(×1.6) ¦ LK=$1391(×1.8) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP BD ×1.5-2.0: Limited BD wind experience [⚠ NO URL] LK ×1.5-2.3: ADB Mannar $2,481/kW (incl. harbor) (https://www.adb.org/results/helping-sri-lanka-go-green) | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
PWRWON | Onshore Wind | Fixed O&M | USD/kW/yr | 22 | 22 | 21 | 20 | 20 | 19 | 19 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
PWRWON | Onshore Wind | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
PWRWON | Onshore Wind | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRWON | Onshore Wind | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRWON | Onshore Wind | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
PWRWOF | Offshore Wind | CAPEX | USD/kW | 3800 | 3768 | 3442 | 2014 | 1960 | 1919 | 1886 | IN(base)=$2339/kW ¦ BD=N/A ¦ LK=$3781(×1.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
PWRWOF | Offshore Wind | Fixed O&M | USD/kW/yr | 114 | 114 | 105 | 97 | 90 | 84 | 80 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
PWRWOF | Offshore Wind | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
PWRWOF | Offshore Wind | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRWOF | Offshore Wind | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRWOF | Offshore Wind | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
PWRHDR | Hydro – Reservoir | CAPEX | USD/kW | 2500 | 2550 | 2625 | 2700 | 2775 | 2850 | 2925 | IN(base)=$1500/kW ¦ BD=N/A ¦ LK=$2500(×1.7) ¦ NP=$2761(×1.8) ¦ BT=$1200(×0.8) ¦ MV=N/A Anchor refs: CEA; Nepal NEA; Bhutan PSMP LK ×~1.5: No specific LK data [⚠ NO URL] NP ×2.0-3.0: Tanahu $3,607/kW; Upper Trishuli $2,997/kW (https://www.adb.org) BT ×0.9-1.3: Mangdechhu $938/kW; Tala $1,176/kW | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHDR | Hydro – Reservoir | Fixed O&M | USD/kW/yr | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHDR | Hydro – Reservoir | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHDR | Hydro – Reservoir | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRHDR | Hydro – Reservoir | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRHDR | Hydro – Reservoir | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHRO | Hydro – Run-of-River | CAPEX | USD/kW | 1750 | 1785 | 1873 | 1960 | 2048 | 2135 | 2223 | IN(base)=$1300/kW ¦ BD=N/A ¦ LK=$1840(×1.4) ¦ NP=$1600(×1.2) ¦ BT=$1100(×0.85) ¦ MV=N/A Anchor refs: CEA; CEB LTGEP; PSMP; Nepal NEA LK ×~1.3: CEB LTGEP mini-hydro $1,840/kW (https://www.ceb.lk) NP ×1.3-1.7: NEA/industry ~$2,000/kW avg (https://www.adb.org/sites/default/files/publication/612641/hydropower-development-economic-growth-nepal.pdf) BT ×0.8-1.1: PSMP $785-1,339/kW; Nikachhu $1,220/kW (https://sasec.asia) | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHRO | Hydro – Run-of-River | Fixed O&M | USD/kW/yr | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHRO | Hydro – Run-of-River | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHRO | Hydro – Run-of-River | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRHRO | Hydro – Run-of-River | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRHRO | Hydro – Run-of-River | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHPS | Hydro – Pumped Storage | CAPEX | USD/kW | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | IN(base)=$635/kW ¦ BD=N/A ¦ LK=N/A ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP (India only) LK ×~1.5: No specific LK data [⚠ NO URL] NP ×2.0-3.0: Tanahu $3,607/kW; Upper Trishuli $2,997/kW (https://www.adb.org) BT ×0.9-1.3: Mangdechhu $938/kW; Tala $1,176/kW | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
PWRHPS | Hydro – Pumped Storage | Fixed O&M | USD/kW/yr | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
PWRHPS | Hydro – Pumped Storage | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
PWRHPS | Hydro – Pumped Storage | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRHPS | Hydro – Pumped Storage | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRHPS | Hydro – Pumped Storage | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
PWRCOASCPC | Coal – Supercritical | CAPEX | USD/kW | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | IN(base)=$1059/kW ¦ BD=$1694(×1.6) ¦ LK=$2132(×2.0) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP BD ×~1.6: Payra/Rampal cost reporting LK ×~2.0: CEB LTGEP $2,132/kW (https://www.ceb.lk) | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOASCPC | Coal – Supercritical | Fixed O&M | USD/kW/yr | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOASCPC | Coal – Supercritical | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOASCPC | Coal – Supercritical | Heat Rate | GJ/MWh | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOASCPC | Coal – Supercritical | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Coal' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRCOASCPC | Coal – Supercritical | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | CAPEX | USD/kW | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | BD ×~1.6: Payra/Rampal cost reporting LK ×~2.0: CEB LTGEP $2,132/kW (https://www.ceb.lk) | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | Fixed O&M | USD/kW/yr | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | Heat Rate | GJ/MWh | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Coal' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRCOAUSC | Coal – Ultra-supercritical | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCCG | Combined Cycle Gas Turbine | CAPEX | USD/kW | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | IN(base)=$700/kW ¦ BD=$770(×1.1) ¦ LK=$1300(×1.9) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA; IEPMP; CEB LTGEP BD ×~1.1: IEPMP ~$770/kW LK ×~1.9: CEB LTGEP $1,273-1,507/kW (https://www.ceb.lk) | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWRCCG | Combined Cycle Gas Turbine | Fixed O&M | USD/kW/yr | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWRCCG | Combined Cycle Gas Turbine | Variable O&M | USD/MWh | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWRCCG | Combined Cycle Gas Turbine | Heat Rate | GJ/MWh | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWRCCG | Combined Cycle Gas Turbine | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Natural gas' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRCCG | Combined Cycle Gas Turbine | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | CAPEX | USD/kW | 360 | 360 | 360 | 360 | 360 | 360 | 360 | IN(base)=$450/kW ¦ BD=$495(×1.1) ¦ LK=$360(×0.8) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA; CEB LTGEP BD ×~1.1: IEPMP ~$770/kW LK ×~1.9: CEB LTGEP $1,273-1,507/kW (https://www.ceb.lk) | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | Fixed O&M | USD/kW/yr | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | Variable O&M | USD/MWh | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | Heat Rate | GJ/MWh | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Natural gas' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWROCG | Open Cycle Gas Turbine | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROIL | Oil/Diesel generation | CAPEX | USD/kW | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | IN(base)=$700/kW ¦ BD=$770(×1.1) ¦ LK=$1000(×1.4) ¦ NP=N/A ¦ BT=N/A ¦ MV=$700(×1.0) Anchor refs: CEB LTGEP; ADB Maldives BD ×~1.1: BPDB IPP costs LK ×~1.4: CEB LTGEP $1,000-1,124/kW (https://www.ceb.lk) NP ×~1.5: Landlocked transport premium BT ×~1.5: Landlocked transport premium MV ×~1.0: Core competency (STELCO/FENAKA) (https://www.environment.gov.mv) | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWROIL | Oil/Diesel generation | Fixed O&M | USD/kW/yr | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWROIL | Oil/Diesel generation | Variable O&M | USD/MWh | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWROIL | Oil/Diesel generation | Heat Rate | GJ/MWh | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWROIL | Oil/Diesel generation | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Crude oil (Brent)' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWROIL | Oil/Diesel generation | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWRBIO | Biomass/Bagasse | CAPEX | USD/kW | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | IN(base)=$1142/kW ¦ BD=N/A ¦ LK=$1782(×1.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRBIO | Biomass/Bagasse | Fixed O&M | USD/kW/yr | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRBIO | Biomass/Bagasse | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRBIO | Biomass/Bagasse | Heat Rate | GJ/MWh | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRBIO | Biomass/Bagasse | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Biomass residue' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRBIO | Biomass/Bagasse | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRWTE | Waste-to-Energy | CAPEX | USD/kW | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | BD ×~1.1: BPDB IPP costs LK ×~1.4: CEB LTGEP $1,000-1,124/kW (https://www.ceb.lk) NP ×~1.5: Landlocked transport premium BT ×~1.5: Landlocked transport premium MV ×~1.0: Core competency (STELCO/FENAKA) (https://www.environment.gov.mv) | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRWTE | Waste-to-Energy | Fixed O&M | USD/kW/yr | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRWTE | Waste-to-Energy | Variable O&M | USD/MWh | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRWTE | Waste-to-Energy | Heat Rate | GJ/MWh | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRWTE | Waste-to-Energy | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Waste' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRWTE | Waste-to-Energy | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRURN | Nuclear | CAPEX | USD/kW | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | IN(base)=$2000/kW ¦ BD=$5200(×2.6) ¦ LK=$5103(×2.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: India PHWR; BD Rooppur; CEB LTGEP | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Fixed O&M | USD/kW/yr | 134 | 134 | 134 | 134 | 134 | 134 | 134 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Variable O&M | USD/MWh | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Heat Rate | GJ/MWh | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Fuel Cost | USD/GJ | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRGEO | Geothermal | CAPEX | USD/kW | 4589 | 4544 | 4434 | 4327 | 4222 | 4120 | 4020 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
PWRGEO | Geothermal | Fixed O&M | USD/kW/yr | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
PWRGEO | Geothermal | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
PWRGEO | Geothermal | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRGEO | Geothermal | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRGEO | Geothermal | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
PWRSDS | Short-duration storage (Li-ion 4h) | CAPEX | USD/kW | [7 empty] | IN(base)=$882/kW ¦ BD=$1058(×1.2) ¦ LK=$1330(×1.5) ¦ NP=$1147(×1.3) ¦ BT=$1235(×1.4) ¦ MV=$1323(×1.5) Anchor refs: CEA NEP; CEB LTGEP; ADB BD ×~1.2: Limited BD data [⚠ NO URL] LK ×~1.5: CEB LTGEP ~$1,330/kW (https://www.ceb.lk) NP ×~1.3: No specific data [⚠ NO URL] BT ×~1.4: No specific data [⚠ NO URL] MV ×~1.5: Island logistics premium | ⚠ NO SOURCE
PWRSDS | Short-duration storage (Li-ion 4h) | Fixed O&M | USD/kW/yr | 20 | 21 | 17 | 17 | 16 | 16 | 15 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
PWRSDS | Short-duration storage (Li-ion 4h) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
PWRSDS | Short-duration storage (Li-ion 4h) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRSDS | Short-duration storage (Li-ion 4h) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRSDS | Short-duration storage (Li-ion 4h) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
PWRLDS | Long-duration storage (8h+) | CAPEX | USD/kW | [7 empty] | BD ×~1.2: Limited BD data [⚠ NO URL] LK ×~1.5: CEB LTGEP ~$1,330/kW (https://www.ceb.lk) NP ×~1.3: No specific data [⚠ NO URL] BT ×~1.4: No specific data [⚠ NO URL] MV ×~1.5: Island logistics premium | ⚠ NO SOURCE
PWRLDS | Long-duration storage (8h+) | Fixed O&M | USD/kW/yr | 45 | 47 | 38 | 37 | 35 | 34 | 33 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
PWRLDS | Long-duration storage (8h+) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
PWRLDS | Long-duration storage (8h+) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRLDS | Long-duration storage (8h+) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRLDS | Long-duration storage (8h+) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
PWRFPV | Floating Solar PV | CAPEX | USD/kW | 1244 | 1190 | 1054 | 918 | 842 | 767 | 691 | BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
PWRFPV | Floating Solar PV | Fixed O&M | USD/kW/yr | 19 | 18 | 17 | 16 | 15 | 14 | 13 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
PWRFPV | Floating Solar PV | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
PWRFPV | Floating Solar PV | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRFPV | Floating Solar PV | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRFPV | Floating Solar PV | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
PWRH2G | Green Hydrogen Fuel Cell | CAPEX | USD/kW | 2200 | 2100 | 1800 | 1500 | 1300 | 1100 | 1000 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
PWRH2G | Green Hydrogen Fuel Cell | Fixed O&M | USD/kW/yr | 66 | 63 | 54 | 45 | 39 | 33 | 30 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
PWRH2G | Green Hydrogen Fuel Cell | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
PWRH2G | Green Hydrogen Fuel Cell | Heat Rate | GJ/MWh | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 |  | N/A — renewable/non-combustion technology
PWRH2G | Green Hydrogen Fuel Cell | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRH2G | Green Hydrogen Fuel Cell | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
PWRTDL | Tidal / Marine | CAPEX | USD/kW | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
PWRTDL | Tidal / Marine | Fixed O&M | USD/kW/yr | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
PWRTDL | Tidal / Marine | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
PWRTDL | Tidal / Marine | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRTDL | Tidal / Marine | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRTDL | Tidal / Marine | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
PWRBCK | Backstop (penalty generator) | CAPEX | USD/kW | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
PWRBCK | Backstop (penalty generator) | Fixed O&M | USD/kW/yr | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
PWRBCK | Backstop (penalty generator) | Variable O&M | USD/MWh | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
PWRBCK | Backstop (penalty generator) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRBCK | Backstop (penalty generator) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRBCK | Backstop (penalty generator) | Construction Time | years | [8 empty] | N/A — backstop/penalty generator

## RE_Targets_Policies
Country | Node | Policy_Name | Target_Type | Target_Value | Target_Year | Mandate_or_Aspirational | Source
India | IN_N/S/E/W/NE | National Electricity Plan 2023 | Capacity_GW | 500 | 2030 | Mandate | NEP 2023
India | IN_N/S/E/W/NE | India NDC (Updated) | RE_share | 0.5 | 2030 | Mandate | India NDC 2022
Bangladesh | BD | Mujib Climate Prosperity Plan | Capacity_GW | 40 | 2041 | Aspirational | MCPP
Bangladesh | BD | Bangladesh NDC | RE_share | 0.4 | 2041 | Aspirational | Bangladesh NDC 2021
Nepal | NP | National Energy Strategy | Capacity_GW | 15 | 2030 | Aspirational | GoN Energy Strategy
Sri Lanka | LK | Sri Lanka Energy Policy | RE_share | 0.7 | 2030 | Mandate | GoSL NDC 2021
Bhutan | BT | Bhutan NDC | Emissions | Carbon negative | 2030 | Mandate | Bhutan NDC
Maldives | MV | MCCEE Energy Roadmap 2024-2033 | RE_share | 0.33 | 2028 | Mandate | MCCEE Energy Road Map 2024-2033 (ADB, Nov 2024)