## README
OSTRAM — OSeMOSYS for Transmission
South Asia Power System Connectivity Model
Version: | 1.1
Last Updated: | 2026-04-16
Prepared for: | UN ESCAP
═══ WHAT IS THIS TEMPLATE ══════════════════════════════════════════════
This workbook collects the South Asia power-system data needed to run OSTRAM,
an OSeMOSYS-based connectivity model covering BD, BT, IN (×5), NP, LK, MV over 2023–2050.
The study is centred on cross-border interconnection — the orange tabs carry that focus;
the blue, red, and green tabs supply the surrounding system context the interconnector
question has to be answered within.
═══ HOW THE COLOURS WORK ══════════════════════════════════════════════
Each tab is colour-coded by its role in the pipeline:
BLUE — Model inputs. The A3 step reads these directly to populate OSeMOSYS.
7 sheets covering fixed parameters, per-tech trajectories, demand,
transmission, variable cost, and emissions.
RED — Timeslice-dependent sheets. The OSTRAM timeslice Python will rewrite
these whenever the temporal resolution changes (4 seasons × 3 bands today,
but not a hard assumption). Everything indexed by S_D_ lives here.
ORANGE — Interconnectors. The study focus: project inventory and the corresponding
TRNCBD_* tech parameters that encode cross-border corridors in OSeMOSYS.
GREEN — Provenance / nice-to-have. Country-lead inventories and cost-source tables
that explain (or will explain) where the numbers in the blue sheets come from.
Not read by A3 — these are the audit trail.
═══ SHEET INDEX ═══════════════════════════════════════════════════════
Sheet | Colour | What it contains
README | Gray | This sheet.
Fixed_Horizon_Parameters | Blue | Time-invariant per-tech parameters: CapacityToActivityUnit, OperationalLife, Input/OutputActivityRatio. Long-form: one row per (Tech × Parameter).
Primary_Techs | Blue | Fuel-supply / mining techs (MIN*). CapitalCost, FixedCost, ResidualCapacity, TotalAnnualMaxCapacity by year 2023–2050 in wide format.
Secondary_Techs | Blue | Power generation techs (PWR*). Same parameter set as Primary_Techs plus additional fields; the heart of the technology database.
Capacities_CF | Red | CapacityFactor (fraction) per (Timeslice × Tech) by year. 12 timeslices × all generation techs.
VariableCost | Blue | VariableCost (USD/GJ) by Mode.Operation × Tech × year. Primary-tech fuels only.
Demand_Projection | Blue | Annual electricity demand per node-ELC fuel (PJ/yr), 2023–2050. One row per node.
Demand_Profiles | Red | Demand fractions per (Timeslice × node-ELC) by year. Must sum to 1.0 across the 12 timeslices for each node-year.
Demand_Techs | Blue | Transmission tech parameters (PWRTRN, RNWTRN, TRNNLI, TRNRPO) — internal transmission layer, not cross-border.
Emissions | Blue | EmissionActivityRatio (tCO2/PJ) for emitting PWR techs by year. Currently IPCC 2006 defaults; to be replaced with country-specific NC values.
Yearsplit_Template | Red | YearSplit fractions per timeslice (must sum to 1.0 per year). Template form — timeslice Python regenerates this when resolution changes.
DaySplit | Red | DaySplit fractions per daily time bracket. Same rewrite rule as Yearsplit.
Interconnectors | Orange | Project inventory of cross-border corridors: 51 rows with from/to node, circuits, COD year, affiliated power, MW capacity, voltage, AC/DC, status. Pre-populated from Zixuan v3.
Interconnector_Params | Orange | OSeMOSYS parameters for TRNCBD_* techs (cross-border interconnectors). CapitalCost, FixedCost, ResidualCapacity, TotalAnnualMaxCapacity by year — the blue-equivalent of the inventory sheet.
Existing_Generation | Green | Plant-level inventory: ~2,112 plants with capacity MW, commissioning year, expected retirement, annual CF, status, source. Provenance for ResidualCapacity in Secondary_Techs.
Planned_Generation | Green | Project pipeline: ~541 committed/announced projects with expected COD, developer, source. Provenance for TotalAnnualMinCapacity / MaxCapacity in Secondary_Techs.
Technology_Costs | Green | Tech-level CAPEX / Fixed O&M / Variable O&M / Heat Rate trajectories 2023→2050, with source. Provenance for CapitalCost, FixedCost in Secondary_Techs.
RE_Targets_Policies | Green | National RE targets and NDC commitments per country-node: target type (Capacity_GW or RE_share), target year, mandate vs aspirational, source.
═══ HOW TO FILL IT IN ═════════════════════════════════════════════════
Step 1 — Send the green sheets to each country lead
They populate: existing plants, planned projects, cost assumptions, RE targets.
Pre-filled headers and dropdowns; only the empty yellow cells need values.
Step 2 — Transfer green-sheet data into the blue sheets
Existing plants → ResidualCapacity in Secondary_Techs
Planned projects → TotalAnnualMinCapacity (committed) and TotalAnnualMaxCapacity
Cost data → CapitalCost and FixedCost in Secondary_Techs and Primary_Techs
Hourly load data → Demand_Projection (annual) and Demand_Profiles (shapes)
Renewable resource data → Capacities_CF
Step 3 — Update the orange sheets if interconnector plans change
Corridor inventory changes in Interconnectors must be mirrored in Interconnector_Params.
Step 4 — Check before running
Every yellow cell with blue text is a flagged gap — it still needs a value.
Demand profile fractions must sum to 1.0 across the 12 timeslices per node-year.
YearSplit fractions must also sum to 1.0.
ResidualCapacity should decline over time as plants retire.
Step 5 — Run the pipeline
A3 reads the blue + orange sheets. The timeslice Python handles the red sheets.
The otoole-based pipeline produces the OSeMOSYS .txt data file.
═══ RULES — DO NOT BREAK THESE ═══════════════════════════════════════
1. Do not rename or reorder columns in the blue sheets. The pipeline reads exact column names.
2. Do not merge cells. The Python reader cannot handle them.
3. Do not delete rows. If a technology is not available at a node, set TotalAnnualMaxCapacity = 0.
4. Projection.Mode = "User defined" and Projection.Parameter = 0 means year-column values are used as-is.
5. CapacityToActivityUnit = 31.536 converts GW → PJ/yr. Do not change this.
6. All costs in USD 2023. Capacity in GW. Energy in PJ. Fractions as decimals (0.0–1.0).
7. Every VRE technology needs capacity factor values for all 12 timeslices.
8. Backstop (PWRBCK) is a safety valve at every node. Give it a very high cost (~99999 USD/kW).
═══ NAMING CONVENTIONS ════════════════════════════════════════════════
Technologies:
PWR + tech code + node code + XX + 01
PWRSPVBDXX01 = Solar PV, Bangladesh
PWRHDRBTXX01 = Hydro Reservoir, Bhutan
PWRCOASCPCIN_NXX01 = Coal Supercritical, India North
Demand fuels:
ELC + node code + XX02
ELCBDXX02 = Electricity demand, Bangladesh
Cross-border interconnectors:
TRNCBD_ + from_node + _ + to_node
TRNCBD_BD_IN_E = Bangladesh ↔ India East
═══ NODE CODES ════════════════════════════════════════════════════════
BD | Bangladesh
BT | Bhutan
IN_N | India – North
IN_S | India – South
IN_E | India – East
IN_W | India – West
IN_NE | India – Northeast
NP | Nepal
LK | Sri Lanka
MV | Maldives
═══ TIMESLICES ════════════════════════════════════════════════════════
Code | Season | Daily Band
S1D1 | Summer (Apr–May) | Night/Off-peak (22:00–06:00)
S1D2 | Summer (Apr–May) | Day/Shoulder (06:00–17:00)
S1D3 | Summer (Apr–May) | Evening/Peak (17:00–22:00)
S2D1 | Monsoon (Jun–Sep) | Night/Off-peak (22:00–06:00)
S2D2 | Monsoon (Jun–Sep) | Day/Shoulder (06:00–17:00)
S2D3 | Monsoon (Jun–Sep) | Evening/Peak (17:00–22:00)
S3D1 | Post-Monsoon (Oct–Nov) | Night/Off-peak (22:00–06:00)
S3D2 | Post-Monsoon (Oct–Nov) | Day/Shoulder (06:00–17:00)
S3D3 | Post-Monsoon (Oct–Nov) | Evening/Peak (17:00–22:00)
S4D1 | Winter (Dec–Mar) | Night/Off-peak (22:00–06:00)
S4D2 | Winter (Dec–Mar) | Day/Shoulder (06:00–17:00)
S4D3 | Winter (Dec–Mar) | Evening/Peak (17:00–22:00)
═══ UNITS ═════════════════════════════════════════════════════════════
Quantity | Unit
Capacity | GW
Energy | PJ
CAPEX | USD2023/kW
Fixed O&M | USD2023/kW/yr
Variable O&M / Fuel | USD/GJ
Demand | PJ/yr
CapacityToActivityUnit | 31.536 (GW → PJ/yr)
Emissions | tCO₂/PJ
Capacity factors | fraction (0.0–1.0)
Demand profiles | fraction (sum to 1.0 per node-year)
═══ TECHNOLOGY CODES ══════════════════════════════════════════════════
Code | Technology | Eligible Nodes
PWRSPV | Solar PV (utility-scale) | All nodes
PWRSPR | Solar PV (rooftop) | All nodes
PWRCSP | Concentrated Solar Power | IN_N/S/E/W/NE, LK
PWRWON | Onshore Wind | All nodes
PWRWOF | Offshore Wind | IN_S/W/E, BD, LK, MV
PWRHDR | Hydro – Reservoir | NP, BT, IN_N/NE/E, LK
PWRHRO | Hydro – Run-of-River | NP, BT, IN_N/NE
PWRHPS | Hydro – Pumped Storage | IN_S/W/N, NP, LK
PWRCOASCPC | Coal – Supercritical | BD, IN_N/S/E/W, LK
PWRCOAUSC | Coal – Ultra-supercritical | IN_N/S/E/W
PWRCCG | CCGT | BD, IN nodes, MV, LK
PWROCG | OCGT | BD, IN nodes, MV, LK
PWROIL | Oil/Diesel | MV, BD, LK
PWRBIO | Biomass/Bagasse | BD, IN nodes, NP, LK
PWRWTE | Waste-to-Energy | IN nodes, BD, LK
PWRURN | Nuclear | IN nodes, BD
PWRGEO | Geothermal | IN_N
PWRSDS | Short-duration storage (Li-ion 4h) | All nodes
PWRLDS | Long-duration storage (8h+) | All nodes
PWRFPV | Floating Solar PV | IN_S/E, BD, LK, MV
PWRH2G | Green Hydrogen Fuel Cell | IN nodes
PWRTDL | Tidal / Marine | IN_S, LK
PWRBCK | Backstop (penalty generator) | All nodes
MINCOA | Coal mining/import | All nodes
MINGAS | Natural Gas supply | All nodes
MINOIL | Oil supply | All nodes
MINURN | Uranium supply | All nodes
MINBIO | Biomass supply | All nodes
MINH2G | Green hydrogen production | All nodes
PWRTRN | Existing transmission (non-RE) | All nodes
RNWTRN | Existing transmission (RE) | All nodes
TRNNLI | New transmission line | All nodes
TRNRPO | Repower/upgrade transmission | All nodes
TRNCBD | Cross-border interconnector | Per corridor

## Control
scenario | active | rules_script | inherit_restrictions_from | notes
BAU | TRUE | add_max_cap_investment_lid_rule.py |  | Base scenario
A_Calibrated_BAU | TRUE | set_retirement_schedule.py, add_max_cap_investment_lid_rule.py, set_min_capacity_floors.py, relax_interconnectors.py | BAU | Test multi-script chain
B_Optimised_VRE | TRUE | set_retirement_schedule.py, add_max_cap_investment_lid_rule.py, relax_interconnectors.py, add_storage_min_investment.py |  | Loose VRE + open interconnectors (3x). No inheritance — independent solve from BAU base.
C_Target_VRE | TRUE | set_retirement_schedule.py, add_max_cap_investment_lid_rule.py, set_vre_targets.py, relax_interconnectors.py, add_storage_min_investment.py |  | NDC renewable targets. Independent solve from BAU base; hard dep is Executables/BAU_0/ProductionByTechnology.csv read by set_vre_targets.

## Restrictions
scenario | source_sheet | tech | parameter | year | value | rule_applied | source_run_timestamp
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.016068 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.017157 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.018321 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.019563 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.02089 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.022307 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.023819 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.020081 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.021156 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.022289 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.023482 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.02474 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.026064 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.027459 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.02893 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.030479 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.032111 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.03383 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.028396 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.029607 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.03087 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.032187 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.03356 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.034991 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0.036484 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0.03804 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0.039663 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 6.9859e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 7.4596e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 7.9656e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 8.5056e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9.0825e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9.6986e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.00010356 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 8.731e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9.1984e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9.6909e-05 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.0001021 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.00010756 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.00011332 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.00011939 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.00012578 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.00013252 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.00013961 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.00014709 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.00012346 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.00012873 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.00013422 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.00013994 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.00014591 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.00015214 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0.00015863 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0.00016539 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0.00017245 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.40749 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.43512 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.46463 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.49613 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.52978 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.56572 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.60407 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.50928 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.53654 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.56527 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.59553 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.62742 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.66102 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.6964 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.7337 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.77297 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.81437 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.85796 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.72015 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.75086 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.78289 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.81628 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.85111 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.88741 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0.92526 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0.96473 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.0059 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.00037493 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.00042653 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.00043551 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.00046603 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.00048356 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.0005827 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.00040757 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.00039566 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.00054243 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.00054243 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.00054243 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.00054243 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.00054243 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.00061315 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.00061315 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.00061314 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.00061315 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.00061315 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.00069942 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.00073126 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.00076458 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.0007994 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.00083581 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.00087388 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.00091368 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0.00095531 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0.00099881 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 1.212 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 1.212 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.034056 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.038743 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.039559 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.042332 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.043924 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.052929 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.037021 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.035939 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.049272 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.049271 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.049272 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.049271 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.049272 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.055695 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.055695 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.055694 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.055695 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.055695 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.063531 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.066424 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.069451 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.072613 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.075921 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.079379 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.082994 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0.086775 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0.090727 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.39701 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 1.3332 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.45269 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.48337 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.51616 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.55117 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.58853 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.49618 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.52275 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.55074 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.58022 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.61129 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.64402 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.67849 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.71483 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.7531 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.79343 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.8359 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.70163 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.73155 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.76275 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.79529 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.82923 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.86459 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0.90147 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0.93992 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0.98002 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.38708 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.44035 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.44963 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.505 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.49924 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.60159 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.42078 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.40848 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.56002 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.56001 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.56002 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.56001 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.56002 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.63302 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.63302 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.63301 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.63302 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.63302 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.72209 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.75496 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.78937 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.82531 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.8629 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.90221 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.9433 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0.98628 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 1.0312 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.041985 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 3.1159 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.047873 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.051119 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.054586 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.058289 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.06224 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.052473 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.055283 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.058242 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.06136 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.064646 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.068107 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.071753 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.075596 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.079643 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.083908 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.0884 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.0742 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.077364 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.080664 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.084105 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.087694 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.091433 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0.095334 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0.099401 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0.10364 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.07575 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.062475 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.36158 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.07257 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.101 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.080577 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.097097 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.067914 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.06593 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.090387 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.090386 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.090387 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.090386 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.090387 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.10217 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.10217 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.10217 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.10217 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.10217 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.11655 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.12185 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.1274 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.13321 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.13927 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.14562 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.15225 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0.15919 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0.16644 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.0051714 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.0058832 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.006007 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.006428 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.0066698 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.0080372 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.0056216 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.0054574 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.0074819 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.0074817 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.0074819 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.0074817 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.0074819 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.0084572 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.0084572 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.0084571 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.0084572 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.0084572 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.0096471 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.010086 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.010546 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.011026 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.011528 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.012054 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.012603 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0.013177 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0.013777 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 2.3916 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 2.7207 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 2.778 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 2.9727 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 3.0845 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 3.7169 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 2.5998 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 2.5238 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 3.4601 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 3.46 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 3.4601 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 8.1204 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 3.4601 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 3.9111 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 3.9111 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 3.9111 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 3.9111 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 3.9111 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 4.4614 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 4.6646 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 4.8771 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 5.0992 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 5.3315 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 5.5743 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 5.8282 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 6.0937 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 6.3712 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.0044011 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.0046996 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.0050183 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.0053585 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.005722 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.0061101 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.0065243 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.0055005 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.005795 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.0061053 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.0064321 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.202 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.0071394 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.0075215 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.0079244 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.0083486 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.0087957 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.0092665 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.007778 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.0081097 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.0084557 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.0088164 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.0091926 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.0095845 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0.0099934 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0.01042 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0.010864 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.91082 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 5.858 | untie_min_inv | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 1.0386 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 1.109 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 1.1842 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 1.2645 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 1.3502 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 1.1383 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 1.1993 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 1.2635 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 1.3311 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 1.4024 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 1.4775 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 1.5566 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 1.64 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 1.7278 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 1.8203 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 1.9177 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 1.6097 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 1.6783 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 1.7499 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 1.8246 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 1.9024 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.9835 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 2.0682 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 2.1564 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 2.2484 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.02225 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.025312 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.025845 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.027657 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.028697 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.03458 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.024187 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.02348 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.032191 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.03219 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.032191 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.03219 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.032191 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.036387 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.036387 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.036386 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.036387 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.036387 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.041507 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.043397 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.045374 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.04744 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.049601 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.051861 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.054222 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0.056693 | lid_fill | 2026-06-30T10:05:12.360449
BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0.059274 | lid_fill | 2026-06-30T10:05:12.360449
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2029 | 5.5206 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2030 | 5.3583 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2031 | 5.1959 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2032 | 5.0335 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2033 | 4.8711 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2034 | 4.7088 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2035 | 4.5464 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2036 | 4.384 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2037 | 4.2217 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2038 | 4.0593 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2039 | 3.8969 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2040 | 3.7345 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2041 | 3.5722 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2042 | 3.4098 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2043 | 3.2474 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2044 | 3.0851 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2045 | 2.9227 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2046 | 2.7603 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2047 | 2.5979 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2048 | 2.4356 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2049 | 2.2732 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2050 | 2.1108 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2029 | 0.077333 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2030 | 0.074667 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2031 | 0.072 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2032 | 0.069333 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2033 | 0.066667 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2034 | 0.064 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2035 | 0.061333 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2036 | 0.058667 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2037 | 0.056 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2038 | 0.053333 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2039 | 0.050667 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2040 | 0.048 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2041 | 0.045333 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2042 | 0.042667 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2043 | 0.04 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2044 | 0.037333 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2045 | 0.034667 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2046 | 0.032 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2047 | 0.029333 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2048 | 0.026667 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2049 | 0.024 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2050 | 0.021333 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2029 | 35.9399 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2030 | 34.8829 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2031 | 33.8258 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2032 | 32.7688 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2033 | 31.7117 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2034 | 30.6547 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2035 | 29.5976 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2036 | 28.5405 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2037 | 27.4835 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2038 | 26.4264 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2039 | 25.3694 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2040 | 24.3123 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2041 | 23.2553 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2042 | 22.1982 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2043 | 21.1411 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2044 | 20.0841 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2045 | 19.027 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2046 | 17.97 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2047 | 16.9129 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2048 | 15.8559 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2049 | 14.7988 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2050 | 13.7417 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2029 | 12.6034 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2030 | 12.1688 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2031 | 11.7342 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2032 | 11.2996 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2033 | 10.865 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2034 | 10.4304 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2035 | 9.9958 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2036 | 9.5612 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2037 | 9.1266 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2038 | 8.692 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2039 | 8.2574 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2040 | 7.8228 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2041 | 7.3882 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2042 | 6.9536 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2043 | 6.519 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2044 | 6.0844 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2045 | 5.6498 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2046 | 5.2152 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2047 | 4.7806 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2048 | 4.346 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2049 | 3.9114 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2050 | 3.4768 |  | 2026-06-30T15:27:50.016668
A_Calibrated_BAU | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.5 | lid_floor | 2026-06-30T15:27:53.787064
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 2.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 3.3 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 4.1 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 4.9 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 5.7 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 6.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 7 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 7.75 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 8 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 8.25 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 8.5 | override | 2026-06-30T15:28:00.276522
A_Calibrated_BAU | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 8.5 | override | 2026-06-30T15:28:00.276522
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2029 | 5.5206 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2030 | 5.3583 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2031 | 5.1959 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2032 | 5.0335 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2033 | 4.8711 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2034 | 4.7088 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2035 | 4.5464 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2036 | 4.384 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2037 | 4.2217 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2038 | 4.0593 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2039 | 3.8969 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2040 | 3.7345 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2041 | 3.5722 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2042 | 3.4098 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2043 | 3.2474 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2044 | 3.0851 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2045 | 2.9227 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2046 | 2.7603 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2047 | 2.5979 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2048 | 2.4356 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2049 | 2.2732 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2050 | 2.1108 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2029 | 0.077333 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2030 | 0.074667 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2031 | 0.072 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2032 | 0.069333 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2033 | 0.066667 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2034 | 0.064 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2035 | 0.061333 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2036 | 0.058667 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2037 | 0.056 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2038 | 0.053333 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2039 | 0.050667 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2040 | 0.048 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2041 | 0.045333 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2042 | 0.042667 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2043 | 0.04 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2044 | 0.037333 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2045 | 0.034667 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2046 | 0.032 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2047 | 0.029333 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2048 | 0.026667 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2049 | 0.024 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2050 | 0.021333 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2029 | 35.9399 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2030 | 34.8829 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2031 | 33.8258 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2032 | 32.7688 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2033 | 31.7117 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2034 | 30.6547 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2035 | 29.5976 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2036 | 28.5405 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2037 | 27.4835 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2038 | 26.4264 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2039 | 25.3694 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2040 | 24.3123 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2041 | 23.2553 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2042 | 22.1982 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2043 | 21.1411 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2044 | 20.0841 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2045 | 19.027 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2046 | 17.97 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2047 | 16.9129 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2048 | 15.8559 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2049 | 14.7988 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2050 | 13.7417 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2029 | 12.6034 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2030 | 12.1688 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2031 | 11.7342 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2032 | 11.2996 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2033 | 10.865 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2034 | 10.4304 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2035 | 9.9958 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2036 | 9.5612 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2037 | 9.1266 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2038 | 8.692 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2039 | 8.2574 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2040 | 7.8228 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2041 | 7.3882 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2042 | 6.9536 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2043 | 6.519 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2044 | 6.0844 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2045 | 5.6498 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2046 | 5.2152 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2047 | 4.7806 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2048 | 4.346 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2049 | 3.9114 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2050 | 3.4768 |  | 2026-06-30T15:55:30.242232
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18104 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 6.9859e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 7.4596e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 7.9656e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 8.5056e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9.0825e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 6.1164e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 6.2879e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 4.2914e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 4.3054e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 4.3085e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 4.2997e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 4.2776e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 4.2408e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 4.1876e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 4.1171e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 4.0265e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 3.9147e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 3.7791e-05 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 2.7198e-05 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 3.7201e-05 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 4.2644e-05 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 4.1842e-05 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 3.2341e-05 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 6.7516e-06 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.40749 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.43512 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.46463 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.49613 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.53508 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.36034 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.37044 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.25282 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.25364 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.25383 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.25331 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.25201 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.24984 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.24671 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.24255 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.23722 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.23063 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.22264 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18104 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.00037493 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.00042653 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.00043551 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.00046603 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.00048356 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.00037565 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.00018128 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.00015098 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.00026523 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.00023962 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.00021403 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.00018842 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.00016283 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.00019292 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.00016398 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.00013504 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.00010611 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 8.5679e-05 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.00017999 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.00026414 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.00034159 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.00040804 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.00048711 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.0004959 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.00023519 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 1.212 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 1.212 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18104 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.034056 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.038743 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.039559 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.042332 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.043924 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.034122 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.016466 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.013714 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.024092 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.021766 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.019441 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.017115 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.01479 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.017524 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.014895 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.012266 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.0096383 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.0077826 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.016349 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.023993 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.031028 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.037064 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.044246 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.045044 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.021363 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.39701 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 1.3332 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.45269 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.48337 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.51616 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.34759 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.35734 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.24388 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.24467 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.24485 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.24435 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.2431 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.24101 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.23798 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.23397 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.22883 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.22247 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.21477 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.15456 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.21141 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.24235 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.23779 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.1838 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.03837 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.38708 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.44035 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.44963 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.505 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.83206 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.90492 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.56146 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.46762 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.82147 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.74216 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.66289 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.58358 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.50432 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.59752 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.5079 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.41825 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.32864 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.26537 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.55747 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.8181 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 1.058 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 1.2638 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 1.5087 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 1.6904 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.5819 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 3.426 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 3.8802 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 3.1159 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.11337 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.10868 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.12429 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.13954 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.15425 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.17331 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.19127 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.20785 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.22263 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.23528 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.24984 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.19615 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.36158 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.101 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.1343 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.14606 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.18562 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.19166 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.19259 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.18838 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.1845 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.24432 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.22953 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.20702 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.17681 | lid_relaxed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.15705 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.3599 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.57218 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.79688 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 1.0199 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 1.3799 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 1.6904 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.5819 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 3.426 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 3.8802 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.11102 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.16979 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.28229 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.42807 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.63201 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 1.0195 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 1.6904 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.5819 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 3.426 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 3.8802 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 2.3916 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 2.7207 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 2.778 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 2.9727 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 3.0845 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 2.424 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 2.424 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.96307 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 1.6918 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 1.5285 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 1.3652 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 8.1204 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 1.0386 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 1.2306 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 1.046 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.86139 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.67685 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.54653 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 1.1481 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 1.6849 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 2.1789 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 2.6028 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 3.1071 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 3.1632 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 1.5002 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.202 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18104 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.91082 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 5.858 | untie_min_inv | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 1.0386 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 1.109 | lid_fill | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 1.421 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.95695 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.98378 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.67141 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.6736 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.6741 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.67271 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.66926 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.6635 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.65518 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.64414 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.62997 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.61248 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.59127 | lid_family_capped | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.42552 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.58204 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.66719 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.65465 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.11102 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.16979 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.28229 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.42807 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.63201 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 1.0195 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 1.6904 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.5819 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 3.426 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 3.8802 | lid_adequacy_scaled | 2026-06-30T15:55:35.480904
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 2.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 3.3 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 4.1 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 4.9 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 5.7 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 6.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 7 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 7.75 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 8 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 8.25 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 8.5 | override | 2026-06-30T15:55:38.924841
B_Optimised_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 8.5 | override | 2026-06-30T15:55:38.924841
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2029 | 5.5206 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2030 | 5.3583 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2031 | 5.1959 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2032 | 5.0335 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2033 | 4.8711 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2034 | 4.7088 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2035 | 4.5464 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2036 | 4.384 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2037 | 4.2217 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2038 | 4.0593 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2039 | 3.8969 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2040 | 3.7345 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2041 | 3.5722 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2042 | 3.4098 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2043 | 3.2474 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2044 | 3.0851 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2045 | 2.9227 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2046 | 2.7603 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2047 | 2.5979 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2048 | 2.4356 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2049 | 2.2732 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOABGDXX | ResidualCapacity | 2050 | 2.1108 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2029 | 0.077333 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2030 | 0.074667 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2031 | 0.072 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2032 | 0.069333 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2033 | 0.066667 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2034 | 0.064 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2035 | 0.061333 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2036 | 0.058667 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2037 | 0.056 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2038 | 0.053333 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2039 | 0.050667 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2040 | 0.048 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2041 | 0.045333 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2042 | 0.042667 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2043 | 0.04 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2044 | 0.037333 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2045 | 0.034667 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2046 | 0.032 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2047 | 0.029333 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2048 | 0.026667 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2049 | 0.024 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSINDEA | ResidualCapacity | 2050 | 0.021333 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2029 | 35.9399 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2030 | 34.8829 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2031 | 33.8258 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2032 | 32.7688 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2033 | 31.7117 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2034 | 30.6547 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2035 | 29.5976 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2036 | 28.5405 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2037 | 27.4835 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2038 | 26.4264 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2039 | 25.3694 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2040 | 24.3123 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2041 | 23.2553 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2042 | 22.1982 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2043 | 21.1411 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2044 | 20.0841 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2045 | 19.027 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2046 | 17.97 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2047 | 16.9129 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2048 | 15.8559 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2049 | 14.7988 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRCOAINDEA | ResidualCapacity | 2050 | 13.7417 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2029 | 12.6034 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2030 | 12.1688 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2031 | 11.7342 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2032 | 11.2996 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2033 | 10.865 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2034 | 10.4304 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2035 | 9.9958 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2036 | 9.5612 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2037 | 9.1266 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2038 | 8.692 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2039 | 8.2574 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2040 | 7.8228 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2041 | 7.3882 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2042 | 6.9536 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2043 | 6.519 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2044 | 6.0844 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2045 | 5.6498 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2046 | 5.2152 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2047 | 4.7806 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2048 | 4.346 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2049 | 3.9114 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | ResidualCapacity | 2050 | 3.4768 |  | 2026-06-30T15:57:17.535870
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18288 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 6.9859e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 7.4596e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 7.9656e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 8.5056e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9.0825e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 6.1164e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 6.2879e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 4.2914e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 4.3054e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 4.3085e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 4.2997e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 4.2776e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 4.2408e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 4.1876e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 4.1171e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 4.0265e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 3.9147e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 3.7791e-05 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 2.7474e-05 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 3.7201e-05 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 4.2644e-05 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 4.1842e-05 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 3.2341e-05 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 6.7516e-06 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.40749 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.43512 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.46463 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.49613 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.53508 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.36034 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.37044 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.25282 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.25364 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.25383 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.25331 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.25201 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.24984 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.24671 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.24255 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.23722 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.23063 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.22264 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18288 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWROILBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.00037493 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.00042653 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.00043551 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.00046603 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.00048356 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.00037565 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.00018128 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.00015098 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.00026523 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.00023962 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.00021403 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.00018842 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.00016283 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.00019292 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.00016398 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.00013504 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.00010611 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9.9822e-05 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.00021903 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.00031764 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.00040366 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.00046942 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.00053788 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.0004959 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.00023519 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWASINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 1.212 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 1.212 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18288 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRURNBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.034056 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.038743 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.039559 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.042332 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.043924 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.034122 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.016466 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.013714 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.024092 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.021766 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.019441 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.017115 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.01479 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.017524 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.014895 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.012266 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.0096383 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.0090673 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.019896 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.028852 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.036666 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.042639 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 0.048858 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 0.045044 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 0.021363 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRBIOINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.39701 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 1.3332 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.45269 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.48337 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.51616 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.34759 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.35734 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.24388 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.24467 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.24485 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.24435 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.2431 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.24101 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.23798 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.23397 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.22883 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.22247 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.21477 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.15614 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.21141 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.24235 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.23779 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.1838 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 0.03837 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOABGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.38708 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.44035 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.44963 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.505 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.51588 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.41368 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.20587 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.1777 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.32311 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.30181 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.27842 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.35451 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.22526 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.27486 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.2404 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.20355 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.16432 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.16489 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.38443 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.59028 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.79181 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.96927 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 1.2217 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 1.6904 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.5819 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 3.426 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRHYDINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 3.8802 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 3.1159 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18288 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.36158 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.101 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.12935 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.20663 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.33947 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.50585 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.72708 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 1.1257 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 1.6904 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.5819 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 3.426 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 3.8802 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.12935 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.20663 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.33947 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.50585 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.72708 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 1.1257 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 1.6904 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.5819 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 3.426 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 3.8802 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0 | lid_floor_suppressed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 2.3916 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 2.7207 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 2.778 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 2.9727 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 3.0845 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 2.424 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 2.424 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.96307 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 1.6918 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 1.5285 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 1.3652 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 8.1204 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 1.0386 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 1.2306 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 1.046 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.86139 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.67685 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.63674 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 1.3972 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 2.0261 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 2.5748 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 2.9943 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 3.431 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 3.1632 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 1.5002 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRCOAINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 0 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSDSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_maxcap_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRLDSINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 9999 | exempt_uncapped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.202 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.18288 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.29424 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.42497 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.58277 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRWONBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 0.91082 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 5.858 | untie_min_inv | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 1.0386 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 1.109 | lid_fill | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 1.2236 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 0.85062 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 0.9018 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 0.63784 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 0.66237 | lid_relaxed | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 0.6741 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 0.67271 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 0.66926 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 0.6635 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 0.65518 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 0.64414 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 0.62997 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 0.61248 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 0.59127 | lid_family_capped | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 0.42985 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 0.58204 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 0.66719 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 0.65465 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 0.7957 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 1.011 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 1.2063 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 1.392 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRNGSBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 1.5731 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 0.1 | lid_floor | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 0.12935 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 0.20663 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 0.33947 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 0.50585 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 0.72708 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 1.1257 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 1.6904 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.5819 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 3.426 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSHPINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 3.8802 | lid_adequacy_scaled | 2026-06-30T15:57:21.661310
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2023 | 5.0934 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2024 | 5.9084 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2025 | 5.89 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2026 | 6.3721 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2027 | 6.8917 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2028 | 11.1178 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2029 | 15.598 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2030 | 20.1517 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2031 | 20.6313 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2032 | 21.3411 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2033 | 21.3498 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2034 | 21.3339 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2035 | 24.2408 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2036 | 24.8799 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2037 | 26.0704 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2038 | 27.262 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2039 | 28.4525 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2040 | 29.5719 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2041 | 30.6111 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2042 | 32.0103 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2043 | 33.5129 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2044 | 35.1037 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2045 | 36.7864 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2046 | 38.5658 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2047 | 40.4454 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2048 | 42.4288 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2049 | 44.5187 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityLowerLimit | 2050 | 46.7002 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2023 | 1.2508 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2024 | 1.3614 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2025 | 1.7597 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2026 | 1.8468 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2027 | 1.968 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2028 | 2.5617 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2029 | 3.594 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2030 | 4.6433 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2031 | 4.7538 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2032 | 4.9173 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2033 | 4.9193 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2034 | 4.9157 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2035 | 5.5855 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2036 | 5.7327 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2037 | 6.007 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2038 | 6.2816 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2039 | 6.5559 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2040 | 6.8138 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2041 | 7.0533 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2042 | 7.3757 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2043 | 7.7219 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2044 | 8.0885 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2045 | 8.4762 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2046 | 8.8862 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2047 | 9.3193 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2048 | 9.7763 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2049 | 10.2578 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacity | 2050 | 10.7605 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2023 | 5.4283 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2024 | 5.9674 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2025 | 7.637 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2026 | 8.0151 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2027 | 8.5411 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2028 | 11.229 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2029 | 15.754 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2030 | 20.3532 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2031 | 20.8376 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2032 | 21.5546 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2033 | 21.5633 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2034 | 21.5472 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2035 | 24.4832 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2036 | 25.1287 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2037 | 26.3311 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2038 | 27.5347 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2039 | 28.7371 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2040 | 29.8676 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2041 | 30.9172 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2042 | 32.3304 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2043 | 33.8481 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2044 | 35.4547 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2045 | 37.1543 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2046 | 38.9514 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2047 | 40.8498 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2048 | 42.8531 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2049 | 44.9639 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVINDEA | TotalTechnologyAnnualActivityUpperLimit | 2050 | 47.1672 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2023 | 3.0413 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2024 | 2.3611 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2025 | 3.2685 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2026 | 3.3086 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2027 | 3.3439 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2028 | 8.9297 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2029 | 16.4319 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2030 | 25.6723 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2031 | 31.9278 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2032 | 39.1373 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2033 | 51.1236 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2034 | 64.8435 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2035 | 61.4204 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2036 | 72.6909 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2037 | 82.0182 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2038 | 92.2123 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2039 | 103.3622 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2040 | 116.1527 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2041 | 130.8397 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2042 | 142.9487 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2043 | 155.4428 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2044 | 168.5038 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2045 | 182.1375 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2046 | 196.3515 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2047 | 211.1572 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2048 | 226.5785 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2049 | 242.6481 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityLowerLimit | 2050 | 259.6457 | activity_floor | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2023 | 1.3212 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2023 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2024 | 1.3716 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2024 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2025 | 5.1106 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2025 | 3.739 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2026 | 5.168 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2026 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2027 | 5.2294 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2027 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2028 | 5.2949 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2028 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2029 | 5.3648 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2029 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2030 | 5.8077 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2030 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2031 | 7.2228 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2031 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2032 | 8.8538 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2032 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2033 | 11.5654 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2033 | 2.7116 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2034 | 14.6691 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2034 | 3.1038 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2035 | 13.8947 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2035 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2036 | 16.4444 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2036 | 2.5497 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2037 | 18.5545 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2037 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2038 | 20.8606 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2038 | 2.4 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2039 | 23.383 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2039 | 2.5224 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2040 | 26.2765 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2040 | 2.8935 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2041 | 29.599 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2041 | 3.3225 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2042 | 32.3384 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2042 | 2.7394 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2043 | 35.1648 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2043 | 2.8265 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2044 | 38.1195 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2044 | 2.9547 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2045 | 41.2038 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2045 | 3.0843 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2046 | 44.4194 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2046 | 3.2155 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2047 | 47.7688 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2047 | 3.3494 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2048 | 51.2574 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2048 | 3.4887 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2049 | 54.8927 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2049 | 3.6353 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacity | 2050 | 58.738 | cap_envelope_maxcap | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalAnnualMaxCapacityInvestment | 2050 | 3.8452 | cap_envelope_maxinv | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2023 | 5.8402 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2024 | 6.063 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2025 | 22.5907 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2026 | 22.8448 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2027 | 23.1159 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2028 | 23.4055 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2029 | 23.7148 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2030 | 25.929 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2031 | 32.247 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2032 | 39.5287 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2033 | 51.6349 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2034 | 65.492 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2035 | 62.0346 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2036 | 73.4178 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2037 | 82.8384 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2038 | 93.1344 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2039 | 104.3958 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2040 | 117.3142 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2041 | 132.1481 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2042 | 144.3782 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2043 | 156.9972 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2044 | 170.1888 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2045 | 183.9589 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2046 | 198.315 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2047 | 213.2688 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2048 | 228.8443 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2049 | 245.0746 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | PWRSPVBGDXX | TotalTechnologyAnnualActivityUpperLimit | 2050 | 262.2421 | pin_generation_upper | 2026-06-30T15:57:26.383231
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2023 | 2.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2024 | 3.3 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2025 | 4.1 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2026 | 4.9 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2027 | 5.7 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2028 | 6.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2029 | 7 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2030 | 7.75 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2031 | 8 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2032 | 8.25 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2033 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2034 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2035 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2036 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2037 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2038 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2039 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2040 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2041 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2042 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2043 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2044 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2045 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2046 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2047 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2048 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2049 | 8.5 | override | 2026-06-30T15:57:29.791788
C_Target_VRE | Secondary Techs | TRNBGDXXINDEA | TotalAnnualMaxCapacityInvestment | 2050 | 8.5 | override | 2026-06-30T15:57:29.791788

## Fixed_Horizon_Parameters
scenario | Tech.Type | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Value
BAU | Secondary | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Secondary | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Secondary | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Secondary | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Secondary | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Secondary | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Secondary | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 2 | OperationalLife | years | 80
BAU | Secondary | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Secondary | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 40
BAU | Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
BAU | Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 35 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
BAU | Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 2 | OperationalLife | years | 40
BAU | Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.4726
BAU | Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 38 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 91300
BAU | Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 27.5
BAU | Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
BAU | Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 41 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
BAU | Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 2 | OperationalLife | years | 27.5
BAU | Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.3377
BAU | Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 44 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
BAU | Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 30
BAU | Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
BAU | Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 50 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 73300
BAU | Secondary | 52 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 52 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 30
BAU | Secondary | 52 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
BAU | Secondary | 52 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 55 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 55 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 2 | OperationalLife | years | 30
BAU | Secondary | 55 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
BAU | Secondary | 55 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
BAU | Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 62 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
BAU | Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
BAU | Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 65 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
BAU | Secondary | 69 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 69 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 2 | OperationalLife | years | 60
BAU | Secondary | 69 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
BAU | Secondary | 69 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 72 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 72 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 60
BAU | Secondary | 72 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
BAU | Secondary | 72 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 74 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 74 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 15
BAU | Secondary | 74 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
BAU | Secondary | 74 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 78 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 78 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 2 | OperationalLife | years | 15
BAU | Secondary | 78 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
BAU | Secondary | 78 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 84 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 84 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 84 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
BAU | Secondary | 84 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Secondary | 88 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 88 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 2 | OperationalLife | years | 25
BAU | Secondary | 88 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
BAU | Secondary | 88 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 94 | MINCOABGD | Coal mining/import, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 94 | MINCOABGD | Coal mining/import, Bangladesh | 2 | OperationalLife | years | 99
BAU | Primary | 94 | MINCOABGD | Coal mining/import, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 94 | MINCOABGD | Coal mining/import, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 96 | MINCOAIND | Coal mining/import, India | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 96 | MINCOAIND | Coal mining/import, India | 2 | OperationalLife | years | 99
BAU | Primary | 96 | MINCOAIND | Coal mining/import, India | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 96 | MINCOAIND | Coal mining/import, India | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 100 | MINGASBGD | Natural Gas supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 100 | MINGASBGD | Natural Gas supply, Bangladesh | 2 | OperationalLife | years | 99
BAU | Primary | 100 | MINGASBGD | Natural Gas supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 100 | MINGASBGD | Natural Gas supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 102 | MINGASIND | Natural Gas supply, India | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 102 | MINGASIND | Natural Gas supply, India | 2 | OperationalLife | years | 99
BAU | Primary | 102 | MINGASIND | Natural Gas supply, India | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 102 | MINGASIND | Natural Gas supply, India | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 106 | MINOILBGD | Oil supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 106 | MINOILBGD | Oil supply, Bangladesh | 2 | OperationalLife | years | 99
BAU | Primary | 106 | MINOILBGD | Oil supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 106 | MINOILBGD | Oil supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 108 | MINOILIND | Oil supply, India | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 108 | MINOILIND | Oil supply, India | 2 | OperationalLife | years | 99
BAU | Primary | 108 | MINOILIND | Oil supply, India | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 108 | MINOILIND | Oil supply, India | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 112 | MINURNBGD | Uranium supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 112 | MINURNBGD | Uranium supply, Bangladesh | 2 | OperationalLife | years | 99
BAU | Primary | 112 | MINURNBGD | Uranium supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 112 | MINURNBGD | Uranium supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 114 | MINURNIND | Uranium supply, India | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 114 | MINURNIND | Uranium supply, India | 2 | OperationalLife | years | 99
BAU | Primary | 114 | MINURNIND | Uranium supply, India | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 114 | MINURNIND | Uranium supply, India | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 118 | RNWBIOBGDXX | Biomass supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 118 | RNWBIOBGDXX | Biomass supply, Bangladesh | 2 | OperationalLife | years | 99
BAU | Primary | 118 | RNWBIOBGDXX | Biomass supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 118 | RNWBIOBGDXX | Biomass supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Primary | 122 | RNWBIOINDEA | Biomass supply, India – East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Primary | 122 | RNWBIOINDEA | Biomass supply, India – East | 2 | OperationalLife | years | 99
BAU | Primary | 122 | RNWBIOINDEA | Biomass supply, India – East | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Primary | 122 | RNWBIOINDEA | Biomass supply, India – East | 4 | OutputActivityRatio | PJ/PJ | 1
BAU | Demand | 128 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 128 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 2 | OperationalLife | years | 50
BAU | Demand | 128 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 128 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
BAU | Demand | 132 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 132 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 2 | OperationalLife | years | 50
BAU | Demand | 132 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 132 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
BAU | Demand | 138 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 138 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 2 | OperationalLife | years | 50
BAU | Demand | 138 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 138 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
BAU | Demand | 142 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 142 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 2 | OperationalLife | years | 50
BAU | Demand | 142 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 142 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
BAU | Demand | 148 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 148 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 2 | OperationalLife | years | 50
BAU | Demand | 148 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 148 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
BAU | Demand | 152 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 152 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 2 | OperationalLife | years | 50
BAU | Demand | 152 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 152 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
BAU | Demand | 158 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 158 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 2 | OperationalLife | years | 50
BAU | Demand | 158 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 158 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
BAU | Demand | 162 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 162 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 2 | OperationalLife | years | 50
BAU | Demand | 162 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 162 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
BAU | Demand | 168 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Demand | 168 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 2 | OperationalLife | years | 50
BAU | Demand | 168 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Demand | 168 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 4 | OutputActivityRatio | PJ/PJ | 0.95
BAU | Secondary | 27 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
BAU | Secondary | 27 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
BAU | Secondary | 27 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) | 2 | OperationalLife | years | 80
BAU | Secondary | 27 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1

## Primary_Techs
scenario | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BAU | 1 | MINCOABGD | Coal mining/import, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
BAU | 1 | MINCOABGD | Coal mining/import, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 1 | MINCOABGD | Coal mining/import, Bangladesh | 3 | ResidualCapacity | GW |  | 0
BAU | 1 | MINCOABGD | Coal mining/import, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 1 | MINCOABGD | Coal mining/import, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 3 | MINCOAIND | Coal mining/import, India | 1 | CapitalCost | USD/kW |  | 0
BAU | 3 | MINCOAIND | Coal mining/import, India | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 3 | MINCOAIND | Coal mining/import, India | 3 | ResidualCapacity | GW |  | 0
BAU | 3 | MINCOAIND | Coal mining/import, India | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 3 | MINCOAIND | Coal mining/import, India | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 7 | MINGASBGD | Natural Gas supply, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
BAU | 7 | MINGASBGD | Natural Gas supply, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 7 | MINGASBGD | Natural Gas supply, Bangladesh | 3 | ResidualCapacity | GW |  | 0
BAU | 7 | MINGASBGD | Natural Gas supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 7 | MINGASBGD | Natural Gas supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 9 | MINGASIND | Natural Gas supply, India | 1 | CapitalCost | USD/kW |  | 0
BAU | 9 | MINGASIND | Natural Gas supply, India | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 9 | MINGASIND | Natural Gas supply, India | 3 | ResidualCapacity | GW |  | 0
BAU | 9 | MINGASIND | Natural Gas supply, India | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 9 | MINGASIND | Natural Gas supply, India | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 13 | MINOILBGD | Oil supply, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
BAU | 13 | MINOILBGD | Oil supply, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 13 | MINOILBGD | Oil supply, Bangladesh | 3 | ResidualCapacity | GW |  | 0
BAU | 13 | MINOILBGD | Oil supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 13 | MINOILBGD | Oil supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 15 | MINOILIND | Oil supply, India | 1 | CapitalCost | USD/kW |  | 0
BAU | 15 | MINOILIND | Oil supply, India | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 15 | MINOILIND | Oil supply, India | 3 | ResidualCapacity | GW |  | 0
BAU | 15 | MINOILIND | Oil supply, India | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 15 | MINOILIND | Oil supply, India | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 19 | MINURNBGD | Uranium supply, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
BAU | 19 | MINURNBGD | Uranium supply, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 19 | MINURNBGD | Uranium supply, Bangladesh | 3 | ResidualCapacity | GW |  | 0
BAU | 19 | MINURNBGD | Uranium supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 19 | MINURNBGD | Uranium supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 21 | MINURNIND | Uranium supply, India | 1 | CapitalCost | USD/kW |  | 0
BAU | 21 | MINURNIND | Uranium supply, India | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 21 | MINURNIND | Uranium supply, India | 3 | ResidualCapacity | GW |  | 0
BAU | 21 | MINURNIND | Uranium supply, India | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 21 | MINURNIND | Uranium supply, India | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 1 | CapitalCost | USD/kW |  | 0
BAU | 25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 3 | ResidualCapacity | GW |  | 0
BAU | 25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0
BAU | 29 | RNWBIOINDEA | Biomass supply, India – East | 1 | CapitalCost | USD/kW |  | 0
BAU | 29 | RNWBIOINDEA | Biomass supply, India – East | 2 | FixedCost | USD/kW/yr |  | 0
BAU | 29 | RNWBIOINDEA | Biomass supply, India – East | 3 | ResidualCapacity | GW |  | 0
BAU | 29 | RNWBIOINDEA | Biomass supply, India – East | 4 | TotalAnnualMaxCapacity | GW |  | 0
BAU | 29 | RNWBIOINDEA | Biomass supply, India – East | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ |  | 0

## Secondary_Techs
scenario | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 840 | 822 | 804 | 785.4 | 766.8 | 748.2 | 729.6 | 711 | 692.7 | 674.4 | 656.1 | 637.8 | 619.5 | 609.3 | 599.1 | 588.9 | 578.7 | 568.5 | 558.3 | 548.1 | 537.9 | 527.7 | 517.5 | 507.3 | 497.1 | 486.9 | 476.7 | 466.5
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 12 | 12 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 10.5 | 10.2 | 9.9 | 9.6 | 9.3 | 9 | 9 | 9 | 9 | 9 | 9 | 8.7 | 8.4 | 8.1 | 7.8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601 | 0.601
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 3.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647 | 0.96647
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0.075 | 0.024 | 0.358 | 0.01 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1218 | 1158.78 | 1099.56 | 1091.88 | 1084.2 | 1076.51 | 1068.83 | 1061.15 | 1053.79 | 1046.42 | 1039.06 | 1031.7 | 1024.34 | 1016.97 | 1009.61 | 1002.25 | 994.89 | 987.52 | 980.16 | 972.8 | 965.44 | 958.07 | 950.71 | 943.03 | 935.35 | 927.66 | 919.98 | 912.3
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 35.2 | 35.2 | 35.2 | 34.88 | 34.56 | 34.24 | 33.92 | 33.6 | 33.28 | 32.96 | 32.64 | 32.32 | 32 | 32 | 32 | 32 | 32 | 32 | 31.68 | 31.36 | 31.04 | 30.72 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 11 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 15 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3800 | 3784 | 3768 | 3702.8 | 3637.6 | 3572.4 | 3507.2 | 3442 | 3156.4 | 2870.8 | 2585.2 | 2299.6 | 2014 | 2003.2 | 1992.4 | 1981.6 | 1970.8 | 1960 | 1951.8 | 1943.6 | 1935.4 | 1927.2 | 1919 | 1912.4 | 1905.8 | 1899.2 | 1892.6 | 1886
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114 | 114 | 114 | 112.2 | 110.4 | 108.6 | 106.8 | 105 | 103.4 | 101.8 | 100.2 | 98.6 | 97 | 95.6 | 94.2 | 92.8 | 91.4 | 90 | 88.8 | 87.6 | 86.4 | 85.2 | 84 | 83.2 | 82.4 | 81.6 | 80.8 | 80
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 23 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 6650 | 6510 | 6370 | 6060.6 | 5751.2 | 5441.8 | 5132.4 | 4823 | 4602.8 | 4382.7 | 4162.6 | 3942.4 | 3722.2 | 3694.2 | 3666.2 | 3638.2 | 3610.2 | 3582.2 | 3561.2 | 3540.2 | 3519.2 | 3498.2 | 3477.2 | 3460.8 | 3444.3 | 3427.9 | 3411.5 | 3395
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 199.5 | 195.12 | 190.75 | 187.6 | 184.45 | 181.3 | 178.15 | 175 | 172.2 | 169.4 | 166.6 | 163.8 | 161 | 158.9 | 156.8 | 154.7 | 152.6 | 150.5 | 148.4 | 146.3 | 144.2 | 142.1 | 140 | 138.25 | 136.5 | 134.75 | 133 | 131.25
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 24 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2500 | 2525 | 2550 | 2565 | 2580 | 2595 | 2610 | 2625 | 2640 | 2655 | 2670 | 2685 | 2700 | 2715 | 2730 | 2745 | 2760 | 2775 | 2790 | 2805 | 2820 | 2835 | 2850 | 2865 | 2880 | 2895 | 2910 | 2925
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 31 | PWRHYDINDEA | Large Hydropower, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.066 | 0.12 | 0.5 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | bar: 2023
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | bar: 2023
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023
BAU | 33 | PWRHYDBGDXX | Large Hydropower, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | bar: 2023
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683 | 5.683
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
BAU | 36 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 1.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175 | 2175
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997 | 36.997
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
BAU | 39 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0.66 | 2.26 | 1.32 | 2.92 | 2.4 | 2.4 | 0 | 0 | 0 | 0 | 8.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913 | 913
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715 | 11.715
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038 | 13.038
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
BAU | 42 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65 | 10.65
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
BAU | 45 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833 | 5.833
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
BAU | 51 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | bar: 2023
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | bar: 2023
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023
BAU | 56 | PWROILINDEA | Oil/Diesel generation, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | bar: 2023
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4 | 2138.4
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56 | 85.56
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BAU | 59 | PWRBIOBGDXX | Biomass/Bagasse, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684 | 0.52684
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BAU | 62 | PWRBIOINDEA | Biomass/Bagasse, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058 | 0.0058
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | 69 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | 72 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
BAU | 76 | PWRURNINDEA | Nuclear, India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
BAU | 79 | PWRURNBGDXX | Nuclear, Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 1.2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1058.4 | 964.8 | 871.2 | 844.6 | 817.9 | 791.3 | 764.6 | 738 | 727.4 | 716.9 | 706.3 | 695.8 | 685.2 | 674.9 | 664.6 | 654.2 | 643.9 | 633.6 | 622.8 | 612 | 601.2 | 590.4 | 579.6 | 569 | 558.5 | 547.9 | 537.4 | 526.8
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 24 | 24.6 | 25.2 | 24.24 | 23.28 | 22.32 | 21.36 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.16 | 19.92 | 19.68 | 19.44 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 18.96 | 18.72 | 18.48 | 18.24 | 18
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
BAU | 81 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 882 | 804 | 726 | 703.8 | 681.6 | 659.4 | 637.2 | 615 | 606.2 | 597.4 | 588.6 | 579.8 | 571 | 562.4 | 553.8 | 545.2 | 536.6 | 528 | 519 | 510 | 501 | 492 | 483 | 474.2 | 465.4 | 456.6 | 447.8 | 439
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
BAU | 85 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2160 | 1957.8 | 1755.6 | 1694.2 | 1632.7 | 1571.3 | 1509.8 | 1448.4 | 1425.4 | 1402.3 | 1379.3 | 1356.2 | 1333.2 | 1310.2 | 1287.1 | 1264.1 | 1241 | 1218 | 1195 | 1171.9 | 1148.9 | 1125.8 | 1102.8 | 1080.2 | 1057.7 | 1035.1 | 1012.6 | 990
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
BAU | 91 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1800 | 1631.5 | 1463 | 1411.8 | 1360.6 | 1309.4 | 1258.2 | 1207 | 1187.8 | 1168.6 | 1149.4 | 1130.2 | 1111 | 1091.8 | 1072.6 | 1053.4 | 1034.2 | 1015 | 995.8 | 976.6 | 957.4 | 938.2 | 919 | 900.2 | 881.4 | 862.6 | 843.8 | 825
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
BAU | 95 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 9 | TotalAnnualMinCapacityInvestment | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | CapitalCost | USD/kW | User defined |  | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | FixedCost | USD/kW/yr | User defined |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | ResidualCapacity | GW | User defined |  | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442 | 0.3442
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | TotalAnnualMaxCapacity | GW | User defined
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | TotalAnnualMinCapacity | GW | User defined
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | AvailabilityFactor | fraction | User defined |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | Efficiency | fraction | User defined | bar: 2023 to 2050
BAU | 31 | PWRSHPINDEA | Small Hydropower, India – East, region XX (investable) |  | TotalAnnualMinCapacityInvestment | GW | User defined |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on J2: CostDB PWRSPV CAPEX (Conservative) ¦ BD=$840/kW (×1.5)
Note on J3: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J4: ResidualCapacity (GW): BGD solar ~750 MW. Source: BPDB 2024; Bangladesh_Power_Sector.xlsx ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on J8: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on J9: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J11: CostDB PWRSPV CAPEX (Conservative) ¦ IN base=$560/kW
Note on J12: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J13: ResidualCapacity (GW): IND East solar ~5 GW. Source: CEA Monthly RE Installed Capacity ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on J17: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on J18: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J20: CostDB PWRWON CAPEX (Conservative) ¦ BD=$1218/kW (×1.6)
Note on J21: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J22: ResidualCapacity (GW): BGD wind ~2 MW. Source: BPDB ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on J26: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on J27: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J29: CostDB PWRWON CAPEX (Conservative) ¦ IN base=$761/kW
Note on J30: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J31: ResidualCapacity (GW): IND East onshore wind ~0.5 GW. Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on J35: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on J36: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J38: CostDB PWRWOF CAPEX (Conservative) ¦ IN base=$2339/kW
Note on J39: CostDB PWRWOF Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J44: AvailabilityFactor=0.95 PWRWOF standard availability factor
Note on J45: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J53: AvailabilityFactor=0.95 PWRWOF standard availability factor
Note on J54: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J56: CostDB PWRHDR CAPEX (Conservative) ¦ IN base=$1500/kW
Note on J57: CostDB PWRHDR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J58: ResidualCapacity=5.988 GW (5988 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Hydro ¦ Node: IN_E (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on J62: AvailabilityFactor=0.95 Reservoir hydro — high mechanical availability. Source: BPC PDB 2024, NEA
Note on J63: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J74: CostDB PWRCOASCPC CAPEX (Conservative) ¦ BD=$1694/kW (×1.6)
Note on J75: CostDB PWRCOASCPC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J80: AvailabilityFactor=0.85 India CEA fleet PLF ~60-65%; AF allows ~85% availability. Source: IND_DA_Final Daily PLF sheet (NITI Aayog ICED)
Note on J81: InputActivityRatio/Efficiency=0.38 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J83: CostDB PWRCOASCPC CAPEX (Conservative) ¦ IN base=$1059/kW
Note on J84: CostDB PWRCOASCPC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J89: AvailabilityFactor=0.85 India CEA fleet PLF ~60-65%; AF allows ~85% availability. Source: IND_DA_Final Daily PLF sheet (NITI Aayog ICED)
Note on J90: InputActivityRatio/Efficiency=0.38 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J92: CostDB PWRCCG CAPEX (Conservative) ¦ BD=$770/kW (×1.1)
Note on J93: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J98: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on J99: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J101: CostDB PWRCCG CAPEX (Conservative) ¦ IN base=$700/kW
Note on J102: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J107: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on J108: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J110: CostDB PWROIL CAPEX (Conservative) ¦ BD=$770/kW (×1.1)
Note on J111: CostDB PWROIL Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J116: AvailabilityFactor=0.9 Oil/diesel backup. Source: CEB LTGEP, BPDB fleet data
Note on J117: InputActivityRatio/Efficiency=0.32 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J134: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on J135: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J137: CostDB PWRBIO CAPEX (Conservative) ¦ IN base=$1142/kW
Note on J138: CostDB PWRBIO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J139: ResidualCapacity=0.576 GW (576 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Bio Power ¦ Node: IN_E (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on J143: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on J144: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J146: CostDB PWRWTE CAPEX (Conservative)
Note on J147: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J152: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on J153: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J155: CostDB PWRWTE CAPEX (Conservative)
Note on J156: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J161: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on J162: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J164: CostDB PWRURN CAPEX (Conservative) ¦ IN base=$2000/kW
Note on J165: CostDB PWRURN Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J170: AvailabilityFactor=0.9 India nuclear fleet AF ~80-90%. Source: NPCIL annual reports
Note on J171: InputActivityRatio/Efficiency=0.33 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J173: CostDB PWRURN CAPEX (Conservative) ¦ BD=$5200/kW (×2.6)
Note on J174: CostDB PWRURN Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J179: AvailabilityFactor=0.9 India nuclear fleet AF ~80-90%. Source: NPCIL annual reports
Note on J180: InputActivityRatio/Efficiency=0.33 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J183: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J188: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on J189: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J192: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J197: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on J198: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J201: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J206: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on J207: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on J210: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on J215: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on J216: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.

## Capacities_CF
scenario | Timeslices | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BAU | S1D1 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S1D2 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524
BAU | S1D3 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S2D1 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06
BAU | S2D2 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975
BAU | S2D3 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S3D1 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05
BAU | S3D2 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906
BAU | S3D3 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05
BAU | S4D1 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S4D2 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214
BAU | S4D3 | 1 | PWRSPVBGDXX | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S1D1 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05
BAU | S1D2 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516
BAU | S1D3 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S2D1 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502
BAU | S2D2 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663
BAU | S2D3 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S3D1 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638
BAU | S3D2 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446
BAU | S3D3 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S4D1 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298
BAU | S4D2 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348
BAU | S4D3 | 5 | PWRSPVINDEA | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BAU | S1D1 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271
BAU | S1D2 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973
BAU | S1D3 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761
BAU | S2D1 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216
BAU | S2D2 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854
BAU | S2D3 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451
BAU | S3D1 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614
BAU | S3D2 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055
BAU | S3D3 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914
BAU | S4D1 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462
BAU | S4D2 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134
BAU | S4D3 | 27 | PWRWONBGDXX | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855
BAU | S1D1 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451
BAU | S1D2 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909
BAU | S1D3 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672
BAU | S2D1 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438
BAU | S2D2 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886
BAU | S2D3 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172
BAU | S3D1 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549
BAU | S3D2 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303
BAU | S3D3 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717
BAU | S4D1 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851
BAU | S4D2 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597
BAU | S4D3 | 31 | PWRWONINDEA | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278
BAU | S1D1 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S1D2 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S1D3 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S2D1 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S2D2 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S2D3 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S3D1 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S3D2 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S3D3 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S4D1 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S4D2 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S4D3 | 39 | PWRWOFINDEA | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
BAU | S1D1 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
BAU | S1D2 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
BAU | S1D3 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
BAU | S2D1 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
BAU | S2D2 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
BAU | S2D3 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
BAU | S3D1 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
BAU | S3D2 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
BAU | S3D3 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
BAU | S4D1 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
BAU | S4D2 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
BAU | S4D3 | 40 | PWRWOFBGDXX | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
BAU | S1D1 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BAU | S1D2 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BAU | S1D3 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BAU | S2D1 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
BAU | S2D2 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
BAU | S2D3 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
BAU | S3D1 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BAU | S3D2 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BAU | S3D3 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BAU | S4D1 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
BAU | S4D2 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
BAU | S4D3 | 47 | PWRHYDINDEA | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
BAU | S1D1 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D2 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D3 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D1 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D2 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D3 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D1 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D2 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D3 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D1 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D2 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D3 | 58 | PWRSDSBGDXX | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D1 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D2 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D3 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D1 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D2 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D3 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D1 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D2 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D3 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D1 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D2 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D3 | 62 | PWRSDSINDEA | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D1 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D2 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D3 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D1 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D2 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D3 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D1 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D2 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D3 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D1 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D2 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D3 | 68 | PWRLDSBGDXX | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D1 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D2 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S1D3 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D1 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D2 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S2D3 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D1 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D2 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S3D3 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D1 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D2 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
BAU | S4D3 | 72 | PWRLDSINDEA | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
Note on K2: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on K3: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3524 Previous template value: 0.2480 (replaced)
Note on K4: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on K5: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on K6: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3797 Previous template value: 0.3240 (replaced)
Note on K7: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on K8: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0001
Note on K9: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.2891 Previous template value: 0.2990 (replaced)
Note on K10: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on K11: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on K12: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3421 Previous template value: 0.3600 (replaced)
Note on K13: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on K14: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0001
Note on K15: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3516 Previous template value: 0.4400 (replaced)
Note on K16: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on K17: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0065
Note on K18: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3866 Previous template value: 0.4700 (replaced)
Note on K19: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on K20: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0056
Note on K21: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2645 Previous template value: 0.3800 (replaced)
Note on K22: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on K23: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0003
Note on K24: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3348 Previous template value: 0.4300 (replaced)
Note on K25: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on K26: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1827 Previous template value: 0.1200 (replaced)
Note on K27: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0730 Previous template value: 0.1200 (replaced)
Note on K28: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1776 Previous template value: 0.1200 (replaced)
Note on K29: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3122 Previous template value: 0.1800 (replaced)
Note on K30: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1885 Previous template value: 0.1800 (replaced)
Note on K31: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.4045 Previous template value: 0.1800 (replaced)
Note on K32: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3461 Previous template value: 0.3600 (replaced)
Note on K33: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3106 Previous template value: 0.3600 (replaced)
Note on K34: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3991 Previous template value: 0.3600 (replaced)
Note on K35: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1246 Previous template value: 0.1400 (replaced)
Note on K36: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0613 Previous template value: 0.1400 (replaced)
Note on K37: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1085 Previous template value: 0.1400 (replaced)
Note on K38: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2451 Previous template value: 0.2000 (replaced)
Note on K39: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.1191 Previous template value: 0.2000 (replaced)
Note on K40: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.1672 Previous template value: 0.2000 (replaced)
Note on K41: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3444 Previous template value: 0.2000 (replaced)
Note on K42: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2689 Previous template value: 0.2000 (replaced)
Note on K43: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.4717 Previous template value: 0.2000 (replaced)
Note on K44: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3355 Previous template value: 0.2000 (replaced)
Note on K45: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3230 Previous template value: 0.2000 (replaced)
Note on K46: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.4372 Previous template value: 0.2000 (replaced)
Note on K47: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.1851 Previous template value: 0.2000 (replaced)
Note on K48: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0876 Previous template value: 0.2000 (replaced)
Note on K49: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.1278 Previous template value: 0.2000 (replaced)
Note on K50: Confirmed by Renewables.ninja (2014-2022 mean)=0.2451 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Pre-integration value (~0.20-0.25). Lower CF consistent with Bay of Bengal wind resource.
Note on K51: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.1191 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K52: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.1672 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K53: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.3444 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K54: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.2689 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K55: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.4717 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K56: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.3355 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K57: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.3230 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K58: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.4372 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K59: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.1851 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K60: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.0876 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K61: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.1278 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on K62: AMBIGUITY: Existing=0.1500, Renewables.ninja (2014-2022 mean)=0.1827 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration) Pre-integration value (~0.35-0.45). Bay of Bengal. Limited offshore wind data for BD.
Note on K63: AMBIGUITY: Existing=0.1500, Renewables.ninja (2014-2022 mean)=0.0730 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K64: AMBIGUITY: Existing=0.1500, Renewables.ninja (2014-2022 mean)=0.1776 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K65: AMBIGUITY: Existing=0.2250, Renewables.ninja (2014-2022 mean)=0.3122 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K66: AMBIGUITY: Existing=0.2250, Renewables.ninja (2014-2022 mean)=0.1885 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K67: AMBIGUITY: Existing=0.2250, Renewables.ninja (2014-2022 mean)=0.4045 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K68: AMBIGUITY: Existing=0.4500, Renewables.ninja (2014-2022 mean)=0.3461 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K69: AMBIGUITY: Existing=0.4500, Renewables.ninja (2014-2022 mean)=0.3106 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K70: AMBIGUITY: Existing=0.4500, Renewables.ninja (2014-2022 mean)=0.3991 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K71: AMBIGUITY: Existing=0.1750, Renewables.ninja (2014-2022 mean)=0.1246 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K72: AMBIGUITY: Existing=0.1750, Renewables.ninja (2014-2022 mean)=0.0613 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K73: AMBIGUITY: Existing=0.1750, Renewables.ninja (2014-2022 mean)=0.1085 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on K74: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K75: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K76: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K77: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K78: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K79: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K80: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K81: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K82: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K83: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K84: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K85: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on K86: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K87: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K88: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K89: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K90: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K91: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K92: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K93: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K94: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K95: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K96: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K97: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K98: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K99: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K100: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K101: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K102: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K103: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K104: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K105: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K106: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K107: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K108: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K109: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K110: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K111: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K112: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K113: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K114: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K115: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K116: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K117: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K118: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K119: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K120: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K121: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on K122: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K123: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K124: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K125: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K126: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K127: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K128: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K129: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K130: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K131: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K132: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on K133: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).

## VariableCost
scenario | Mode.Operation | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Parameter | Projection.Mode | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BAU | 1 | 1 | MINCOABGD | Coal mining/import, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.28 | 4.26 | 4.24 | 4.22 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
BAU | 1 | 3 | MINCOAIND | Coal mining/import, India | 12 | VariableCost | USD/GJ | 0 | User defined | 2.2 | 2.2 | 2.2 | 2.22 | 2.24 | 2.26 | 2.28 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.32 | 2.34 | 2.36 | 2.38 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.42 | 2.44 | 2.46 | 2.48 | 2.5
BAU | 1 | 7 | MINGASBGD | Natural Gas supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 5.5 | 5.5 | 5.5 | 5.54 | 5.58 | 5.62 | 5.66 | 5.7 | 5.72 | 5.74 | 5.76 | 5.78 | 5.8 | 5.82 | 5.84 | 5.86 | 5.88 | 5.9 | 5.92 | 5.94 | 5.96 | 5.98 | 6 | 6 | 6 | 6 | 6 | 6
BAU | 1 | 9 | MINGASIND | Natural Gas supply, India | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BAU | 1 | 13 | MINOILBGD | Oil supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.64 | 14.48 | 14.32 | 14.16 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
BAU | 1 | 15 | MINOILIND | Oil supply, India | 12 | VariableCost | USD/GJ | 0 | User defined | 13.56 | 12.825 | 12.09 | 12.286 | 12.482 | 12.678 | 12.874 | 13.07 | 13.07 | 13.07 | 13.07 | 13.07 | 13.07 | 13.136 | 13.202 | 13.268 | 13.334 | 13.4 | 13.302 | 13.204 | 13.106 | 13.008 | 12.91 | 12.812 | 12.714 | 12.616 | 12.518 | 12.42
BAU | 1 | 19 | MINURNBGD | Uranium supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
BAU | 1 | 21 | MINURNIND | Uranium supply, India | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
BAU | 1 | 25 | RNWBIOBGDXX | Biomass supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
BAU | 1 | 29 | RNWBIOINDEA | Biomass supply, India – East | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.02 | 4.04 | 4.06 | 4.08 | 4.1 | 4.12 | 4.14 | 4.16 | 4.18 | 4.2 | 4.22 | 4.24 | 4.26 | 4.28 | 4.3 | 4.32 | 4.34 | 4.36 | 4.38 | 4.4 | 4.42 | 4.44 | 4.46 | 4.48 | 4.5
Note on K2: Fuel: Imported coal (FOB Aus) ¦ Nodes: BD,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 ($107/t FOB, 25 GJ/t) Projection: WEO 2025 + DESNZ Low/Central/High ¦ https://assets.publishing.service.gov.uk/media/66f3e1a8080bdf716392e855/2024-Fossil-Fuel-price-Assumptions-Publication.pdf Unit in CostDB: USD/GJ Notes: 2023 was anomalous (Ukraine war). C=flat real post-2027. A=NZE mine closures.
Note on K3: Fuel: India domestic coal ¦ Nodes: IN_all ¦ Scenario: Conservative Source: Coal India grade pricing + transport Projection: Modest real increase (C/M); decline if demand drops (A) Unit in CostDB: USD/GJ Notes: Pithead cost + rail transport. IN_E lowest, IN_S/W highest.
Note on K4: Fuel: Bangladesh piped gas ¦ Nodes: BD ¦ Scenario: Conservative Source: WB BD ESSEP (~$5.79/MMBtu) ¦ https://www.worldbank.org Projection: C=LNG convergence; M=WB anchor; A=subsidy continuation Unit in CostDB: USD/GJ Notes: Most consequential fuel uncertainty for BD node. C models rapid LNG convergence.
Note on K5: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on K6: Fuel: Diesel / HFO ¦ Nodes: LK,MV ¦ Scenario: Conservative Source: CEB LTGEP + WB Brent trajectory ¦ https://www.ceb.lk Projection: Scaled from oil price scenarios Unit in CostDB: USD/GJ Notes: MV add $4-7/GJ island delivery premium. C=flat post-2027. A=NZE oil collapse.
Note on K7: Fuel: Crude oil (Brent) ¦ Nodes: All ¦ Scenario: Conservative Source: WB CMO Oct 2025 Projection: IEA WEO 2025 STEPS/CPS/NZE ¦ https://www.iea.org/reports/world-energy-outlook-2025 Unit in CostDB: USD/bbl → converted to USD/GJ (÷6.12 GJ/bbl) Notes: C=CPS ~10% above STEPS. M=STEPS verified IISD. A=NZE verified IISD. 2023 USD.
Note on K8: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on K9: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on K10: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on K11: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.

## Demand_Projection
scenario | Demand/Share | Fuel/Tech | Name | Ref.Cap.BY | Ref.OAR.BY | Ref.km.BY | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Improvement_Notes | References
BAU | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 427.324 | 456.303 | 487.247 | 520.29 | 555.573 | 593.249 | 633.481 | 676.44 | 712.658 | 750.815 | 791.015 | 833.367 | 877.987 | 924.996 | 974.521 | 1026.699 | 1081.67 | 1139.585 | 1200.6 | 1251.814 | 1305.212 | 1360.888 | 1418.939 | 1479.467 | 1542.576 | 1608.377 | 1676.985 | 1748.52 | Actualizado a IEPMP 2023 (Power Div / JICA-IEEJ, Nov 2023), escenario ATS (Advanced Technology Scenario) / GDP case In-Between — caso principal IEEJ para planificación de potencia (Capítulo 5). Anchors oficiales IEPMP Tabla 4.3-1 (p.56): 2019=328.68 PJ (histórico), 2030=676.44 PJ, 2041=1200.60 PJ, 2050=1748.52 PJ. Años intermedios: interpolación log-lineal (CAGR entre milestones) — el IEPMP solo publica los 4 milestone years, años intermedios requieren interpolación externa. CAGRs implícitos: 6.78%/año (2019-2030), 5.35%/año (2030-2041), 4.27%/año (2041-2050). Caveat: IEPMP 2023 está en revisión por el gobierno interino; plan sucesor EPSMP 2026-2050 en preparación. IEPMP 2023 sigue siendo el plan aprobado oficial. El alternativo PP2041 (high-growth, 2425 PJ @2050) disponible en workbook fuente para sensibilidad. | Power Division / MoPEMR / JICA-IEEJ (2023). Integrated Energy and Power Master Plan (IEPMP) 2023. Government of Bangladesh, Nov 2023. Tabla 4.3-1 'Outlook of Power Supply' (p.56, PDF p.109): Power Generation TWh por GDP case (PP2041 / In-Between) en years 2019, 2030, 2041, 2050. Tabla 5.2-1 'Maximum Electric Power Demand' (p.64, PDF p.117) para peak cross-check. Escenario central: ATS (Advanced Technology Scenario, JICA-recommended). GDP case: In-Between (caso principal IEEJ Cap.5). Conversión: PJ = TWh × 3.6. URL: https://powerdivision.portal.gov.bd (repositorio IEPMP 2023). Status Abr-2026: plan aprobado vigente, en revisión por gobierno interino (plan sucesor EPSMP 2026-2050 en preparación).
BAU | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 695.444 | 738.864 | 788.26 | 838.696 | 892.667 | 948.668 | 1016.15 | 1063.35 | 1109.171 | 1171.99 | 1234.808 | 1297.627 | 1360.445 | 1423.264 | 1494.272 | 1565.28 | 1636.287 | 1707.295 | 1778.303 | 1859.302 | 1943.989 | 2032.535 | 2125.113 | 2221.908 | 2323.112 | 2428.925 | 2539.559 | 2655.231 | Actualizado a 20th EPS (CEA Nov 2022). 2023-2031: Tabla 2.5 valores exactos (anual). 2036 y 2041: Tabla 6.2 valores exactos. 2032-2035 y 2037-2040: interpolación lineal entre anchors del 20th EPS. 2042-2050: extrapolación con CAGR 4.55%/año (tasa 2036-37 a 2041-42 del 20th EPS) — fuera del horizonte del documento original. | CEA (2022). Report on Twentieth Electric Power Survey of India (Volume-I). Central Electricity Authority, Ministry of Power, Government of India, Nov 2022. Table 2.5 (Chapter 2, Sec. 2.3, printed p.33 / PDF p.34): Region-wise electrical energy requirement at power station bus bars in MU, FY2021-22 to FY2031-32. Table 6.2 (Chapter 6, printed p.166 / PDF p.167): Perspective demand projection for FY2031-32, FY2036-37, FY2041-42. Conversion: PJ = MU × 0.0036. URL: https://cea.nic.in/wp-content/uploads/ps___lf/2023/02/Volume_I_Report_of_20th_Electric_Power_Survey.pdf
Note on J2: BGD: base=86,255 GWh→310.5 PJ (BPDB 2023-24). Growth: IEPMP 2023 7%→5.8%→3.8%/yr. Sources: BGD_DA_Final, Bangladesh_new_data_v2_REV. CROSS-CHECK: Template=310.5 PJ → 86,250 GWh. Source=86,255 GWh (BPDB 2023-24). Diff=< 0.01%. MATCH
Note on J3: IND_E: CEA 20th EPS by state. Sources: India_new_data_v2.

## Demand_Profiles
scenario | Timeslices | Demand/Share | Fuel/Tech | Name | Ref.Cap.BY | Ref.OAR.BY | Ref.km.BY | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BAU | S1D1 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691
BAU | S1D2 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911
BAU | S1D3 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581
BAU | S2D1 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407
BAU | S2D2 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106
BAU | S2D3 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101
BAU | S3D1 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481
BAU | S3D2 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232
BAU | S3D3 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388
BAU | S4D1 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289
BAU | S4D2 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386
BAU | S4D3 | Demand | ELCBGDXX03 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437
BAU | S1D1 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448
BAU | S1D2 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493
BAU | S1D3 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355
BAU | S2D1 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608
BAU | S2D2 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377
BAU | S2D3 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643
BAU | S3D1 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683
BAU | S3D2 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517
BAU | S3D3 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176
BAU | S4D1 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389
BAU | S4D2 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987
BAU | S4D3 | Demand | ELCINDEA03 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351
Note on K2: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K3: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K4: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K5: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K6: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K7: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K8: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K9: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K10: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K11: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K12: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K13: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on K14: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K15: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K16: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K17: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K18: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K19: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K20: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K21: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K22: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K23: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K24: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on K25: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.

## Demand_Techs
scenario | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BAU | 1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
BAU | 1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
BAU | 1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
BAU | 1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 1 | PWRTRNBGDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
BAU | 5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
BAU | 5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
BAU | 5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 5 | PWRTRNINDEA | Existing internal transmission (non-RE), India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
BAU | 11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
BAU | 11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
BAU | 11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 11 | RNWTRNBGDXX | Existing internal transmission (RE), Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
BAU | 15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
BAU | 15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
BAU | 15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 15 | RNWTRNINDEA | Existing internal transmission (RE), India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
BAU | 21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
BAU | 21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
BAU | 21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 21 | TRNNLIBGDXX | New internal transmission line, Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
BAU | 25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
BAU | 25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
BAU | 25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 25 | TRNNLIINDEA | New internal transmission line, India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
BAU | 31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
BAU | 31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
BAU | 31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 31 | TRNRPOBGDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
BAU | 35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
BAU | 35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
BAU | 35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
BAU | 35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
BAU | 35 | TRNRPOINDEA | Repower/upgrade internal transmission, India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0

## Emissions
scenario | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BAU | 1 | PWRCOABGDXX | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
BAU | 4 | PWRCOAINDEA | Coal-fired Power, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300 | 91300
BAU | 7 | PWRNGSBGDXX | Gas-fired Power, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
BAU | 10 | PWRNGSINDEA | Gas-fired Power, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
BAU | 16 | PWROILBGDXX | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300
BAU | 20 | PWRWASINDEA | Waste-to-Energy, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
BAU | 23 | PWRWASBGDXX | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000

## Yearsplit_Template
Timeslices | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
S1D1 | 14 | YearSplit | fraction | User defined | 0 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556
S1D2 | 14 | YearSplit | fraction | User defined | 0 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389
S1D3 | 14 | YearSplit | fraction | User defined | 0 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722
S2D1 | 14 | YearSplit | fraction | User defined | 0 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111
S2D2 | 14 | YearSplit | fraction | User defined | 0 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278
S2D3 | 14 | YearSplit | fraction | User defined | 0 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444
S3D1 | 14 | YearSplit | fraction | User defined | 0 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556
S3D2 | 14 | YearSplit | fraction | User defined | 0 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389
S3D3 | 14 | YearSplit | fraction | User defined | 0 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722
S4D1 | 14 | YearSplit | fraction | User defined | 0 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111
S4D2 | 14 | YearSplit | fraction | User defined | 0 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278
S4D3 | 14 | YearSplit | fraction | User defined | 0 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444
Note on G2: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G3: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G4: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G5: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G6: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G7: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G8: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G9: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G10: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G11: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G12: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G13: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.

## DaySplit
DAILYTIMEBRACKET | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | 12 | DaySplit | fraction | User defined | 0 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913
2 | 12 | DaySplit | fraction | User defined | 0 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256
3 | 12 | DaySplit | fraction | User defined | 0 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571

## Interconnectors
scenario | NO | Project | From_Node | To_Node | Circuits | COD_Date | Affiliated_Power | Capacity_MW | Voltage_kV | DC_AC | Directionality | Status | Export_Resource_Type | Source
BAU | 6 | Bheramara back‑to‑back HVDC (India → Bangladesh) | IN_E | BD | 1 | 2013 | Grid-to-Grid | 1000 | ±400 kV | DC | Bi‑directional | Operational | Fossil / mixed | Zixuan v3 (Sheet 1)
BAU | 23 | Katihar- Parbatipur | IN_E | BD | 1 | 2028 | Grid-to-Grid | 2000 | 765 | DC | Bi-directional | Proposed | Mixed | https://cpd-power-energy-study.com/bangladesh-india-review-progress-of-katihar-parbatipur-baranagar-765kv-transmission-line/?utm_source=chatgpt.com
BAU | 24 | Parbatipur-Boronagar | BD | IN_E | 1 | 2028 | Grid-to-Grid | 2000 | 765 | DC | Bi-directional | Proposed | Mixed | Zixuan v3
BAU | 26 | Adani Power Godda HVDC (India → Bangladesh) | IN_E | BD | 1 | 2023 | Godda Coal Plant | 1496 | 400 kV | HVDC | Uni-directional | Operational | Fossil | Bangladesh_Power_Sector.xlsx
BAU | 28 | Barapukuria HVDC B2B Station | IN_E | BD | 1 | 2030 | Grid-to-Grid | 750 | 400 kV | HVDC B2B | Bi-directional | Planned | Mixed | IEPMP 2023
BAU | 30 | Jamalpur HVDC B2B Station | IN_E | BD | 1 | 2033 | Grid-to-Grid | 750 | 400 kV | HVDC B2B | Bi-directional | Proposed | Mixed | IEPMP 2023
BAU | 32 | Second Bheramara HVDC Expansion | IN_E | BD | 1 | 2029 | Grid-to-Grid | 500 | 400 kV | HVDC B2B | Bi-directional | Proposed | Mixed | PGCB / IEPMP 2023
Note on G3: India Planned: Muzaffarpur-Parbatipur 765kV, Expected COD 2027-28 (NEP Vol.II)
Note on G4: Same corridor as Katihar-Parbatipur (India NEP Vol.II, 2027-28)

## Interconnector_Params
scenario | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
BAU | 1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 1 | CapitalCost | USD/kW | User defined | 0 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
BAU | 1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 2 | FixedCost | USD/kW/yr | User defined | 0 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
BAU | 1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 3 | ResidualCapacity | GW | User defined | 0 | 2.496 | 2.496 | 2.496 | 2.496 | 2.496 | 2.496 | 2.996 | 3.746 | 3.746 | 3.746 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496 | 4.496
BAU | 1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
BAU | 1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
BAU | 1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 14 | TransmissionLossFactor | fraction | User defined | 0 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
BAU | 1 | TRNBGDXXINDEA | Cross-border interconnector: Bangladesh ↔ India East | 2 | OperationalLife | years | User defined | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Note on J2: Source: ADB Bheramara B2B ~$193m/500MW + expansion Corridor: BD↔IN_E Type: ±400kV HVDC B2B + 765kV AC Confidence: High
Note on J3: Source: ADB Bheramara B2B ~$193m/500MW + expansion Corridor: BD↔IN_E Type: ±400kV HVDC B2B + 765kV AC Confidence: High

## Existing_Generation
scenario | Country | Node | Plant_Name | Technology_Code | Technology_Name | Fuel | Capacity_MW | Commissioning_Year | Expected_Retirement_Year | Capacity_Factor_Annual | Status | Source
BAU | Bangladesh | BD | Ghorasal Repowered CCPP Unit-3 (GT) | PWRNGSBGDXX | Natural Gas CC | Gas | 260 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ghorasal Repowered CCPP Unit-4 | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ghorasal TPP Unit-5 | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ghorasal 365 MW CCPP Unit-7 | PWRNGSBGDXX | Natural Gas CC | Gas | 365 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ghorashal 108MW PP (Regent) | PWRNGSBGDXX | Natural Gas CC | Gas | 108 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Tongi 80 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 105 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Meghnaghat 450 MW CCPP (MPL) | PWRNGSBGDXX | Natural Gas CC | Gas | 450 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | 210 MW Siddhirgonj TPP | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Haripur 412 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 412 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Siddhirgonj 2x120 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Siddhirganj 335 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 335 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Meghnaghat 335MW CCPP (Summit) | PWRNGSBGDXX | Natural Gas CC | Gas | 335 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Madanganj-55 MW PP (Summit) | PWROILBGDXX | HFO Engine | HFO | 55 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Gagnagar 102 MW PP (Digital Power) | PWROILBGDXX | HFO Engine | HFO | 102 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Summit Power Ashulia | PWRNGSBGDXX | Natural Gas CC | Gas | 45 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Summit Power Madhabdi | PWRNGSBGDXX | Natural Gas CC | Gas | 35 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Gazipur 52 MW PP | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Gazipur 100 MW PP | PWROILBGDXX | HFO Engine | HFO | 105 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Kodda 150MW PP (BR-Power gen) | PWROILBGDXX | HFO Engine | HFO | 149 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Kamalaghat 54 MW PP (Banco Energy) | PWROILBGDXX | HFO Engine | HFO | 54 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Kodda 300 MW PP Unit-2 (Summit) | PWROILBGDXX | HFO Engine | HFO | 300 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Kodda 149 MW PP Unit-1 (Summit) | PWROILBGDXX | HFO Engine | HFO | 149 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Nababganj 55 MW PP (Southern Power) | PWROILBGDXX | HFO Engine | HFO | 55 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Manikganj 55 MW PP (Northern) | PWROILBGDXX | HFO Engine | HFO | 55 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Meghnaghat 104 MW PP (OPSL) | PWROILBGDXX | HFO Engine | HFO | 104 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Manikgonj 162MW PP (MPGL) | PWROILBGDXX | HFO Engine | HFO | 162 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Manikgonj 35MW Solar PP (Inspectra Solar) | PWRSPVBGDXX | Solar PV | Solar | 35 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Kanchan Purbachal Power Generation | PWROILBGDXX | HFO Engine | HFO | 55 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Unique Meghnaghat 584MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 584 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Meghnaghat 583 MW CCPP (Summit) | PWRNGSBGDXX | Natural Gas CC | Gas | 583 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Meghnaghat (Jera) 718MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 718 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sripur 150 MW (BR-Power gen) | PWROILBGDXX | HFO Engine | HFO | 150 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Karnaphuli Hydro PP Unit-1,2,3,4,5 | PWRHYDBGDXX | Hydro | Hydro | 230 | 2010 | 2060 | 0.45 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Chattogram TPP | PWRNGSBGDXX | Natural Gas CC | Gas | 420 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Kaptai 7 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 6 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Raozan 25 MW PP | PWROILBGDXX | HFO Engine | HFO | 25 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Teknaf 20MW PP (Solartech) | PWRSPVBGDXX | Solar PV | Solar | 20 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Patenga 50MW PP (Baraka) | PWROILBGDXX | HFO Engine | HFO | 50 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sikalbaha 105 MW PP (Baraka Sikalbaha) | PWROILBGDXX | HFO Engine | HFO | 105 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Shikalbaha Peaking GT | PWRNGSBGDXX | Natural Gas CC | Gas | 150 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sikalbaha 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 225 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Anwara 300 MW PP (United) | PWROILBGDXX | HFO Engine | HFO | 300 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Juldah 100 MW PP Unit-3 (Acorn) | PWROILBGDXX | HFO Engine | HFO | 100 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Dohazari-Kalaish 100 MW Peaking | PWROILBGDXX | HFO Engine | HFO | 102 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Hathazari 100 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 98 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Chattogram 108 MW PP (ECPV) | PWROILBGDXX | HFO Engine | HFO | 108 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sikalbaha 54 MW PP (Jodiac Power) | PWROILBGDXX | HFO Engine | HFO | 54 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Karnaphuli Power Ltd. | PWROILBGDXX | HFO Engine | HFO | 110 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Juldah Unit-2 (Acorn) | PWROILBGDXX | HFO Engine | HFO | 100 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Chattogram 116 MW PP (Anlima Energy) | PWROILBGDXX | HFO Engine | HFO | 116 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Mirsharai 150 MW (BR-Power gen) | PWROILBGDXX | HFO Engine | HFO | 163 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | SS Power 2x612MW Coal PP | PWRCOABGDXX | Coal Steam | Coal | 1224 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Matarbari 2x600 MW (CPGCL) | PWRCOABGDXX | Coal Steam | Coal | 1150 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Cox's Bazar Wind PP | PWRWONBGDXX | Wind | Wind | 60 | 2010 | 2035 | 0.25 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 50 MW PP | PWRNGSBGDXX | Natural Gas CC | Gas | 53 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 221 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 450 MW CCPP (South) | PWRNGSBGDXX | Natural Gas CC | Gas | 360 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 450 MW CCPP (North) | PWRNGSBGDXX | Natural Gas CC | Gas | 360 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 420 MW CCPP (East) | PWRNGSBGDXX | Natural Gas CC | Gas | 400 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 195MW PP (APSCL-United) | PWRNGSBGDXX | Natural Gas CC | Gas | 195 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 51 MW PP (Midland) | PWRNGSBGDXX | Natural Gas CC | Gas | 51 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 150MW PP (Midland) | PWROILBGDXX | HFO Engine | HFO | 150 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Titas 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Chandpur 150 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 163 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Chandpur 200MW (Desh Energy) | PWROILBGDXX | HFO Engine | HFO | 200 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Jangalia 52 MW PP (Lakdanavi) | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Cumilla 25 MW PP (Summit) | PWRNGSBGDXX | Natural Gas CC | Gas | 25 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Feni 114 MW (Lakdanavi) | PWROILBGDXX | HFO Engine | HFO | 114 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Chowmuhani 113 MW | PWROILBGDXX | HFO Engine | HFO | 113 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Chandpur 115MW PP (Doreen) | PWROILBGDXX | HFO Engine | HFO | 115 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Ashuganj 55 MW PP (Precision) | PWRNGSBGDXX | Natural Gas CC | Gas | 55 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sonagazi 75 MW Solar Plant (EGCB) | PWRSPVBGDXX | Solar PV | Solar | 75 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | RPCL 210MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Jamalpur 115 MW PP (United) | PWROILBGDXX | HFO Engine | HFO | 115 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Mymensingh 200 MW PP (United) | PWROILBGDXX | HFO Engine | HFO | 200 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sarishabari 3 MW Solar Plant | PWRSPVBGDXX | Solar PV | Solar | 3 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sutiakhali 50 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 50 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bhairob 54 MW PP | PWROILBGDXX | HFO Engine | HFO | 54 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Tangail 22 MW PP (PPGL) | PWROILBGDXX | HFO Engine | HFO | 22 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Fenchugonj CCPP Phase-1 | PWRNGSBGDXX | Natural Gas CC | Gas | 97 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Fenchugonj CCPP Phase-2 | PWRNGSBGDXX | Natural Gas CC | Gas | 104 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Kushiara 163 MW CCPP (KP) | PWRNGSBGDXX | Natural Gas CC | Gas | 163 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Shahjibazar GTPP Unit-8 & 9 | PWRNGSBGDXX | Natural Gas CC | Gas | 70 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Shajibazar 330 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 330 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sylhet 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 231 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sylhet 20 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 20 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Shahjahanulla 25 MW PP | PWRNGSBGDXX | Natural Gas CC | Gas | 25 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bibiana-II 341 MW CCPP (Summit) | PWRNGSBGDXX | Natural Gas CC | Gas | 341 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bibiyana-III 400 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 400 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bibiyana South 383 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 383 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Shahjibazar 100 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 100 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Shahjibazar 86MW PP (Shahjibazar) | PWRNGSBGDXX | Natural Gas CC | Gas | 86 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bheramara 410 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 410 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Faridpur 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 54 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Gopalganj 100 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 109 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Khulna 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | HSD/Gas | 230 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Rupsha 105 MW PP (Orion rupsha) | PWROILBGDXX | HFO Engine | HFO | 105 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Madhumati 100 MW PP | PWROILBGDXX | HFO Engine | HFO | 105 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Mongla Orion 100 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 100 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Maitree Super Thermal 1320 MW PP (BIFPCL) | PWRCOABGDXX | Coal Steam | Coal | 1234 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Khulna 330 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas/HSD | 336 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Barisal 110 MW PP (Summit) | PWROILBGDXX | HFO Engine | HFO | 110 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bhola 225 MW CCPP | PWRNGSBGDXX | Natural Gas CC | Gas | 194 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Payra 1320 MW TPP (BCPCL) | PWRCOABGDXX | Coal Steam | Coal | 1244 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Potuakhali 150MW PP (UPPL) | PWROILBGDXX | HFO Engine | HFO | 150 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Barisal Electric 307 MW Coal | PWRCOABGDXX | Coal Steam | Coal | 307 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Barisal 1 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 1 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bhola 220MW CCPP (Nutan Bidyut BD) | PWRNGSBGDXX | Natural Gas CC | Gas/HSD | 220 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Baghabari 71 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 71 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Baghabari 100 MW GTPP | PWRNGSBGDXX | Natural Gas CC | Gas | 100 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Baghabari 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bera 70 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 71 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Chapainawabganj 100 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 104 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Katakhali 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 50 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Santahar 50 MW Peaking PP | PWROILBGDXX | HFO Engine | HFO | 50 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sirajgonj 225MW CCPP Unit-1 | PWRNGSBGDXX | Natural Gas CC | Gas | 210 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sirajgonj 225MW CCPP Unit-2 | PWRNGSBGDXX | Natural Gas CC | Gas | 220 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sirajgonj 225MW CCPP Unit-3 | PWRNGSBGDXX | Natural Gas CC | Gas | 220 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sirajgonj 400 MW CCPP Unit-4 | PWRNGSBGDXX | Natural Gas CC | Gas | 414 | 2010 | 2045 | 0.55 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Natore 52 MW PP (Rajlanka) | PWROILBGDXX | HFO Engine | HFO | 52 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bagura 113 MW PP (Confidence) U-1 | PWROILBGDXX | HFO Engine | HFO | 113 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Bagura 113 MW PP (Confidence) U-2 | PWROILBGDXX | HFO Engine | HFO | 113 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sirajgonj 6.55 MW Solar | PWRSPVBGDXX | Solar PV | Solar | 6 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sirajganj 68 MW Solar Park | PWRSPVBGDXX | Solar PV | Solar | 68 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Pabna Solar 100 MW | PWRSPVBGDXX | Solar PV | Solar | 100 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sirajgonj 2 MW Wind Power Plant | PWRWONBGDXX | Wind | Wind | 2 | 2010 | 2035 | 0.25 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Pabna 64 MW Solar Plant | PWRSPVBGDXX | Solar PV | Solar | 65 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Barapukuria TPP Unit-1 & 2 | PWRCOABGDXX | Coal Steam | Coal | 250 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Barapukuria 275 MW TPP Unit-3 | PWRCOABGDXX | Coal Steam | Coal | 274 | 2010 | 2045 | 0.65 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Rangpur 20 MW GTPP | PWROILBGDXX | High Speed Diesel | HSD | 20 | 2010 | 2045 | 0.2 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Rangpur 113 MW PP (Confidence) | PWROILBGDXX | HFO Engine | HFO | 113 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Saidpur 20 MW GTPP | PWROILBGDXX | High Speed Diesel | HSD | 20 | 2010 | 2045 | 0.2 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Majipara Tatulia 8 MW Solar PP | PWRSPVBGDXX | Solar PV | Solar | 8 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Thakurgaon 115MW PP (Energypac) | PWROILBGDXX | HFO Engine | HFO | 115 | 2010 | 2045 | 0.3 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Lalmonirhat 30 MW Solar (Intraco) | PWRSPVBGDXX | Solar PV | Solar | 30 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Teesta Solar Limited 200 MW | PWRSPVBGDXX | Solar PV | Solar | 200 | 2010 | 2035 | 0.18 | Operational | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Saidpur 150 MW Simple Cycle PP | PWROILBGDXX | High Speed Diesel | HSD | 162 | 2010 | 2045 | 0.2 | Operational | Bangladesh_Power_Sector.xlsx
BAU | India | IN_E | Amrit Bio Energy & Industries Ltd West Bengal Bankura 10 | PWRBIOINDEA | Biomass Power | Bio Power | 10 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Harinagar Sugar Mills Ltd Bihar Pashchim Champaran 14.5 | PWRBIOINDEA | Biomass Power | Bio Power | 14.5 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Ispat Alloys Ltd West Bengal Bardhaman 10 | PWRBIOINDEA | Biomass Power | Bio Power | 10 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kamarhatty Power Ltd West Bengal Bardhaman 6 | PWRBIOINDEA | Biomass Power | Bio Power | 6 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | New Swadeshi Sugar Mill Ltd Bihar Pashchim Champaran 10 | PWRBIOINDEA | Biomass Power | Bio Power | 10 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] Bihar N.A. 88 | PWRBIOINDEA | Biomass Power | Bio Power | 88 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] Odisha N.A. 30 | PWRBIOINDEA | Biomass Power | Bio Power | 30.4 | Pre-2000 | Odisha | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] West Bengal N. | PWRBIOINDEA | Biomass Power | Bio Power | 274 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Bihar N.A. 26.4 | PWRBIOINDEA | Biomass Power | Bio Power | 26.4 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Jharkhand N.A. 20.14 | PWRBIOINDEA | Biomass Power | Bio Power | 20.14 | Pre-2000 | Jharkhand | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Odisha N.A. 8.82 | PWRBIOINDEA | Biomass Power | Bio Power | 8.82 | Pre-2000 | Odisha | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] West Bengal N.A. 43. | PWRBIOINDEA | Biomass Power | Bio Power | 43.52 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] Bihar N.A. 1.32 | PWRBIOINDEA | Biomass Power | Bio Power | 1.32 | Pre-2000 | Bihar | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] Odisha N.A. 5 | PWRBIOINDEA | Biomass Power | Bio Power | 5 | Pre-2000 | Odisha | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] West Bengal N.A. 8 | PWRBIOINDEA | Biomass Power | Bio Power | 8.34 | Pre-2000 | West Bengal | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Shalivahana Green Energy Ltd Odisha Dhenkanal 20 | PWRBIOINDEA | Biomass Power | Bio Power | 20 | Pre-2000 | Odisha | 0.5 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Bakreshwar TPS | PWRCOAINDEA | Coal Steam | Coal | 1050 | 1999-07-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Bandel TPS | PWRCOAINDEA | Coal Steam | Coal | 270 | 1965-05-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Barauni TPS | PWRCOAINDEA | Coal Steam | Coal | 500 | 2018-01-01 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Barh STPP | PWRCOAINDEA | Coal Steam | Coal | 3300 | 2013-11-30 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Bokaro A Extension TPS | PWRCOAINDEA | Coal Steam | Coal | 500 | 2016-03-22 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Budge Budge TPS | PWRCOAINDEA | Coal Steam | Coal | 750 | 1997-09-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Chandrapura (DVC) TPS | PWRCOAINDEA | Coal Steam | Coal | 500 | 2009-11-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Darlipali STPP | PWRCOAINDEA | Coal Steam | Coal | 1600 | 2019-12-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Derang TPP | PWRCOAINDEA | Coal Steam | Coal | 1200 | 2014-05-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Durgapur Projects (D.P.L.) TPS | PWRCOAINDEA | Coal Steam | Coal | 550 | 2007-11-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Durgapur Steel TPS | PWRCOAINDEA | Coal Steam | Coal | 1000 | 2011-07-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Farakka STPS | PWRCOAINDEA | Coal Steam | Coal | 2100 | 1986-01-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Haldia TPP | PWRCOAINDEA | Coal Steam | Coal | 600 | 2014-01-14 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Hiranmaye TPP | PWRCOAINDEA | Coal Steam | Coal | 300 | 2017-08-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | IB Valley TPS | PWRCOAINDEA | Coal Steam | Coal | 1740 | 1994-05-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Ind Barath (Utkal)/JSW Energy (Utkal) Ltd. | PWRCOAINDEA | Coal Steam | Coal | 700 | 2016-02-25 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Jojobera TPS | PWRCOAINDEA | Coal Steam | Coal | 240 | 2001-10-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kahalgaon STPS | PWRCOAINDEA | Coal Steam | Coal | 2340 | 1992-03-01 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kamalanga TPS | PWRCOAINDEA | Coal Steam | Coal | 1050 | 2013-03-29 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kodarma TPP | PWRCOAINDEA | Coal Steam | Coal | 1000 | 2011-07-20 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kolaghat TPS | PWRCOAINDEA | Coal Steam | Coal | 840 | 1984-10-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Maadurga Thermal Power (MTPCL) | PWRCOAINDEA | Coal Steam | Coal | 60 | 2024-09-23 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Mahadev Prasad or Jamshedpur Kandra STPP | PWRCOAINDEA | Coal Steam | Coal | 540 | 2012-11-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Maithon TPP | PWRCOAINDEA | Coal Steam | Coal | 1050 | 2011-09-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Mejia TPS | PWRCOAINDEA | Coal Steam | Coal | 2340 | 1995-12-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Muzaffarpur TPS | PWRCOAINDEA | Coal Steam | Coal | 390 | 2015-03-31 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Nabi Nagar TPP | PWRCOAINDEA | Coal Steam | Coal | 1000 | 2016-03-20 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | New NabiNagar TPP (Majhiyan) | PWRCOAINDEA | Coal Steam | Coal | 1980 | 2019-07-01 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | North Karanpura TPP | PWRCOAINDEA | Coal Steam | Coal | 1980 | 2023-01-18 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Patratu TPS | PWRCOAINDEA | Coal Steam | Coal | 800 | 2025-10-16 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Raghunathpur TPS | PWRCOAINDEA | Coal Steam | Coal | 1200 | 2014-08-24 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Sagardighi TPS | PWRCOAINDEA | Coal Steam | Coal | 1600 | 2007-09-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Santaldih TPS | PWRCOAINDEA | Coal Steam | Coal | 500 | 2007-11-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Southern Generating Power Station (Southern Repl. TPS) | PWRCOAINDEA | Coal Steam | Coal | 135 | 1990-04-01 | West Bengal | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Sterlite (Jharsuguda)/ Vedanta Thermal Power Plant | PWRCOAINDEA | Coal Steam | Coal | 600 | 2010-10-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Super Critical Buxar Thermal Power Plant | PWRCOAINDEA | Coal Steam | Coal | 660 | 2025-11-05 | Bihar | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Talcher or Kaniha Talcher STPS | PWRCOAINDEA | Coal Steam | Coal | 3000 | 1995-02-01 | Odisha | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Tenughat TPS | PWRCOAINDEA | Coal Steam | Coal | 420 | 1994-04-01 | Jharkhand | 0.65 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Balimela Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 510 | 1973-08-14 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Chuzachen Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 110 | 2013-04-20 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Dikchu Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 96 | 2017-04-11 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Hirakud (Burla & Chiplima) Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 359.8 | 1956-12-18 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Jaldhaka I Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 36 | 1967-08-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Jorethang Loop Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 96 | 2015-09-22 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Machkund Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 114.75 | 1955-08-19 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Maithon Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 63.2 | 1957-10-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Panchet Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 80 | 1959-06-12 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Purulia Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 900 | 2007-12-17 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rammam II Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 50 | 1995-08-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rangit Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 60 | 2000-02-03 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rengali Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 250 | 1985-08-27 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rongnichu Hydro Power Project | PWRHYDINDEA | Hydro | Hydro | 113 | 2021-06-01 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Subernarekha I & II Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 130 | 1977-05-30 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Tashiding Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 97 | 2018-11-06 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Teesta III Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 1200 | 2017-01-14 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Teesta Low Dam III Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 132 | 2013-01-20 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Teesta Low Dam IV Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 160 | 2016-02-14 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Teesta V Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 510 | 2008-02-06 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Upper Indravati Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 600 | 1999-09-19 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Upper Kolab Hydroelectric Power Project | PWRHYDINDEA | Hydro | Hydro | 320 | 1988-03-15 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Amethi Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.5 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Angoor Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Arwal Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.5 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | BSHPC Small Hydro Project 1 | PWRHYDINDEA | Hydro | Small Hydro | 2 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | BSHPC Small Hydro Project 2 | PWRHYDINDEA | Hydro | Small Hydro | 3.3 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Baitarini Power Hydel Project | PWRHYDINDEA | Hydro | Small Hydro | 24 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Barun Small Hydel Power Station | PWRHYDINDEA | Hydro | Small Hydro | 3.3 | 1996-12-01 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Belsar Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Dehri Small Hydel Power Station | PWRHYDINDEA | Hydro | Small Hydro | 6.6 | 1995-12-01 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Dhelabagh Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Fazi Hydel Project | PWRHYDINDEA | Hydro | Small Hydro | 1.2 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Goutamghagh Mini Hydel Scheme | PWRHYDINDEA | Hydro | Small Hydro | 0.01 | 1999-01-07 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Jaldhaka Small Hydro Project II | PWRHYDINDEA | Hydro | Small Hydro | 8 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Jalimghagh Mini Hydel Scheme | PWRHYDINDEA | Hydro | Small Hydro | 0.02 | 1997-03-14 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kakatiya Hydroelectric Project | PWRHYDINDEA | Hydro | Small Hydro | 9 | 2022-04-30 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kataiya Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kosi Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 20 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Little Rangit Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 2 | 1970-01-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Lower Kolab Small Hydro Electric Project | PWRHYDINDEA | Hydro | Small Hydro | 12 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Massanjore Hydel Project | PWRHYDINDEA | Hydro | Small Hydro | 4 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Middle Kolab Small Hydro Electric Project | PWRHYDINDEA | Hydro | Small Hydro | 25 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Mungopoo-Kalikhola Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | 2003-12-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Nasriganj Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Neora Hydro Limited Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | 2006-04-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Nindighagh Mini Hydel Scheme | PWRHYDINDEA | Hydro | Small Hydro | 0.02 | 1997-03-14 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Nippon Power Limited Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | 2007-03-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Paharma Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Potteru Hydro Electric Project Phase I | PWRHYDINDEA | Hydro | Small Hydro | 6 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rajpur Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.7 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rampur Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.25 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Richington Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 2 | 1979-12-01 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 1 | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 10 | PWRHYDINDEA | Hydro | Small Hydro | 8 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 2 | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 3 | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 4 | PWRHYDINDEA | Hydro | Small Hydro | 2 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 5 | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 6 | PWRHYDINDEA | Hydro | Small Hydro | 2 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 7 | PWRHYDINDEA | Hydro | Small Hydro | 12 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 8 | PWRHYDINDEA | Hydro | Small Hydro | 4 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPDCL Small Hydro Project 9 | PWRHYDINDEA | Hydro | Small Hydro | 2.5 | Pre-2000 | Sikkim | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Samal Hydro Electric Project | PWRHYDINDEA | Hydro | Small Hydro | 20 | 2009-10-11 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Sapthadharo Small Hydroelectric Project | PWRHYDINDEA | Hydro | Small Hydro | 18 | Pre-2000 | Odisha | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Sebari Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Shrikhinda Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.7 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Sidrapong Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 0.6 | 1897-10-11 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Teesta Falls Small Hydro Project Phase 1 | PWRHYDINDEA | Hydro | Small Hydro | 22.5 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Teesta Falls Small Hydro Project Phase 2 | PWRHYDINDEA | Hydro | Small Hydro | 22.5 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Teesta Falls Small Hydro Project Phase 3 | PWRHYDINDEA | Hydro | Small Hydro | 22.5 | Pre-2000 | West Bengal | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Tejpura Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 1.5 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Titaiya Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 4 | 1953-02-01 | Jharkhand | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Triveni Link Canal Small Hydro Project | PWRHYDINDEA | Hydro | Small Hydro | 3 | Pre-2000 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Valmikinagar Hydroelectric Power Station | PWRHYDINDEA | Hydro | Small Hydro | 15 | 1993-12-01 | Bihar | 0.45 | Operational | India_Electricity_Infrastructure.xlsx

## Planned_Generation
scenario | Country | Node | Project_Name | Technology_Code | Technology_Name | Fuel | Capacity_MW | Expected_COD | Status | Developer | Source
BAU | Bangladesh | BD | Rooppur Nuclear Power Plant Unit-1 | PWRURNBGDXX | Nuclear Power Plant | Nuclear | 1200 | 2024 | Under Construction / Test | NPCBL / Rosatom (Russia) | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Rooppur Nuclear Power Plant Unit-2 | PWRURNBGDXX | Nuclear Power Plant | Nuclear | 1200 | 2025 | Under Construction | NPCBL / Rosatom (Russia) | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Patuakhali 1320 MW Coal PP (RNPL) | PWRCOABGDXX | Coal Power Plant | Coal | 1320 | 2025 | Test Run | RPCL | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Rupsha 800 MW CCPP | PWRNGSBGDXX | Natural Gas CC/OC | Gas/HSD | 800 | 2025 | Test Run | NWPGCL | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Sonagazi 75 MW Solar Plant (EGCB) | PWRSPVBGDXX | Solar PV | Solar | 75 | 2025 | Test Run / Commissioning | EGCB | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Moulvibazar 10 MW Solar Power Plant | PWRSPVBGDXX | Solar PV | Solar | 10 | 2025 | Under Development | IPP | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Additional LNG-based Gas Power (Multiple) | PWRNGSBGDXX | Natural Gas CC/OC | Gas/LNG | 5000 | 2025 | Committed Pipeline | Various IPP/PDB | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Large-scale Solar Expansion | PWRSPVBGDXX | Solar PV | Solar | 3000 | 2025 | Planning/Committed | Various IPP | Bangladesh_Power_Sector.xlsx
BAU | Bangladesh | BD | Offshore Wind (Pilot) | PWRWONBGDXX | Wind Power | Wind | 200 | 2035 | Pre-Feasibility | TBD | Bangladesh_Power_Sector.xlsx
BAU | India | IN_E | Hiranmaye TPP | PWRCOAINDEA | Coal Power Plant | Coal | 150 | 2035 | Pipeline | Hiranmaye Energy Ltd. | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kandarei TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1050 | 2035 | Pipeline | KVK Nilanchal Ltd. | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Kodarma TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1600 | 2028 | Pipeline | Damodar Valley Corporation(DVC) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Lanco Babandh TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1320 | 2035 | Pipeline | LBP Ltd. | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Malibrahmani Power Station | PWRCOAINDEA | Coal Power Plant | Coal | 1050 | 2013 | Pipeline | Jindal Power Ltd. (JPL) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Matrishri Usha Jayaswal TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1080 | 2035 | Pipeline | Corporate Power Ltd. | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | New NabiNagar TPP (Majhiyan) | PWRCOAINDEA | Coal Power Plant | Coal | 2400 | 2029 | Pipeline | NTPC Ltd. & BSPGCL (NPGCL) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Patratu TPS | PWRCOAINDEA | Coal Power Plant | Coal | 1600 | 2026 | Pipeline | Patratu Vidyut Utpadan Nigam Limited | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Raghunathpur TPS | PWRCOAINDEA | Coal Power Plant | Coal | 1320 | 2028 | Pipeline | Damodar Valley Corporation(DVC) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Sagardighi TPS | PWRCOAINDEA | Coal Power Plant | Coal | 660 | 2025 | Pipeline | West Bengal Power Development Corp. Ltd. | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Siriya TPS or Banka Power Project | PWRCOAINDEA | Coal Power Plant | Coal | 2640 | 2035 | Pipeline | Jas Infrastructure and Power | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Super Critical Buxar Thermal Power Plant | PWRCOAINDEA | Coal Power Plant | Coal | 660 | 2026 | Pipeline | Satlaj Jal Vidhut Nigam Limited (SJVN Ltd) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Talabira TPP | PWRCOAINDEA | Coal Power Plant | Coal | 2400 | 2030 | Pipeline | NLC India Limited (formerly Neyveli Lignite Corp. Ltd.) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Talcher or Kaniha Talcher STPS | PWRCOAINDEA | Coal Power Plant | Coal | 1320 | 2027 | Pipeline | NTPC Ltd. | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Tori TPP | PWRCOAINDEA | Coal Power Plant | Coal | 1800 | 2035 | Pipeline | Essar Power Ltd. | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Bhasmey Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 51 | 2035 | Pipeline | Gati Infrastructure Pvt. Limited (GIPL) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Panan Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 300 | 2035 | Pipeline | Himgiri Hydro Energy Private Limited | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rammam III Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 120 | 2029 | Pipeline | National Thermal Power Corporation Limited (NTPC) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rangit-II Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 66 | 2025 | Pipeline | Sikkim Hydro Power Limited | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Rangit-IV Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 120 | 2026 | Pipeline | Jal Power Corporation Limited | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Teesta- VI Hydro Power Project | PWRHYDINDEA | Hydropower | Hydro | 500 | 2027 | Pipeline | National Hydroelectric Power Corporation (NHPC) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | Damodar Valley Corporation (DVC) Jharkhand 10.0 | PWRSPVINDEA | Solar PV | Solar | 10 | 2026 | Pipeline | Damodar Valley Corporation (DVC) | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | GVREL Jharkhand 155.0 | PWRSPVINDEA | Solar PV | Solar | 155 | 2025 | Pipeline | GVREL | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | GVREL Jharkhand 80.0 | PWRSPVINDEA | Solar PV | Solar | 80 | 2025 | Pipeline | GVREL | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | GVREL West Bengal 75.0 | PWRSPVINDEA | Solar PV | Solar | 75 | 2025 | Pipeline | GVREL | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | NHPC Limited Odisha 40.0 | PWRSPVINDEA | Solar PV | Solar | 40 | 2025 | Pipeline | NHPC Limited | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SECI Jharkhand 100.0 | PWRSPVINDEA | Solar PV | Solar | 100 | 2027 | Pipeline | SECI | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SJVN GREEN ENERGY LIMITED Bihar 75.0 | PWRSPVINDEA | Solar PV | Solar | 75 | 2023 | Pipeline | SJVN GREEN ENERGY LIMITED | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPD Jharkhand 8.0 | PWRSPVINDEA | Solar PV | Solar | 8 | 2025 | Pipeline | SPD | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPD West Bengal 10.0 | PWRSPVINDEA | Solar PV | Solar | 10 | 2024 | Pipeline | SPD | India_Electricity_Infrastructure.xlsx
BAU | India | IN_E | SPD West Bengal 14.0 | PWRSPVINDEA | Solar PV | Solar | 14 | 2024 | Pipeline | SPD | India_Electricity_Infrastructure.xlsx

## Technology_Costs
scenario | Technology_Code | Technology_Name | Parameter | Unit | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Source | Notes
BAU | PWRSPV | Solar PV (utility-scale) | CAPEX | USD/kW | 560 | 536 | 474 | 413 | 379 | 345 | 311 | IN(base)=$560/kW ¦ BD=$840(×1.5) ¦ LK=$849(×1.5) ¦ NP=$896(×1.6) ¦ BT=$1008(×1.8) ¦ MV=$1680(×3.0) Anchor refs: IRENA 2024; ADB PADs; CEB LTGEP BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRSPV | Solar PV (utility-scale) | Fixed O&M | USD/kW/yr | 8 | 8 | 7 | 6 | 6 | 5 | 5 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRSPV | Solar PV (utility-scale) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRSPV | Solar PV (utility-scale) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRSPV | Solar PV (utility-scale) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRSPV | Solar PV (utility-scale) | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRSPR | Solar PV (rooftop/distributed) | CAPEX | USD/kW | 850 | 813 | 720 | 627 | 576 | 524 | 472 | IN(base)=$850/kW ¦ BD=$1275(×1.5) ¦ LK=$982(×1.2) ¦ NP=$1360(×1.6) ¦ BT=$1530(×1.8) ¦ MV=$2550(×3.0) Anchor refs: CERC; CEB LTGEP BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
BAU | PWRSPR | Solar PV (rooftop/distributed) | Fixed O&M | USD/kW/yr | 9 | 9 | 8 | 7 | 7 | 6 | 6 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
BAU | PWRSPR | Solar PV (rooftop/distributed) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
BAU | PWRSPR | Solar PV (rooftop/distributed) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRSPR | Solar PV (rooftop/distributed) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRSPR | Solar PV (rooftop/distributed) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
BAU | PWRCSP | Concentrated Solar Power | CAPEX | USD/kW | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
BAU | PWRCSP | Concentrated Solar Power | Fixed O&M | USD/kW/yr | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
BAU | PWRCSP | Concentrated Solar Power | Variable O&M | USD/MWh | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
BAU | PWRCSP | Concentrated Solar Power | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRCSP | Concentrated Solar Power | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRCSP | Concentrated Solar Power | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
BAU | PWRWON | Onshore Wind | CAPEX | USD/kW | 761 | 687 | 663 | 640 | 617 | 594 | 570 | IN(base)=$761/kW ¦ BD=$1218(×1.6) ¦ LK=$1391(×1.8) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP BD ×1.5-2.0: Limited BD wind experience [⚠ NO URL] LK ×1.5-2.3: ADB Mannar $2,481/kW (incl. harbor) (https://www.adb.org/results/helping-sri-lanka-go-green) | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRWON | Onshore Wind | Fixed O&M | USD/kW/yr | 22 | 22 | 21 | 20 | 20 | 19 | 19 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRWON | Onshore Wind | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRWON | Onshore Wind | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRWON | Onshore Wind | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRWON | Onshore Wind | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRWOF | Offshore Wind | CAPEX | USD/kW | 3800 | 3768 | 3442 | 2014 | 1960 | 1919 | 1886 | IN(base)=$2339/kW ¦ BD=N/A ¦ LK=$3781(×1.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
BAU | PWRWOF | Offshore Wind | Fixed O&M | USD/kW/yr | 114 | 114 | 105 | 97 | 90 | 84 | 80 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
BAU | PWRWOF | Offshore Wind | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
BAU | PWRWOF | Offshore Wind | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRWOF | Offshore Wind | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRWOF | Offshore Wind | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
BAU | PWRHDR | Hydro – Reservoir | CAPEX | USD/kW | 2500 | 2550 | 2625 | 2700 | 2775 | 2850 | 2925 | IN(base)=$1500/kW ¦ BD=N/A ¦ LK=$2500(×1.7) ¦ NP=$2761(×1.8) ¦ BT=$1200(×0.8) ¦ MV=N/A Anchor refs: CEA; Nepal NEA; Bhutan PSMP LK ×~1.5: No specific LK data [⚠ NO URL] NP ×2.0-3.0: Tanahu $3,607/kW; Upper Trishuli $2,997/kW (https://www.adb.org) BT ×0.9-1.3: Mangdechhu $938/kW; Tala $1,176/kW | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
BAU | PWRHDR | Hydro – Reservoir | Fixed O&M | USD/kW/yr | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
BAU | PWRHDR | Hydro – Reservoir | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
BAU | PWRHDR | Hydro – Reservoir | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRHDR | Hydro – Reservoir | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRHDR | Hydro – Reservoir | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
BAU | PWRHRO | Hydro – Run-of-River | CAPEX | USD/kW | 1750 | 1785 | 1873 | 1960 | 2048 | 2135 | 2223 | IN(base)=$1300/kW ¦ BD=N/A ¦ LK=$1840(×1.4) ¦ NP=$1600(×1.2) ¦ BT=$1100(×0.85) ¦ MV=N/A Anchor refs: CEA; CEB LTGEP; PSMP; Nepal NEA LK ×~1.3: CEB LTGEP mini-hydro $1,840/kW (https://www.ceb.lk) NP ×1.3-1.7: NEA/industry ~$2,000/kW avg (https://www.adb.org/sites/default/files/publication/612641/hydropower-development-economic-growth-nepal.pdf) BT ×0.8-1.1: PSMP $785-1,339/kW; Nikachhu $1,220/kW (https://sasec.asia) | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
BAU | PWRHRO | Hydro – Run-of-River | Fixed O&M | USD/kW/yr | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
BAU | PWRHRO | Hydro – Run-of-River | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
BAU | PWRHRO | Hydro – Run-of-River | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRHRO | Hydro – Run-of-River | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRHRO | Hydro – Run-of-River | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
BAU | PWRHPS | Hydro – Pumped Storage | CAPEX | USD/kW | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | IN(base)=$635/kW ¦ BD=N/A ¦ LK=N/A ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP (India only) LK ×~1.5: No specific LK data [⚠ NO URL] NP ×2.0-3.0: Tanahu $3,607/kW; Upper Trishuli $2,997/kW (https://www.adb.org) BT ×0.9-1.3: Mangdechhu $938/kW; Tala $1,176/kW | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
BAU | PWRHPS | Hydro – Pumped Storage | Fixed O&M | USD/kW/yr | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
BAU | PWRHPS | Hydro – Pumped Storage | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
BAU | PWRHPS | Hydro – Pumped Storage | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRHPS | Hydro – Pumped Storage | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRHPS | Hydro – Pumped Storage | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
BAU | PWRCOASCPC | Coal – Supercritical | CAPEX | USD/kW | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | IN(base)=$1059/kW ¦ BD=$1694(×1.6) ¦ LK=$2132(×2.0) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP BD ×~1.6: Payra/Rampal cost reporting LK ×~2.0: CEB LTGEP $2,132/kW (https://www.ceb.lk) | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
BAU | PWRCOASCPC | Coal – Supercritical | Fixed O&M | USD/kW/yr | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
BAU | PWRCOASCPC | Coal – Supercritical | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
BAU | PWRCOASCPC | Coal – Supercritical | Heat Rate | GJ/MWh | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
BAU | PWRCOASCPC | Coal – Supercritical | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Coal' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
BAU | PWRCOASCPC | Coal – Supercritical | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
BAU | PWRCOAUSC | Coal – Ultra-supercritical | CAPEX | USD/kW | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | BD ×~1.6: Payra/Rampal cost reporting LK ×~2.0: CEB LTGEP $2,132/kW (https://www.ceb.lk) | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
BAU | PWRCOAUSC | Coal – Ultra-supercritical | Fixed O&M | USD/kW/yr | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
BAU | PWRCOAUSC | Coal – Ultra-supercritical | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
BAU | PWRCOAUSC | Coal – Ultra-supercritical | Heat Rate | GJ/MWh | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
BAU | PWRCOAUSC | Coal – Ultra-supercritical | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Coal' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
BAU | PWRCOAUSC | Coal – Ultra-supercritical | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
BAU | PWRCCG | Combined Cycle Gas Turbine | CAPEX | USD/kW | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | IN(base)=$700/kW ¦ BD=$770(×1.1) ¦ LK=$1300(×1.9) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA; IEPMP; CEB LTGEP BD ×~1.1: IEPMP ~$770/kW LK ×~1.9: CEB LTGEP $1,273-1,507/kW (https://www.ceb.lk) | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWRCCG | Combined Cycle Gas Turbine | Fixed O&M | USD/kW/yr | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWRCCG | Combined Cycle Gas Turbine | Variable O&M | USD/MWh | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWRCCG | Combined Cycle Gas Turbine | Heat Rate | GJ/MWh | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWRCCG | Combined Cycle Gas Turbine | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Natural gas' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
BAU | PWRCCG | Combined Cycle Gas Turbine | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWROCG | Open Cycle Gas Turbine | CAPEX | USD/kW | 360 | 360 | 360 | 360 | 360 | 360 | 360 | IN(base)=$450/kW ¦ BD=$495(×1.1) ¦ LK=$360(×0.8) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA; CEB LTGEP BD ×~1.1: IEPMP ~$770/kW LK ×~1.9: CEB LTGEP $1,273-1,507/kW (https://www.ceb.lk) | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWROCG | Open Cycle Gas Turbine | Fixed O&M | USD/kW/yr | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWROCG | Open Cycle Gas Turbine | Variable O&M | USD/MWh | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWROCG | Open Cycle Gas Turbine | Heat Rate | GJ/MWh | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWROCG | Open Cycle Gas Turbine | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Natural gas' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
BAU | PWROCG | Open Cycle Gas Turbine | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
BAU | PWROIL | Oil/Diesel generation | CAPEX | USD/kW | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | IN(base)=$700/kW ¦ BD=$770(×1.1) ¦ LK=$1000(×1.4) ¦ NP=N/A ¦ BT=N/A ¦ MV=$700(×1.0) Anchor refs: CEB LTGEP; ADB Maldives BD ×~1.1: BPDB IPP costs LK ×~1.4: CEB LTGEP $1,000-1,124/kW (https://www.ceb.lk) NP ×~1.5: Landlocked transport premium BT ×~1.5: Landlocked transport premium MV ×~1.0: Core competency (STELCO/FENAKA) (https://www.environment.gov.mv) | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
BAU | PWROIL | Oil/Diesel generation | Fixed O&M | USD/kW/yr | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
BAU | PWROIL | Oil/Diesel generation | Variable O&M | USD/MWh | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
BAU | PWROIL | Oil/Diesel generation | Heat Rate | GJ/MWh | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
BAU | PWROIL | Oil/Diesel generation | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Crude oil (Brent)' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
BAU | PWROIL | Oil/Diesel generation | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
BAU | PWRBIO | Biomass/Bagasse | CAPEX | USD/kW | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | IN(base)=$1142/kW ¦ BD=N/A ¦ LK=$1782(×1.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRBIO | Biomass/Bagasse | Fixed O&M | USD/kW/yr | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRBIO | Biomass/Bagasse | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRBIO | Biomass/Bagasse | Heat Rate | GJ/MWh | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRBIO | Biomass/Bagasse | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Biomass residue' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
BAU | PWRBIO | Biomass/Bagasse | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRWTE | Waste-to-Energy | CAPEX | USD/kW | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | BD ×~1.1: BPDB IPP costs LK ×~1.4: CEB LTGEP $1,000-1,124/kW (https://www.ceb.lk) NP ×~1.5: Landlocked transport premium BT ×~1.5: Landlocked transport premium MV ×~1.0: Core competency (STELCO/FENAKA) (https://www.environment.gov.mv) | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
BAU | PWRWTE | Waste-to-Energy | Fixed O&M | USD/kW/yr | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
BAU | PWRWTE | Waste-to-Energy | Variable O&M | USD/MWh | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
BAU | PWRWTE | Waste-to-Energy | Heat Rate | GJ/MWh | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
BAU | PWRWTE | Waste-to-Energy | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Waste' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
BAU | PWRWTE | Waste-to-Energy | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
BAU | PWRURN | Nuclear | CAPEX | USD/kW | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | IN(base)=$2000/kW ¦ BD=$5200(×2.6) ¦ LK=$5103(×2.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: India PHWR; BD Rooppur; CEB LTGEP | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
BAU | PWRURN | Nuclear | Fixed O&M | USD/kW/yr | 134 | 134 | 134 | 134 | 134 | 134 | 134 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
BAU | PWRURN | Nuclear | Variable O&M | USD/MWh | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
BAU | PWRURN | Nuclear | Heat Rate | GJ/MWh | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
BAU | PWRURN | Nuclear | Fuel Cost | USD/GJ | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
BAU | PWRURN | Nuclear | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
BAU | PWRGEO | Geothermal | CAPEX | USD/kW | 4589 | 4544 | 4434 | 4327 | 4222 | 4120 | 4020 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRGEO | Geothermal | Fixed O&M | USD/kW/yr | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRGEO | Geothermal | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRGEO | Geothermal | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRGEO | Geothermal | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRGEO | Geothermal | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRSDS | Short-duration storage (Li-ion 4h) | CAPEX | USD/kW | [7 empty] | IN(base)=$882/kW ¦ BD=$1058(×1.2) ¦ LK=$1330(×1.5) ¦ NP=$1147(×1.3) ¦ BT=$1235(×1.4) ¦ MV=$1323(×1.5) Anchor refs: CEA NEP; CEB LTGEP; ADB BD ×~1.2: Limited BD data [⚠ NO URL] LK ×~1.5: CEB LTGEP ~$1,330/kW (https://www.ceb.lk) NP ×~1.3: No specific data [⚠ NO URL] BT ×~1.4: No specific data [⚠ NO URL] MV ×~1.5: Island logistics premium | ⚠ NO SOURCE
BAU | PWRSDS | Short-duration storage (Li-ion 4h) | Fixed O&M | USD/kW/yr | 20 | 21 | 17 | 17 | 16 | 16 | 15 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRSDS | Short-duration storage (Li-ion 4h) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRSDS | Short-duration storage (Li-ion 4h) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRSDS | Short-duration storage (Li-ion 4h) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRSDS | Short-duration storage (Li-ion 4h) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
BAU | PWRLDS | Long-duration storage (8h+) | CAPEX | USD/kW | [7 empty] | BD ×~1.2: Limited BD data [⚠ NO URL] LK ×~1.5: CEB LTGEP ~$1,330/kW (https://www.ceb.lk) NP ×~1.3: No specific data [⚠ NO URL] BT ×~1.4: No specific data [⚠ NO URL] MV ×~1.5: Island logistics premium | ⚠ NO SOURCE
BAU | PWRLDS | Long-duration storage (8h+) | Fixed O&M | USD/kW/yr | 45 | 47 | 38 | 37 | 35 | 34 | 33 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
BAU | PWRLDS | Long-duration storage (8h+) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
BAU | PWRLDS | Long-duration storage (8h+) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRLDS | Long-duration storage (8h+) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRLDS | Long-duration storage (8h+) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
BAU | PWRFPV | Floating Solar PV | CAPEX | USD/kW | 1244 | 1190 | 1054 | 918 | 842 | 767 | 691 | BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRFPV | Floating Solar PV | Fixed O&M | USD/kW/yr | 19 | 18 | 17 | 16 | 15 | 14 | 13 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRFPV | Floating Solar PV | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRFPV | Floating Solar PV | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRFPV | Floating Solar PV | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRFPV | Floating Solar PV | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
BAU | PWRH2G | Green Hydrogen Fuel Cell | CAPEX | USD/kW | 2200 | 2100 | 1800 | 1500 | 1300 | 1100 | 1000 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRH2G | Green Hydrogen Fuel Cell | Fixed O&M | USD/kW/yr | 66 | 63 | 54 | 45 | 39 | 33 | 30 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRH2G | Green Hydrogen Fuel Cell | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRH2G | Green Hydrogen Fuel Cell | Heat Rate | GJ/MWh | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 |  | N/A — renewable/non-combustion technology
BAU | PWRH2G | Green Hydrogen Fuel Cell | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRH2G | Green Hydrogen Fuel Cell | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRTDL | Tidal / Marine | CAPEX | USD/kW | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRTDL | Tidal / Marine | Fixed O&M | USD/kW/yr | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRTDL | Tidal / Marine | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRTDL | Tidal / Marine | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRTDL | Tidal / Marine | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRTDL | Tidal / Marine | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
BAU | PWRBCK | Backstop (penalty generator) | CAPEX | USD/kW | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
BAU | PWRBCK | Backstop (penalty generator) | Fixed O&M | USD/kW/yr | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
BAU | PWRBCK | Backstop (penalty generator) | Variable O&M | USD/MWh | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
BAU | PWRBCK | Backstop (penalty generator) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRBCK | Backstop (penalty generator) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
BAU | PWRBCK | Backstop (penalty generator) | Construction Time | years | [8 empty] | N/A — backstop/penalty generator
Note on F2: Source: CEA NEP Annexure-A (4.64 Cr/MW) Node default: IN
Note on F3: Source: CEA NEP Annexure-A (4.64 Cr/MW) Node default: IN
Note on F4: Source: CEA NEP Annexure-A (4.64 Cr/MW) Node default: IN
Note on F5: ⚠ MISSING: No cost data for PWRSPV / Heat Rate. Check CostDB or ATB fallback.
Note on F6: ⚠ MISSING: No cost data for PWRSPV / Fuel Cost. Check CostDB or ATB fallback.
Note on F7: Source: CEA NEP Annexure-A (4.64 Cr/MW) Node default: IN
Note on F8: Source: CERC/MNRE benchmarks; SL LTGEP $982/kW Node default: IN
Note on F9: Source: CERC/MNRE benchmarks; SL LTGEP $982/kW Node default: IN
Note on F10: Source: CERC/MNRE benchmarks; SL LTGEP $982/kW Node default: IN
Note on F11: ⚠ MISSING: No cost data for PWRSPR / Heat Rate. Check CostDB or ATB fallback.
Note on F12: ⚠ MISSING: No cost data for PWRSPR / Fuel Cost. Check CostDB or ATB fallback.
Note on F13: Source: CERC/MNRE benchmarks; SL LTGEP $982/kW Node default: IN
Note on F14: Source: NREL ATB 2024 (no SA-specific data) Node default: ATB
Note on F15: Source: NREL ATB 2024 (no SA-specific data) Node default: ATB
Note on F16: Source: NREL ATB 2024 (no SA-specific data) Node default: ATB
Note on F17: ⚠ MISSING: No cost data for PWRCSP / Heat Rate. Check CostDB or ATB fallback.
Note on F18: ⚠ MISSING: No cost data for PWRCSP / Fuel Cost. Check CostDB or ATB fallback.
Note on F19: Source: NREL ATB 2024 (no SA-specific data) Node default: ATB
Note on F20: Source: CEA NEP Annexure-A (6.32 Cr/MW) Node default: IN
Note on F21: Source: CEA NEP Annexure-A (6.32 Cr/MW) Node default: IN
Note on F22: Source: CEA NEP Annexure-A (6.32 Cr/MW) Node default: IN
Note on F23: ⚠ MISSING: No cost data for PWRWON / Heat Rate. Check CostDB or ATB fallback.
Note on F24: ⚠ MISSING: No cost data for PWRWON / Fuel Cost. Check CostDB or ATB fallback.
Note on F25: Source: CEA NEP Annexure-A (6.32 Cr/MW) Node default: IN
Note on F26: Source: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) Node default: LK
Note on F27: Source: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) Node default: LK
Note on F28: Source: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) Node default: LK
Note on F29: ⚠ MISSING: No cost data for PWRWOF / Heat Rate. Check CostDB or ATB fallback.
Note on F30: ⚠ MISSING: No cost data for PWRWOF / Fuel Cost. Check CostDB or ATB fallback.
Note on F31: Source: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) Node default: LK
Note on F32: Source: Bhutan PSMP 2040; Nepal NEA; IRENA Node default: Regional
Note on F33: Source: Bhutan PSMP 2040; Nepal NEA; IRENA Node default: Regional
Note on F34: Source: Bhutan PSMP 2040; Nepal NEA; IRENA Node default: Regional
Note on F35: ⚠ MISSING: No cost data for PWRHDR / Heat Rate. Check CostDB or ATB fallback.
Note on F36: ⚠ MISSING: No cost data for PWRHDR / Fuel Cost. Check CostDB or ATB fallback.
Note on F37: Source: Bhutan PSMP 2040; Nepal NEA; IRENA Node default: Regional
Note on F38: Source: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW Node default: Regional
Note on F39: Source: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW Node default: Regional
Note on F40: Source: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW Node default: Regional
Note on F41: ⚠ MISSING: No cost data for PWRHRO / Heat Rate. Check CostDB or ATB fallback.
Note on F42: ⚠ MISSING: No cost data for PWRHRO / Fuel Cost. Check CostDB or ATB fallback.
Note on F43: Source: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW Node default: Regional
Note on F44: Source: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW Node default: IN
Note on F45: Source: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW Node default: IN
Note on F46: Source: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW Node default: IN
Note on F47: ⚠ MISSING: No cost data for PWRHPS / Heat Rate. Check CostDB or ATB fallback.
Note on F48: ⚠ MISSING: No cost data for PWRHPS / Fuel Cost. Check CostDB or ATB fallback.
Note on F49: Source: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW Node default: IN
Note on F50: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on F51: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on F52: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on F53: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on F54: ⚠ MISSING: No cost data for PWRCOASCPC / Fuel Cost. Check CostDB or ATB fallback.
Note on F55: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on F56: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on F57: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on F58: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on F59: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on F60: ⚠ MISSING: No cost data for PWRCOAUSC / Fuel Cost. Check CostDB or ATB fallback.
Note on F61: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on F62: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on F63: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on F64: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on F65: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on F66: ⚠ MISSING: No cost data for PWRCCG / Fuel Cost. Check CostDB or ATB fallback.
Note on F67: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on F68: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on F69: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on F70: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on F71: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on F72: ⚠ MISSING: No cost data for PWROCG / Fuel Cost. Check CostDB or ATB fallback.
Note on F73: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on F74: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on F75: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on F76: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on F77: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on F78: ⚠ MISSING: No cost data for PWROIL / Fuel Cost. Check CostDB or ATB fallback.
Note on F79: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on F80: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on F81: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on F82: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on F83: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on F84: ⚠ MISSING: No cost data for PWRBIO / Fuel Cost. Check CostDB or ATB fallback.
Note on F85: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on F86: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on F87: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on F88: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on F89: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on F90: ⚠ MISSING: No cost data for PWRWTE / Fuel Cost. Check CostDB or ATB fallback.
Note on F91: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on F92: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on F93: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on F94: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on F95: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on F96: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on F97: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on F98: Source: IRENA global avg; ATB Hydro/Flash Node default: Intl
Note on F99: Source: IRENA global avg; ATB Hydro/Flash Node default: Intl
Note on F100: Source: IRENA global avg; ATB Hydro/Flash Node default: Intl
Note on F101: ⚠ MISSING: No cost data for PWRGEO / Heat Rate. Check CostDB or ATB fallback.
Note on F102: ⚠ MISSING: No cost data for PWRGEO / Fuel Cost. Check CostDB or ATB fallback.
Note on F103: Source: IRENA global avg; ATB Hydro/Flash Node default: Intl
Note on F104: ⚠ MISSING: No cost data for PWRSDS / CAPEX. Check CostDB or ATB fallback.
Note on F105: Source: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW Node default: IN
Note on F106: Source: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW Node default: IN
Note on F107: ⚠ MISSING: No cost data for PWRSDS / Heat Rate. Check CostDB or ATB fallback.
Note on F108: ⚠ MISSING: No cost data for PWRSDS / Fuel Cost. Check CostDB or ATB fallback.
Note on F109: Source: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW Node default: IN
Note on F110: ⚠ MISSING: No cost data for PWRLDS / CAPEX. Check CostDB or ATB fallback.
Note on F111: Source: Generic 8h+ proxy; not single chemistry Node default: Regional
Note on F112: Source: Generic 8h+ proxy; not single chemistry Node default: Regional
Note on F113: ⚠ MISSING: No cost data for PWRLDS / Heat Rate. Check CostDB or ATB fallback.
Note on F114: ⚠ MISSING: No cost data for PWRLDS / Fuel Cost. Check CostDB or ATB fallback.
Note on F115: Source: Generic 8h+ proxy; not single chemistry Node default: Regional
Note on F116: Source: CEB LTGEP ($1,244/kW, 1.5% FOM) Node default: LK
Note on F117: Source: CEB LTGEP ($1,244/kW, 1.5% FOM) Node default: LK
Note on F118: Source: CEB LTGEP ($1,244/kW, 1.5% FOM) Node default: LK
Note on F119: ⚠ MISSING: No cost data for PWRFPV / Heat Rate. Check CostDB or ATB fallback.
Note on F120: ⚠ MISSING: No cost data for PWRFPV / Fuel Cost. Check CostDB or ATB fallback.
Note on F121: Source: CEB LTGEP ($1,244/kW, 1.5% FOM) Node default: LK
Note on F122: Source: DOE FC targets; India NGHM Node default: Intl
Note on F123: Source: DOE FC targets; India NGHM Node default: Intl
Note on F124: Source: DOE FC targets; India NGHM Node default: Intl
Note on F125: Source: DOE FC targets; India NGHM Node default: Intl
Note on F126: ⚠ MISSING: No cost data for PWRH2G / Fuel Cost. Check CostDB or ATB fallback.
Note on F127: Source: DOE FC targets; India NGHM Node default: Intl
Note on F128: Source: Marine energy literature Node default: Intl
Note on F129: Source: Marine energy literature Node default: Intl
Note on F130: Source: Marine energy literature Node default: Intl
Note on F131: ⚠ MISSING: No cost data for PWRTDL / Heat Rate. Check CostDB or ATB fallback.
Note on F132: ⚠ MISSING: No cost data for PWRTDL / Fuel Cost. Check CostDB or ATB fallback.
Note on F133: Source: Marine energy literature Node default: Intl
Note on F134: Source: Modeling construct Node default: All
Note on F135: Source: Modeling construct Node default: All
Note on F136: Source: Modeling construct Node default: All
Note on F137: ⚠ MISSING: No cost data for PWRBCK / Heat Rate. Check CostDB or ATB fallback.
Note on F138: ⚠ MISSING: No cost data for PWRBCK / Fuel Cost. Check CostDB or ATB fallback.
Note on F139: ⚠ MISSING: No cost data for PWRBCK / Construction Time. Check CostDB or ATB fallback.

## RE_Targets_Policies
scenario | Country | Node | Policy_Name | Target_Type | Target_Value | Target_Year | Mandate_or_Aspirational | Source
BAU | India | IN_N/S/E/W/NE | National Electricity Plan 2023 | Capacity_GW | 500 | 2030 | Mandate | NEP 2023
BAU | India | IN_N/S/E/W/NE | India NDC (Updated) | RE_share | 0.5 | 2030 | Mandate | India NDC 2022
BAU | Bangladesh | BD | Mujib Climate Prosperity Plan | Capacity_GW | 40 | 2041 | Aspirational | MCPP
BAU | Bangladesh | BD | Bangladesh NDC | RE_share | 0.4 | 2041 | Aspirational | Bangladesh NDC 2021
Note on I2: India 500 GW RE by 2030: CEA NEP 2023. NDC updated Aug 2022: 50% non-fossil capacity. Source: https://unfccc.int/NDCREG
Note on I3: India 50% RE share by 2030: Updated NDC Aug 2022. Source: https://pib.gov.in/PressReleasePage.aspx?PRID=1847812
Note on I4: Bangladesh 40 GW RE by 2041: Mujib Climate Prosperity Plan. ⚠ IEPMP 2023 supersedes with lower targets. Review.
Note on I5: Bangladesh 40% RE by 2041: NDC 2021. ⚠ IEPMP 2023 has more specific targets. Cross-ref BGD_DA_Final 2_Demand_Forecasts.