## README
OSTRAM — OSeMOSYS for Transmission
South Asia Power System Connectivity Model
Version: | 1.0
Last Updated: | 2026-02-26
Prepared for: | UN ESCAP
═══ WHAT IS THIS TEMPLATE ══════════════════════════════════════════════
This workbook has two types of sheets:
• Green tabs (Inventory sheets) — for collecting data. Send these to the country lead for each node.
• Blue tabs (A-O sheets) — for the OSeMOSYS model. Our Python pipeline reads these directly.
The country lead is whoever is responsible for filling in data for a given country or node.
═══ HOW TO FILL IT IN ═════════════════════════════════════════════════
Step 1 — Send the green sheets to each country lead
They fill in: existing plants, planned projects, cost data, RE targets, and interconnector updates.
Each green sheet has pre-filled headers and dropdowns. Just fill in the empty yellow cells.
Step 2 — Transfer the collected data into the blue sheets
Existing plants → ResidualCapacity in Secondary_Techs
Planned projects → TotalAnnualMinCapacity (committed) and TotalAnnualMaxCapacity
Cost data → CapitalCost and FixedCost in Secondary_Techs
Hourly load data → Demand_Projection and Demand_Profiles
Renewable resource data → Capacities_CF
Step 3 — Check the blue sheets before running the model
Every yellow cell with blue text is a gap — it needs a value.
Demand profile fractions must sum to 1.0 across the 12 timeslices for each node and year.
YearSplit fractions must also sum to 1.0.
ResidualCapacity should decline over time as plants retire.
Step 4 — Run the pipeline
The otoole-based Python pipeline reads the blue sheets and produces the OSeMOSYS .txt data file.
═══ RULES — DO NOT BREAK THESE ═══════════════════════════════════════
1. Do not rename or reorder columns in the blue sheets. The pipeline reads exact column names.
2. Do not merge cells. The Python reader cannot handle them.
3. Do not delete rows. If a technology is not available at a node, set TotalAnnualMaxCapacity = 0.
4. Projection.Mode = "User defined" and Projection.Parameter = 0 means the year-column values are used as-is.
5. CapacityToActivityUnit = 31.536 converts GW → PJ/yr. Do not change this.
6. All costs in USD 2023. Capacity in GW. Energy in PJ. Fractions as decimals (0.0–1.0).
7. Every VRE technology needs capacity factor values for all 12 timeslices.
8. Backstop (PWRBCK) is a safety valve at every node. Give it a very high cost (~99999 USD/kW).
═══ NAMING CONVENTIONS ════════════════════════════════════════════════
Technologies:
PWR + tech code + node code + XX + 01
PWRSPVBDXX01 = Solar PV, Bangladesh
PWRHDRBTXX01 = Hydro Reservoir, Bhutan
PWRCOASCPCIN_NXX01 = Coal Supercritical, India North
Demand fuels:
ELC + node code + XX02
ELCBDXX02 = Electricity demand, Bangladesh
Cross-border interconnectors:
TRNCBD_ + from_node + _ + to_node
TRNCBD_BD_IN_E = Bangladesh ↔ India East
═══ SHEET INDEX ═══════════════════════════════════════════════════════
Sheet | Type | What it contains
README | Reference (gray) | This sheet
Fixed_Horizon_Parameters | A-O (blue) | CapacityToActivityUnit, OperationalLife, I/O ratios, emission ratios
Primary_Techs | A-O (blue) | Fuel/mining tech parameters, 2023–2050
Secondary_Techs | A-O (blue) | Power generation tech parameters, 2023–2050
Capacities_CF | A-O (blue) | Capacity factors by timeslice for VRE, hydro, storage
VariableCost | A-O (blue) | Fuel variable costs by mode of operation, 2023–2050
Demand_Projection | A-O (blue) | Annual electricity demand per node (PJ/yr)
Demand_Profiles | A-O (blue) | Demand profile fractions (12 timeslices × 10 nodes)
Demand_Techs | A-O (blue) | Transmission technology parameters (PWRTRN, RNWTRN, TRNNLI, TRNRPO)
Yearsplit | A-O (blue) | Timeslice fractions of year (must sum to 1.0)
DaySplit | A-O (blue) | Daily bracket fractions
Interconnectors | Inventory (green) | Cross-border project inventory (pre-populated from Zixuan v3)
Interconnector_Params | A-O (blue) | Cross-border corridor parameters for OSeMOSYS
Existing_Generation | Inventory (green) | Plant-level existing capacity — for country leads
Planned_Generation | Inventory (green) | Pipeline projects — for country leads
Technology_Costs | Inventory (green) | Cost assumptions — for country leads
RE_Targets_Policies | Inventory (green) | RE targets and NDC commitments
Emissions | A-O (blue) | Emission factors and annual/model-period limits
Steering_Committees_MOUs | Inventory (green) | Historical agreements and steering committees
BD | Bangladesh
BT | Bhutan
IN_N | India – North
IN_S | India – South
IN_E | India – East
IN_W | India – West
IN_NE | India – Northeast
NP | Nepal
LK | Sri Lanka
MV | Maldives
═══ TIMESLICES ════════════════════════════════════════════════════════
Code | Season | Daily Band
S1D1 | Summer (Apr–May) | Night/Off-peak (22:00–06:00)
S1D2 | Summer (Apr–May) | Day/Shoulder (06:00–17:00)
S1D3 | Summer (Apr–May) | Evening/Peak (17:00–22:00)
S2D1 | Monsoon (Jun–Sep) | Night/Off-peak (22:00–06:00)
S2D2 | Monsoon (Jun–Sep) | Day/Shoulder (06:00–17:00)
S2D3 | Monsoon (Jun–Sep) | Evening/Peak (17:00–22:00)
S3D1 | Post-Monsoon (Oct–Nov) | Night/Off-peak (22:00–06:00)
S3D2 | Post-Monsoon (Oct–Nov) | Day/Shoulder (06:00–17:00)
S3D3 | Post-Monsoon (Oct–Nov) | Evening/Peak (17:00–22:00)
S4D1 | Winter (Dec–Mar) | Night/Off-peak (22:00–06:00)
S4D2 | Winter (Dec–Mar) | Day/Shoulder (06:00–17:00)
S4D3 | Winter (Dec–Mar) | Evening/Peak (17:00–22:00)
═══ UNITS ═════════════════════════════════════════════════════════════
Quantity | Unit
Capacity | GW
Energy | PJ
CAPEX | USD2023/kW
Fixed O&M | USD2023/kW/yr
Variable O&M / Fuel | USD/GJ
Demand | PJ/yr
CapacityToActivityUnit | 31.536 (GW → PJ/yr)
Emissions | tCO₂/PJ
Capacity factors | fraction (0.0–1.0)
Demand profiles | fraction (sum to 1.0 per node-year)
═══ TECHNOLOGY CODES ══════════════════════════════════════════════════
Code | Technology | Eligible Nodes
PWRSPV | Solar PV (utility-scale) | All nodes
PWRSPR | Solar PV (rooftop) | All nodes
PWRCSP | Concentrated Solar Power | IN_N/S/E/W/NE, LK
PWRWON | Onshore Wind | All nodes
PWRWOF | Offshore Wind | IN_S/W/E, BD, LK, MV
PWRHDR | Hydro – Reservoir | NP, BT, IN_N/NE/E, LK
PWRHRO | Hydro – Run-of-River | NP, BT, IN_N/NE
PWRHPS | Hydro – Pumped Storage | IN_S/W/N, NP, LK
PWRCOASCPC | Coal – Supercritical | BD, IN_N/S/E/W, LK
PWRCOAUSC | Coal – Ultra-supercritical | IN_N/S/E/W
PWRCCG | CCGT | BD, IN nodes, MV, LK
PWROCG | OCGT | BD, IN nodes, MV, LK
PWROIL | Oil/Diesel | MV, BD, LK
PWRBIO | Biomass/Bagasse | BD, IN nodes, NP, LK
PWRWTE | Waste-to-Energy | IN nodes, BD, LK
PWRURN | Nuclear | IN nodes, BD
PWRGEO | Geothermal | IN_N
PWRSDS | Short-duration storage (Li-ion 4h) | All nodes
PWRLDS | Long-duration storage (8h+) | All nodes
PWRFPV | Floating Solar PV | IN_S/E, BD, LK, MV
PWRH2G | Green Hydrogen Fuel Cell | IN nodes
PWRTDL | Tidal / Marine | IN_S, LK
PWRBCK | Backstop (penalty generator) | All nodes
MINCOA | Coal mining/import | All nodes
MINGAS | Natural Gas supply | All nodes
MINOIL | Oil supply | All nodes
MINURN | Uranium supply | All nodes
MINBIO | Biomass supply | All nodes
MINH2G | Green hydrogen production | All nodes
PWRTRN | Existing transmission (non-RE) | All nodes
RNWTRN | Existing transmission (RE) | All nodes
TRNNLI | New transmission line | All nodes
TRNRPO | Repower/upgrade transmission | All nodes
TRNCBD | Cross-border interconnector | Per corridor

## Fixed_Horizon_Parameters
Tech.Type | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Value
Secondary | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 80
Secondary | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.25
Secondary | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.25
Secondary | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.25
Secondary | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.25
Secondary | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.25
Secondary | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
Secondary | 58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
Secondary | 59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
Secondary | 59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
Secondary | 60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
Secondary | 60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
Secondary | 61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
Secondary | 61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
Secondary | 62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
Secondary | 62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
Secondary | 63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.5641
Secondary | 63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 94600
Secondary | 64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.381
Secondary | 64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 88000
Secondary | 65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.381
Secondary | 65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 88000
Secondary | 66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.381
Secondary | 66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 88000
Secondary | 67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 2 | OperationalLife | years | 40
Secondary | 67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.381
Secondary | 67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 88000
Secondary | 68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.8182
Secondary | 68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.8182
Secondary | 69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.8182
Secondary | 70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.8182
Secondary | 71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.8182
Secondary | 72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.8182
Secondary | 73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.8182
Secondary | 74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.8182
Secondary | 75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 56100
Secondary | 84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 73300
Secondary | 85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 73300
Secondary | 86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.8571
Secondary | 86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 73300
Secondary | 87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.3333
Secondary | 94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 4
Secondary | 101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | 32000
Secondary | 102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 60
Secondary | 107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 3.0303
Secondary | 107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 2 | OperationalLife | years | 15
Secondary | 118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.1111
Secondary | 118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1.3333
Secondary | 128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 2 | OperationalLife | years | 25
Secondary | 133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 2 | OperationalLife | years | 20
Secondary | 134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.2222
Secondary | 134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 2 | OperationalLife | years | 20
Secondary | 135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.2222
Secondary | 135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 2 | OperationalLife | years | 20
Secondary | 136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.2222
Secondary | 136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 2 | OperationalLife | years | 20
Secondary | 137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.2222
Secondary | 137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 2 | OperationalLife | years | 20
Secondary | 138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 2.2222
Secondary | 138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 30
Secondary | 140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Secondary | 150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Secondary | 150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 2 | OperationalLife | years | 1
Secondary | 150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 3 | InputActivityRatio | PJ/PJ | 1
Secondary | 150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 151 | MINCOABD | Coal mining/import, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 151 | MINCOABD | Coal mining/import, Bangladesh | 2 | OperationalLife | years | 99
Primary | 151 | MINCOABD | Coal mining/import, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 151 | MINCOABD | Coal mining/import, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 152 | MINCOABT | Coal mining/import, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 152 | MINCOABT | Coal mining/import, Bhutan | 2 | OperationalLife | years | 99
Primary | 152 | MINCOABT | Coal mining/import, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 152 | MINCOABT | Coal mining/import, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 153 | MINCOAIN_N | Coal mining/import, India – North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 153 | MINCOAIN_N | Coal mining/import, India – North | 2 | OperationalLife | years | 99
Primary | 153 | MINCOAIN_N | Coal mining/import, India – North | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 153 | MINCOAIN_N | Coal mining/import, India – North | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 154 | MINCOAIN_S | Coal mining/import, India – South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 154 | MINCOAIN_S | Coal mining/import, India – South | 2 | OperationalLife | years | 99
Primary | 154 | MINCOAIN_S | Coal mining/import, India – South | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 154 | MINCOAIN_S | Coal mining/import, India – South | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 155 | MINCOAIN_E | Coal mining/import, India – East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 155 | MINCOAIN_E | Coal mining/import, India – East | 2 | OperationalLife | years | 99
Primary | 155 | MINCOAIN_E | Coal mining/import, India – East | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 155 | MINCOAIN_E | Coal mining/import, India – East | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 156 | MINCOAIN_W | Coal mining/import, India – West | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 156 | MINCOAIN_W | Coal mining/import, India – West | 2 | OperationalLife | years | 99
Primary | 156 | MINCOAIN_W | Coal mining/import, India – West | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 156 | MINCOAIN_W | Coal mining/import, India – West | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 157 | MINCOAIN_NE | Coal mining/import, India – Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 157 | MINCOAIN_NE | Coal mining/import, India – Northeast | 2 | OperationalLife | years | 99
Primary | 157 | MINCOAIN_NE | Coal mining/import, India – Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 157 | MINCOAIN_NE | Coal mining/import, India – Northeast | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 158 | MINCOANP | Coal mining/import, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 158 | MINCOANP | Coal mining/import, Nepal | 2 | OperationalLife | years | 99
Primary | 158 | MINCOANP | Coal mining/import, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 158 | MINCOANP | Coal mining/import, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 159 | MINCOALK | Coal mining/import, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 159 | MINCOALK | Coal mining/import, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 159 | MINCOALK | Coal mining/import, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 159 | MINCOALK | Coal mining/import, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 160 | MINCOAMV | Coal mining/import, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 160 | MINCOAMV | Coal mining/import, Maldives | 2 | OperationalLife | years | 99
Primary | 160 | MINCOAMV | Coal mining/import, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 160 | MINCOAMV | Coal mining/import, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 161 | MINGASBD | Natural Gas supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 161 | MINGASBD | Natural Gas supply, Bangladesh | 2 | OperationalLife | years | 99
Primary | 161 | MINGASBD | Natural Gas supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 161 | MINGASBD | Natural Gas supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 162 | MINGASBT | Natural Gas supply, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 162 | MINGASBT | Natural Gas supply, Bhutan | 2 | OperationalLife | years | 99
Primary | 162 | MINGASBT | Natural Gas supply, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 162 | MINGASBT | Natural Gas supply, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 163 | MINGASIN_N | Natural Gas supply, India – North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 163 | MINGASIN_N | Natural Gas supply, India – North | 2 | OperationalLife | years | 99
Primary | 163 | MINGASIN_N | Natural Gas supply, India – North | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 163 | MINGASIN_N | Natural Gas supply, India – North | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 164 | MINGASIN_S | Natural Gas supply, India – South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 164 | MINGASIN_S | Natural Gas supply, India – South | 2 | OperationalLife | years | 99
Primary | 164 | MINGASIN_S | Natural Gas supply, India – South | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 164 | MINGASIN_S | Natural Gas supply, India – South | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 165 | MINGASIN_E | Natural Gas supply, India – East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 165 | MINGASIN_E | Natural Gas supply, India – East | 2 | OperationalLife | years | 99
Primary | 165 | MINGASIN_E | Natural Gas supply, India – East | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 165 | MINGASIN_E | Natural Gas supply, India – East | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 166 | MINGASIN_W | Natural Gas supply, India – West | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 166 | MINGASIN_W | Natural Gas supply, India – West | 2 | OperationalLife | years | 99
Primary | 166 | MINGASIN_W | Natural Gas supply, India – West | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 166 | MINGASIN_W | Natural Gas supply, India – West | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 167 | MINGASIN_NE | Natural Gas supply, India – Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 167 | MINGASIN_NE | Natural Gas supply, India – Northeast | 2 | OperationalLife | years | 99
Primary | 167 | MINGASIN_NE | Natural Gas supply, India – Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 167 | MINGASIN_NE | Natural Gas supply, India – Northeast | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 168 | MINGASNP | Natural Gas supply, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 168 | MINGASNP | Natural Gas supply, Nepal | 2 | OperationalLife | years | 99
Primary | 168 | MINGASNP | Natural Gas supply, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 168 | MINGASNP | Natural Gas supply, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 169 | MINGASLK | Natural Gas supply, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 169 | MINGASLK | Natural Gas supply, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 169 | MINGASLK | Natural Gas supply, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 169 | MINGASLK | Natural Gas supply, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 170 | MINGASMV | Natural Gas supply, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 170 | MINGASMV | Natural Gas supply, Maldives | 2 | OperationalLife | years | 99
Primary | 170 | MINGASMV | Natural Gas supply, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 170 | MINGASMV | Natural Gas supply, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 171 | MINOILBD | Oil supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 171 | MINOILBD | Oil supply, Bangladesh | 2 | OperationalLife | years | 99
Primary | 171 | MINOILBD | Oil supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 171 | MINOILBD | Oil supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 172 | MINOILBT | Oil supply, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 172 | MINOILBT | Oil supply, Bhutan | 2 | OperationalLife | years | 99
Primary | 172 | MINOILBT | Oil supply, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 172 | MINOILBT | Oil supply, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 173 | MINOILIN_N | Oil supply, India – North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 173 | MINOILIN_N | Oil supply, India – North | 2 | OperationalLife | years | 99
Primary | 173 | MINOILIN_N | Oil supply, India – North | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 173 | MINOILIN_N | Oil supply, India – North | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 174 | MINOILIN_S | Oil supply, India – South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 174 | MINOILIN_S | Oil supply, India – South | 2 | OperationalLife | years | 99
Primary | 174 | MINOILIN_S | Oil supply, India – South | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 174 | MINOILIN_S | Oil supply, India – South | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 175 | MINOILIN_E | Oil supply, India – East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 175 | MINOILIN_E | Oil supply, India – East | 2 | OperationalLife | years | 99
Primary | 175 | MINOILIN_E | Oil supply, India – East | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 175 | MINOILIN_E | Oil supply, India – East | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 176 | MINOILIN_W | Oil supply, India – West | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 176 | MINOILIN_W | Oil supply, India – West | 2 | OperationalLife | years | 99
Primary | 176 | MINOILIN_W | Oil supply, India – West | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 176 | MINOILIN_W | Oil supply, India – West | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 177 | MINOILIN_NE | Oil supply, India – Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 177 | MINOILIN_NE | Oil supply, India – Northeast | 2 | OperationalLife | years | 99
Primary | 177 | MINOILIN_NE | Oil supply, India – Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 177 | MINOILIN_NE | Oil supply, India – Northeast | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 178 | MINOILNP | Oil supply, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 178 | MINOILNP | Oil supply, Nepal | 2 | OperationalLife | years | 99
Primary | 178 | MINOILNP | Oil supply, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 178 | MINOILNP | Oil supply, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 179 | MINOILLK | Oil supply, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 179 | MINOILLK | Oil supply, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 179 | MINOILLK | Oil supply, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 179 | MINOILLK | Oil supply, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 180 | MINOILMV | Oil supply, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 180 | MINOILMV | Oil supply, Maldives | 2 | OperationalLife | years | 99
Primary | 180 | MINOILMV | Oil supply, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 180 | MINOILMV | Oil supply, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 181 | MINURNBD | Uranium supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 181 | MINURNBD | Uranium supply, Bangladesh | 2 | OperationalLife | years | 99
Primary | 181 | MINURNBD | Uranium supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 181 | MINURNBD | Uranium supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 182 | MINURNBT | Uranium supply, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 182 | MINURNBT | Uranium supply, Bhutan | 2 | OperationalLife | years | 99
Primary | 182 | MINURNBT | Uranium supply, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 182 | MINURNBT | Uranium supply, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 183 | MINURNIN_N | Uranium supply, India – North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 183 | MINURNIN_N | Uranium supply, India – North | 2 | OperationalLife | years | 99
Primary | 183 | MINURNIN_N | Uranium supply, India – North | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 183 | MINURNIN_N | Uranium supply, India – North | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 184 | MINURNIN_S | Uranium supply, India – South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 184 | MINURNIN_S | Uranium supply, India – South | 2 | OperationalLife | years | 99
Primary | 184 | MINURNIN_S | Uranium supply, India – South | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 184 | MINURNIN_S | Uranium supply, India – South | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 185 | MINURNIN_E | Uranium supply, India – East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 185 | MINURNIN_E | Uranium supply, India – East | 2 | OperationalLife | years | 99
Primary | 185 | MINURNIN_E | Uranium supply, India – East | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 185 | MINURNIN_E | Uranium supply, India – East | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 186 | MINURNIN_W | Uranium supply, India – West | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 186 | MINURNIN_W | Uranium supply, India – West | 2 | OperationalLife | years | 99
Primary | 186 | MINURNIN_W | Uranium supply, India – West | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 186 | MINURNIN_W | Uranium supply, India – West | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 187 | MINURNIN_NE | Uranium supply, India – Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 187 | MINURNIN_NE | Uranium supply, India – Northeast | 2 | OperationalLife | years | 99
Primary | 187 | MINURNIN_NE | Uranium supply, India – Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 187 | MINURNIN_NE | Uranium supply, India – Northeast | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 188 | MINURNNP | Uranium supply, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 188 | MINURNNP | Uranium supply, Nepal | 2 | OperationalLife | years | 99
Primary | 188 | MINURNNP | Uranium supply, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 188 | MINURNNP | Uranium supply, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 189 | MINURNLK | Uranium supply, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 189 | MINURNLK | Uranium supply, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 189 | MINURNLK | Uranium supply, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 189 | MINURNLK | Uranium supply, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 190 | MINURNMV | Uranium supply, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 190 | MINURNMV | Uranium supply, Maldives | 2 | OperationalLife | years | 99
Primary | 190 | MINURNMV | Uranium supply, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 190 | MINURNMV | Uranium supply, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 191 | MINBIOBD | Biomass supply, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 191 | MINBIOBD | Biomass supply, Bangladesh | 2 | OperationalLife | years | 99
Primary | 191 | MINBIOBD | Biomass supply, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 191 | MINBIOBD | Biomass supply, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 192 | MINBIOBT | Biomass supply, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 192 | MINBIOBT | Biomass supply, Bhutan | 2 | OperationalLife | years | 99
Primary | 192 | MINBIOBT | Biomass supply, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 192 | MINBIOBT | Biomass supply, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 193 | MINBIOIN_N | Biomass supply, India – North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 193 | MINBIOIN_N | Biomass supply, India – North | 2 | OperationalLife | years | 99
Primary | 193 | MINBIOIN_N | Biomass supply, India – North | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 193 | MINBIOIN_N | Biomass supply, India – North | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 194 | MINBIOIN_S | Biomass supply, India – South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 194 | MINBIOIN_S | Biomass supply, India – South | 2 | OperationalLife | years | 99
Primary | 194 | MINBIOIN_S | Biomass supply, India – South | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 194 | MINBIOIN_S | Biomass supply, India – South | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 195 | MINBIOIN_E | Biomass supply, India – East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 195 | MINBIOIN_E | Biomass supply, India – East | 2 | OperationalLife | years | 99
Primary | 195 | MINBIOIN_E | Biomass supply, India – East | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 195 | MINBIOIN_E | Biomass supply, India – East | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 196 | MINBIOIN_W | Biomass supply, India – West | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 196 | MINBIOIN_W | Biomass supply, India – West | 2 | OperationalLife | years | 99
Primary | 196 | MINBIOIN_W | Biomass supply, India – West | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 196 | MINBIOIN_W | Biomass supply, India – West | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 197 | MINBIOIN_NE | Biomass supply, India – Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 197 | MINBIOIN_NE | Biomass supply, India – Northeast | 2 | OperationalLife | years | 99
Primary | 197 | MINBIOIN_NE | Biomass supply, India – Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 197 | MINBIOIN_NE | Biomass supply, India – Northeast | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 198 | MINBIONP | Biomass supply, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 198 | MINBIONP | Biomass supply, Nepal | 2 | OperationalLife | years | 99
Primary | 198 | MINBIONP | Biomass supply, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 198 | MINBIONP | Biomass supply, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 199 | MINBIOLK | Biomass supply, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 199 | MINBIOLK | Biomass supply, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 199 | MINBIOLK | Biomass supply, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 199 | MINBIOLK | Biomass supply, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 200 | MINBIOMV | Biomass supply, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 200 | MINBIOMV | Biomass supply, Maldives | 2 | OperationalLife | years | 99
Primary | 200 | MINBIOMV | Biomass supply, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 200 | MINBIOMV | Biomass supply, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 201 | MINH2GBD | Green hydrogen production, Bangladesh | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 201 | MINH2GBD | Green hydrogen production, Bangladesh | 2 | OperationalLife | years | 99
Primary | 201 | MINH2GBD | Green hydrogen production, Bangladesh | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 201 | MINH2GBD | Green hydrogen production, Bangladesh | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 202 | MINH2GBT | Green hydrogen production, Bhutan | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 202 | MINH2GBT | Green hydrogen production, Bhutan | 2 | OperationalLife | years | 99
Primary | 202 | MINH2GBT | Green hydrogen production, Bhutan | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 202 | MINH2GBT | Green hydrogen production, Bhutan | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 203 | MINH2GIN_N | Green hydrogen production, India – North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 203 | MINH2GIN_N | Green hydrogen production, India – North | 2 | OperationalLife | years | 99
Primary | 203 | MINH2GIN_N | Green hydrogen production, India – North | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 203 | MINH2GIN_N | Green hydrogen production, India – North | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 204 | MINH2GIN_S | Green hydrogen production, India – South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 204 | MINH2GIN_S | Green hydrogen production, India – South | 2 | OperationalLife | years | 99
Primary | 204 | MINH2GIN_S | Green hydrogen production, India – South | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 204 | MINH2GIN_S | Green hydrogen production, India – South | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 205 | MINH2GIN_E | Green hydrogen production, India – East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 205 | MINH2GIN_E | Green hydrogen production, India – East | 2 | OperationalLife | years | 99
Primary | 205 | MINH2GIN_E | Green hydrogen production, India – East | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 205 | MINH2GIN_E | Green hydrogen production, India – East | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 206 | MINH2GIN_W | Green hydrogen production, India – West | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 206 | MINH2GIN_W | Green hydrogen production, India – West | 2 | OperationalLife | years | 99
Primary | 206 | MINH2GIN_W | Green hydrogen production, India – West | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 206 | MINH2GIN_W | Green hydrogen production, India – West | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 207 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 207 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 2 | OperationalLife | years | 99
Primary | 207 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 207 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 208 | MINH2GNP | Green hydrogen production, Nepal | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 208 | MINH2GNP | Green hydrogen production, Nepal | 2 | OperationalLife | years | 99
Primary | 208 | MINH2GNP | Green hydrogen production, Nepal | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 208 | MINH2GNP | Green hydrogen production, Nepal | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 209 | MINH2GLK | Green hydrogen production, Sri Lanka | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 209 | MINH2GLK | Green hydrogen production, Sri Lanka | 2 | OperationalLife | years | 99
Primary | 209 | MINH2GLK | Green hydrogen production, Sri Lanka | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 209 | MINH2GLK | Green hydrogen production, Sri Lanka | 4 | OutputActivityRatio | PJ/PJ | 1
Primary | 210 | MINH2GMV | Green hydrogen production, Maldives | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Primary | 210 | MINH2GMV | Green hydrogen production, Maldives | 2 | OperationalLife | years | 99
Primary | 210 | MINH2GMV | Green hydrogen production, Maldives | 3 | InputActivityRatio | PJ/PJ | 1
Primary | 210 | MINH2GMV | Green hydrogen production, Maldives | 4 | OutputActivityRatio | PJ/PJ | 1
Demand | 211 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 211 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 2 | OperationalLife | years | 50
Demand | 211 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 211 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 212 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 212 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 2 | OperationalLife | years | 50
Demand | 212 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 212 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 213 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 213 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 2 | OperationalLife | years | 50
Demand | 213 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 213 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 214 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 214 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 2 | OperationalLife | years | 50
Demand | 214 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 214 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 215 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 215 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 2 | OperationalLife | years | 50
Demand | 215 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 215 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 216 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 216 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 2 | OperationalLife | years | 50
Demand | 216 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 216 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 217 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 217 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 2 | OperationalLife | years | 50
Demand | 217 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 217 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 218 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 218 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 2 | OperationalLife | years | 50
Demand | 218 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 218 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 219 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 219 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 2 | OperationalLife | years | 50
Demand | 219 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 219 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 220 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 220 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 2 | OperationalLife | years | 50
Demand | 220 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 220 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 221 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 221 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 2 | OperationalLife | years | 50
Demand | 221 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 221 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 222 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 222 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 2 | OperationalLife | years | 50
Demand | 222 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 222 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 223 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 223 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 2 | OperationalLife | years | 50
Demand | 223 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 223 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 224 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 224 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 2 | OperationalLife | years | 50
Demand | 224 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 224 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 225 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 225 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 2 | OperationalLife | years | 50
Demand | 225 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 225 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 226 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 226 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 2 | OperationalLife | years | 50
Demand | 226 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 226 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 227 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 227 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 2 | OperationalLife | years | 50
Demand | 227 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 227 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 228 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 228 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 2 | OperationalLife | years | 50
Demand | 228 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 228 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 229 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 229 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 2 | OperationalLife | years | 50
Demand | 229 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 229 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 230 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 230 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 2 | OperationalLife | years | 50
Demand | 230 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 230 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 231 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 231 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 2 | OperationalLife | years | 50
Demand | 231 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 231 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 232 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 232 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 2 | OperationalLife | years | 50
Demand | 232 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 232 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 233 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 233 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 2 | OperationalLife | years | 50
Demand | 233 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 233 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 234 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 234 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 2 | OperationalLife | years | 50
Demand | 234 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 234 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 235 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 235 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 2 | OperationalLife | years | 50
Demand | 235 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 235 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 236 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 236 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 2 | OperationalLife | years | 50
Demand | 236 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 236 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 237 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 237 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 2 | OperationalLife | years | 50
Demand | 237 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 237 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 238 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 238 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 2 | OperationalLife | years | 50
Demand | 238 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 238 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 239 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 239 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 2 | OperationalLife | years | 50
Demand | 239 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 239 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 240 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 240 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 2 | OperationalLife | years | 50
Demand | 240 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 240 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 241 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 241 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 2 | OperationalLife | years | 50
Demand | 241 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 241 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 242 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 242 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 2 | OperationalLife | years | 50
Demand | 242 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 242 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 243 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 243 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 2 | OperationalLife | years | 50
Demand | 243 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 243 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 244 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 244 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 2 | OperationalLife | years | 50
Demand | 244 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 244 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 245 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 245 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 2 | OperationalLife | years | 50
Demand | 245 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 245 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 246 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 246 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 2 | OperationalLife | years | 50
Demand | 246 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 246 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 247 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 247 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 2 | OperationalLife | years | 50
Demand | 247 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 247 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 248 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 248 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 2 | OperationalLife | years | 50
Demand | 248 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 248 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 249 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 249 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 2 | OperationalLife | years | 50
Demand | 249 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 249 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 250 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 250 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 2 | OperationalLife | years | 50
Demand | 250 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 250 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 4 | OutputActivityRatio | PJ/PJ | 0.97
Demand | 251 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 251 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 2 | OperationalLife | years | 50
Demand | 251 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 251 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 252 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 252 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 2 | OperationalLife | years | 50
Demand | 252 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 252 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 253 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 253 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 2 | OperationalLife | years | 50
Demand | 253 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 253 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 254 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 254 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 2 | OperationalLife | years | 50
Demand | 254 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 254 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 255 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 255 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 2 | OperationalLife | years | 50
Demand | 255 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 255 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 256 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 256 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 2 | OperationalLife | years | 50
Demand | 256 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 256 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 257 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 257 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 2 | OperationalLife | years | 50
Demand | 257 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 257 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 258 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 258 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 2 | OperationalLife | years | 50
Demand | 258 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 258 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 259 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 259 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 2 | OperationalLife | years | 50
Demand | 259 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 259 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 260 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 260 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 2 | OperationalLife | years | 50
Demand | 260 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 260 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 261 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 261 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 2 | OperationalLife | years | 50
Demand | 261 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 261 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 262 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 262 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 2 | OperationalLife | years | 50
Demand | 262 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 262 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 4 | OutputActivityRatio | PJ/PJ | 0.95
Demand | 263 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 1 | CapacityToActivityUnit | PJ/GW | 31.536
Demand | 263 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 2 | OperationalLife | years | 50
Demand | 263 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 3 | InputActivityRatio | PJ/PJ | 1
Demand | 263 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 4 | OutputActivityRatio | PJ/PJ | 0.95

## Primary_Techs
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | MINCOABD | Coal mining/import, Bangladesh | 1 | CapitalCost | USD/kW | User defined | 0
1 | MINCOABD | Coal mining/import, Bangladesh | 2 | FixedCost | USD/kW/yr | User defined | 0
1 | MINCOABD | Coal mining/import, Bangladesh | 3 | ResidualCapacity | GW | User defined | 0
1 | MINCOABD | Coal mining/import, Bangladesh | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
1 | MINCOABD | Coal mining/import, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
2 | MINCOABT | Coal mining/import, Bhutan | 1 | CapitalCost | USD/kW | User defined | 0
2 | MINCOABT | Coal mining/import, Bhutan | 2 | FixedCost | USD/kW/yr | User defined | 0
2 | MINCOABT | Coal mining/import, Bhutan | 3 | ResidualCapacity | GW | User defined | 0
2 | MINCOABT | Coal mining/import, Bhutan | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
2 | MINCOABT | Coal mining/import, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
3 | MINCOAIN_N | Coal mining/import, India – North | 1 | CapitalCost | USD/kW | User defined | 0
3 | MINCOAIN_N | Coal mining/import, India – North | 2 | FixedCost | USD/kW/yr | User defined | 0
3 | MINCOAIN_N | Coal mining/import, India – North | 3 | ResidualCapacity | GW | User defined | 0
3 | MINCOAIN_N | Coal mining/import, India – North | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
3 | MINCOAIN_N | Coal mining/import, India – North | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
4 | MINCOAIN_S | Coal mining/import, India – South | 1 | CapitalCost | USD/kW | User defined | 0
4 | MINCOAIN_S | Coal mining/import, India – South | 2 | FixedCost | USD/kW/yr | User defined | 0
4 | MINCOAIN_S | Coal mining/import, India – South | 3 | ResidualCapacity | GW | User defined | 0
4 | MINCOAIN_S | Coal mining/import, India – South | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
4 | MINCOAIN_S | Coal mining/import, India – South | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
5 | MINCOAIN_E | Coal mining/import, India – East | 1 | CapitalCost | USD/kW | User defined | 0
5 | MINCOAIN_E | Coal mining/import, India – East | 2 | FixedCost | USD/kW/yr | User defined | 0
5 | MINCOAIN_E | Coal mining/import, India – East | 3 | ResidualCapacity | GW | User defined | 0
5 | MINCOAIN_E | Coal mining/import, India – East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
5 | MINCOAIN_E | Coal mining/import, India – East | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
6 | MINCOAIN_W | Coal mining/import, India – West | 1 | CapitalCost | USD/kW | User defined | 0
6 | MINCOAIN_W | Coal mining/import, India – West | 2 | FixedCost | USD/kW/yr | User defined | 0
6 | MINCOAIN_W | Coal mining/import, India – West | 3 | ResidualCapacity | GW | User defined | 0
6 | MINCOAIN_W | Coal mining/import, India – West | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
6 | MINCOAIN_W | Coal mining/import, India – West | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
7 | MINCOAIN_NE | Coal mining/import, India – Northeast | 1 | CapitalCost | USD/kW | User defined | 0
7 | MINCOAIN_NE | Coal mining/import, India – Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0
7 | MINCOAIN_NE | Coal mining/import, India – Northeast | 3 | ResidualCapacity | GW | User defined | 0
7 | MINCOAIN_NE | Coal mining/import, India – Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
7 | MINCOAIN_NE | Coal mining/import, India – Northeast | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
8 | MINCOANP | Coal mining/import, Nepal | 1 | CapitalCost | USD/kW | User defined | 0
8 | MINCOANP | Coal mining/import, Nepal | 2 | FixedCost | USD/kW/yr | User defined | 0
8 | MINCOANP | Coal mining/import, Nepal | 3 | ResidualCapacity | GW | User defined | 0
8 | MINCOANP | Coal mining/import, Nepal | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
8 | MINCOANP | Coal mining/import, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
9 | MINCOALK | Coal mining/import, Sri Lanka | 1 | CapitalCost | USD/kW | User defined | 0
9 | MINCOALK | Coal mining/import, Sri Lanka | 2 | FixedCost | USD/kW/yr | User defined | 0
9 | MINCOALK | Coal mining/import, Sri Lanka | 3 | ResidualCapacity | GW | User defined | 0
9 | MINCOALK | Coal mining/import, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
9 | MINCOALK | Coal mining/import, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
10 | MINCOAMV | Coal mining/import, Maldives | 1 | CapitalCost | USD/kW | User defined | 0
10 | MINCOAMV | Coal mining/import, Maldives | 2 | FixedCost | USD/kW/yr | User defined | 0
10 | MINCOAMV | Coal mining/import, Maldives | 3 | ResidualCapacity | GW | User defined | 0
10 | MINCOAMV | Coal mining/import, Maldives | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
10 | MINCOAMV | Coal mining/import, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
11 | MINGASBD | Natural Gas supply, Bangladesh | 1 | CapitalCost | USD/kW | User defined | 0
11 | MINGASBD | Natural Gas supply, Bangladesh | 2 | FixedCost | USD/kW/yr | User defined | 0
11 | MINGASBD | Natural Gas supply, Bangladesh | 3 | ResidualCapacity | GW | User defined | 0
11 | MINGASBD | Natural Gas supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
11 | MINGASBD | Natural Gas supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
12 | MINGASBT | Natural Gas supply, Bhutan | 1 | CapitalCost | USD/kW | User defined | 0
12 | MINGASBT | Natural Gas supply, Bhutan | 2 | FixedCost | USD/kW/yr | User defined | 0
12 | MINGASBT | Natural Gas supply, Bhutan | 3 | ResidualCapacity | GW | User defined | 0
12 | MINGASBT | Natural Gas supply, Bhutan | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
12 | MINGASBT | Natural Gas supply, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
13 | MINGASIN_N | Natural Gas supply, India – North | 1 | CapitalCost | USD/kW | User defined | 0
13 | MINGASIN_N | Natural Gas supply, India – North | 2 | FixedCost | USD/kW/yr | User defined | 0
13 | MINGASIN_N | Natural Gas supply, India – North | 3 | ResidualCapacity | GW | User defined | 0
13 | MINGASIN_N | Natural Gas supply, India – North | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
13 | MINGASIN_N | Natural Gas supply, India – North | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
14 | MINGASIN_S | Natural Gas supply, India – South | 1 | CapitalCost | USD/kW | User defined | 0
14 | MINGASIN_S | Natural Gas supply, India – South | 2 | FixedCost | USD/kW/yr | User defined | 0
14 | MINGASIN_S | Natural Gas supply, India – South | 3 | ResidualCapacity | GW | User defined | 0
14 | MINGASIN_S | Natural Gas supply, India – South | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
14 | MINGASIN_S | Natural Gas supply, India – South | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
15 | MINGASIN_E | Natural Gas supply, India – East | 1 | CapitalCost | USD/kW | User defined | 0
15 | MINGASIN_E | Natural Gas supply, India – East | 2 | FixedCost | USD/kW/yr | User defined | 0
15 | MINGASIN_E | Natural Gas supply, India – East | 3 | ResidualCapacity | GW | User defined | 0
15 | MINGASIN_E | Natural Gas supply, India – East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
15 | MINGASIN_E | Natural Gas supply, India – East | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
16 | MINGASIN_W | Natural Gas supply, India – West | 1 | CapitalCost | USD/kW | User defined | 0
16 | MINGASIN_W | Natural Gas supply, India – West | 2 | FixedCost | USD/kW/yr | User defined | 0
16 | MINGASIN_W | Natural Gas supply, India – West | 3 | ResidualCapacity | GW | User defined | 0
16 | MINGASIN_W | Natural Gas supply, India – West | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
16 | MINGASIN_W | Natural Gas supply, India – West | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
17 | MINGASIN_NE | Natural Gas supply, India – Northeast | 1 | CapitalCost | USD/kW | User defined | 0
17 | MINGASIN_NE | Natural Gas supply, India – Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0
17 | MINGASIN_NE | Natural Gas supply, India – Northeast | 3 | ResidualCapacity | GW | User defined | 0
17 | MINGASIN_NE | Natural Gas supply, India – Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
17 | MINGASIN_NE | Natural Gas supply, India – Northeast | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
18 | MINGASNP | Natural Gas supply, Nepal | 1 | CapitalCost | USD/kW | User defined | 0
18 | MINGASNP | Natural Gas supply, Nepal | 2 | FixedCost | USD/kW/yr | User defined | 0
18 | MINGASNP | Natural Gas supply, Nepal | 3 | ResidualCapacity | GW | User defined | 0
18 | MINGASNP | Natural Gas supply, Nepal | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
18 | MINGASNP | Natural Gas supply, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
19 | MINGASLK | Natural Gas supply, Sri Lanka | 1 | CapitalCost | USD/kW | User defined | 0
19 | MINGASLK | Natural Gas supply, Sri Lanka | 2 | FixedCost | USD/kW/yr | User defined | 0
19 | MINGASLK | Natural Gas supply, Sri Lanka | 3 | ResidualCapacity | GW | User defined | 0
19 | MINGASLK | Natural Gas supply, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
19 | MINGASLK | Natural Gas supply, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
20 | MINGASMV | Natural Gas supply, Maldives | 1 | CapitalCost | USD/kW | User defined | 0
20 | MINGASMV | Natural Gas supply, Maldives | 2 | FixedCost | USD/kW/yr | User defined | 0
20 | MINGASMV | Natural Gas supply, Maldives | 3 | ResidualCapacity | GW | User defined | 0
20 | MINGASMV | Natural Gas supply, Maldives | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
20 | MINGASMV | Natural Gas supply, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
21 | MINOILBD | Oil supply, Bangladesh | 1 | CapitalCost | USD/kW | User defined | 0
21 | MINOILBD | Oil supply, Bangladesh | 2 | FixedCost | USD/kW/yr | User defined | 0
21 | MINOILBD | Oil supply, Bangladesh | 3 | ResidualCapacity | GW | User defined | 0
21 | MINOILBD | Oil supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
21 | MINOILBD | Oil supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
22 | MINOILBT | Oil supply, Bhutan | 1 | CapitalCost | USD/kW | User defined | 0
22 | MINOILBT | Oil supply, Bhutan | 2 | FixedCost | USD/kW/yr | User defined | 0
22 | MINOILBT | Oil supply, Bhutan | 3 | ResidualCapacity | GW | User defined | 0
22 | MINOILBT | Oil supply, Bhutan | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
22 | MINOILBT | Oil supply, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
23 | MINOILIN_N | Oil supply, India – North | 1 | CapitalCost | USD/kW | User defined | 0
23 | MINOILIN_N | Oil supply, India – North | 2 | FixedCost | USD/kW/yr | User defined | 0
23 | MINOILIN_N | Oil supply, India – North | 3 | ResidualCapacity | GW | User defined | 0
23 | MINOILIN_N | Oil supply, India – North | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
23 | MINOILIN_N | Oil supply, India – North | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
24 | MINOILIN_S | Oil supply, India – South | 1 | CapitalCost | USD/kW | User defined | 0
24 | MINOILIN_S | Oil supply, India – South | 2 | FixedCost | USD/kW/yr | User defined | 0
24 | MINOILIN_S | Oil supply, India – South | 3 | ResidualCapacity | GW | User defined | 0
24 | MINOILIN_S | Oil supply, India – South | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
24 | MINOILIN_S | Oil supply, India – South | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
25 | MINOILIN_E | Oil supply, India – East | 1 | CapitalCost | USD/kW | User defined | 0
25 | MINOILIN_E | Oil supply, India – East | 2 | FixedCost | USD/kW/yr | User defined | 0
25 | MINOILIN_E | Oil supply, India – East | 3 | ResidualCapacity | GW | User defined | 0
25 | MINOILIN_E | Oil supply, India – East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
25 | MINOILIN_E | Oil supply, India – East | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
26 | MINOILIN_W | Oil supply, India – West | 1 | CapitalCost | USD/kW | User defined | 0
26 | MINOILIN_W | Oil supply, India – West | 2 | FixedCost | USD/kW/yr | User defined | 0
26 | MINOILIN_W | Oil supply, India – West | 3 | ResidualCapacity | GW | User defined | 0
26 | MINOILIN_W | Oil supply, India – West | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
26 | MINOILIN_W | Oil supply, India – West | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
27 | MINOILIN_NE | Oil supply, India – Northeast | 1 | CapitalCost | USD/kW | User defined | 0
27 | MINOILIN_NE | Oil supply, India – Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0
27 | MINOILIN_NE | Oil supply, India – Northeast | 3 | ResidualCapacity | GW | User defined | 0
27 | MINOILIN_NE | Oil supply, India – Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
27 | MINOILIN_NE | Oil supply, India – Northeast | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
28 | MINOILNP | Oil supply, Nepal | 1 | CapitalCost | USD/kW | User defined | 0
28 | MINOILNP | Oil supply, Nepal | 2 | FixedCost | USD/kW/yr | User defined | 0
28 | MINOILNP | Oil supply, Nepal | 3 | ResidualCapacity | GW | User defined | 0
28 | MINOILNP | Oil supply, Nepal | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
28 | MINOILNP | Oil supply, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
29 | MINOILLK | Oil supply, Sri Lanka | 1 | CapitalCost | USD/kW | User defined | 0
29 | MINOILLK | Oil supply, Sri Lanka | 2 | FixedCost | USD/kW/yr | User defined | 0
29 | MINOILLK | Oil supply, Sri Lanka | 3 | ResidualCapacity | GW | User defined | 0
29 | MINOILLK | Oil supply, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
29 | MINOILLK | Oil supply, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
30 | MINOILMV | Oil supply, Maldives | 1 | CapitalCost | USD/kW | User defined | 0
30 | MINOILMV | Oil supply, Maldives | 2 | FixedCost | USD/kW/yr | User defined | 0
30 | MINOILMV | Oil supply, Maldives | 3 | ResidualCapacity | GW | User defined | 0
30 | MINOILMV | Oil supply, Maldives | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
30 | MINOILMV | Oil supply, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
31 | MINURNBD | Uranium supply, Bangladesh | 1 | CapitalCost | USD/kW | User defined | 0
31 | MINURNBD | Uranium supply, Bangladesh | 2 | FixedCost | USD/kW/yr | User defined | 0
31 | MINURNBD | Uranium supply, Bangladesh | 3 | ResidualCapacity | GW | User defined | 0
31 | MINURNBD | Uranium supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
31 | MINURNBD | Uranium supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
32 | MINURNBT | Uranium supply, Bhutan | 1 | CapitalCost | USD/kW | User defined | 0
32 | MINURNBT | Uranium supply, Bhutan | 2 | FixedCost | USD/kW/yr | User defined | 0
32 | MINURNBT | Uranium supply, Bhutan | 3 | ResidualCapacity | GW | User defined | 0
32 | MINURNBT | Uranium supply, Bhutan | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
32 | MINURNBT | Uranium supply, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
33 | MINURNIN_N | Uranium supply, India – North | 1 | CapitalCost | USD/kW | User defined | 0
33 | MINURNIN_N | Uranium supply, India – North | 2 | FixedCost | USD/kW/yr | User defined | 0
33 | MINURNIN_N | Uranium supply, India – North | 3 | ResidualCapacity | GW | User defined | 0
33 | MINURNIN_N | Uranium supply, India – North | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
33 | MINURNIN_N | Uranium supply, India – North | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
34 | MINURNIN_S | Uranium supply, India – South | 1 | CapitalCost | USD/kW | User defined | 0
34 | MINURNIN_S | Uranium supply, India – South | 2 | FixedCost | USD/kW/yr | User defined | 0
34 | MINURNIN_S | Uranium supply, India – South | 3 | ResidualCapacity | GW | User defined | 0
34 | MINURNIN_S | Uranium supply, India – South | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
34 | MINURNIN_S | Uranium supply, India – South | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
35 | MINURNIN_E | Uranium supply, India – East | 1 | CapitalCost | USD/kW | User defined | 0
35 | MINURNIN_E | Uranium supply, India – East | 2 | FixedCost | USD/kW/yr | User defined | 0
35 | MINURNIN_E | Uranium supply, India – East | 3 | ResidualCapacity | GW | User defined | 0
35 | MINURNIN_E | Uranium supply, India – East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
35 | MINURNIN_E | Uranium supply, India – East | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
36 | MINURNIN_W | Uranium supply, India – West | 1 | CapitalCost | USD/kW | User defined | 0
36 | MINURNIN_W | Uranium supply, India – West | 2 | FixedCost | USD/kW/yr | User defined | 0
36 | MINURNIN_W | Uranium supply, India – West | 3 | ResidualCapacity | GW | User defined | 0
36 | MINURNIN_W | Uranium supply, India – West | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
36 | MINURNIN_W | Uranium supply, India – West | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
37 | MINURNIN_NE | Uranium supply, India – Northeast | 1 | CapitalCost | USD/kW | User defined | 0
37 | MINURNIN_NE | Uranium supply, India – Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0
37 | MINURNIN_NE | Uranium supply, India – Northeast | 3 | ResidualCapacity | GW | User defined | 0
37 | MINURNIN_NE | Uranium supply, India – Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
37 | MINURNIN_NE | Uranium supply, India – Northeast | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
38 | MINURNNP | Uranium supply, Nepal | 1 | CapitalCost | USD/kW | User defined | 0
38 | MINURNNP | Uranium supply, Nepal | 2 | FixedCost | USD/kW/yr | User defined | 0
38 | MINURNNP | Uranium supply, Nepal | 3 | ResidualCapacity | GW | User defined | 0
38 | MINURNNP | Uranium supply, Nepal | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
38 | MINURNNP | Uranium supply, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
39 | MINURNLK | Uranium supply, Sri Lanka | 1 | CapitalCost | USD/kW | User defined | 0
39 | MINURNLK | Uranium supply, Sri Lanka | 2 | FixedCost | USD/kW/yr | User defined | 0
39 | MINURNLK | Uranium supply, Sri Lanka | 3 | ResidualCapacity | GW | User defined | 0
39 | MINURNLK | Uranium supply, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
39 | MINURNLK | Uranium supply, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
40 | MINURNMV | Uranium supply, Maldives | 1 | CapitalCost | USD/kW | User defined | 0
40 | MINURNMV | Uranium supply, Maldives | 2 | FixedCost | USD/kW/yr | User defined | 0
40 | MINURNMV | Uranium supply, Maldives | 3 | ResidualCapacity | GW | User defined | 0
40 | MINURNMV | Uranium supply, Maldives | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
40 | MINURNMV | Uranium supply, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
41 | MINBIOBD | Biomass supply, Bangladesh | 1 | CapitalCost | USD/kW | User defined | 0
41 | MINBIOBD | Biomass supply, Bangladesh | 2 | FixedCost | USD/kW/yr | User defined | 0
41 | MINBIOBD | Biomass supply, Bangladesh | 3 | ResidualCapacity | GW | User defined | 0
41 | MINBIOBD | Biomass supply, Bangladesh | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
41 | MINBIOBD | Biomass supply, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
42 | MINBIOBT | Biomass supply, Bhutan | 1 | CapitalCost | USD/kW | User defined | 0
42 | MINBIOBT | Biomass supply, Bhutan | 2 | FixedCost | USD/kW/yr | User defined | 0
42 | MINBIOBT | Biomass supply, Bhutan | 3 | ResidualCapacity | GW | User defined | 0
42 | MINBIOBT | Biomass supply, Bhutan | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
42 | MINBIOBT | Biomass supply, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
43 | MINBIOIN_N | Biomass supply, India – North | 1 | CapitalCost | USD/kW | User defined | 0
43 | MINBIOIN_N | Biomass supply, India – North | 2 | FixedCost | USD/kW/yr | User defined | 0
43 | MINBIOIN_N | Biomass supply, India – North | 3 | ResidualCapacity | GW | User defined | 0
43 | MINBIOIN_N | Biomass supply, India – North | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
43 | MINBIOIN_N | Biomass supply, India – North | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
44 | MINBIOIN_S | Biomass supply, India – South | 1 | CapitalCost | USD/kW | User defined | 0
44 | MINBIOIN_S | Biomass supply, India – South | 2 | FixedCost | USD/kW/yr | User defined | 0
44 | MINBIOIN_S | Biomass supply, India – South | 3 | ResidualCapacity | GW | User defined | 0
44 | MINBIOIN_S | Biomass supply, India – South | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
44 | MINBIOIN_S | Biomass supply, India – South | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
45 | MINBIOIN_E | Biomass supply, India – East | 1 | CapitalCost | USD/kW | User defined | 0
45 | MINBIOIN_E | Biomass supply, India – East | 2 | FixedCost | USD/kW/yr | User defined | 0
45 | MINBIOIN_E | Biomass supply, India – East | 3 | ResidualCapacity | GW | User defined | 0
45 | MINBIOIN_E | Biomass supply, India – East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
45 | MINBIOIN_E | Biomass supply, India – East | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
46 | MINBIOIN_W | Biomass supply, India – West | 1 | CapitalCost | USD/kW | User defined | 0
46 | MINBIOIN_W | Biomass supply, India – West | 2 | FixedCost | USD/kW/yr | User defined | 0
46 | MINBIOIN_W | Biomass supply, India – West | 3 | ResidualCapacity | GW | User defined | 0
46 | MINBIOIN_W | Biomass supply, India – West | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
46 | MINBIOIN_W | Biomass supply, India – West | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
47 | MINBIOIN_NE | Biomass supply, India – Northeast | 1 | CapitalCost | USD/kW | User defined | 0
47 | MINBIOIN_NE | Biomass supply, India – Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0
47 | MINBIOIN_NE | Biomass supply, India – Northeast | 3 | ResidualCapacity | GW | User defined | 0
47 | MINBIOIN_NE | Biomass supply, India – Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
47 | MINBIOIN_NE | Biomass supply, India – Northeast | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
48 | MINBIONP | Biomass supply, Nepal | 1 | CapitalCost | USD/kW | User defined | 0
48 | MINBIONP | Biomass supply, Nepal | 2 | FixedCost | USD/kW/yr | User defined | 0
48 | MINBIONP | Biomass supply, Nepal | 3 | ResidualCapacity | GW | User defined | 0
48 | MINBIONP | Biomass supply, Nepal | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
48 | MINBIONP | Biomass supply, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
49 | MINBIOLK | Biomass supply, Sri Lanka | 1 | CapitalCost | USD/kW | User defined | 0
49 | MINBIOLK | Biomass supply, Sri Lanka | 2 | FixedCost | USD/kW/yr | User defined | 0
49 | MINBIOLK | Biomass supply, Sri Lanka | 3 | ResidualCapacity | GW | User defined | 0
49 | MINBIOLK | Biomass supply, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
49 | MINBIOLK | Biomass supply, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
50 | MINBIOMV | Biomass supply, Maldives | 1 | CapitalCost | USD/kW | User defined | 0
50 | MINBIOMV | Biomass supply, Maldives | 2 | FixedCost | USD/kW/yr | User defined | 0
50 | MINBIOMV | Biomass supply, Maldives | 3 | ResidualCapacity | GW | User defined | 0
50 | MINBIOMV | Biomass supply, Maldives | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
50 | MINBIOMV | Biomass supply, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
51 | MINH2GBD | Green hydrogen production, Bangladesh | 1 | CapitalCost | USD/kW | User defined | 0
51 | MINH2GBD | Green hydrogen production, Bangladesh | 2 | FixedCost | USD/kW/yr | User defined | 0
51 | MINH2GBD | Green hydrogen production, Bangladesh | 3 | ResidualCapacity | GW | User defined | 0
51 | MINH2GBD | Green hydrogen production, Bangladesh | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
51 | MINH2GBD | Green hydrogen production, Bangladesh | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
52 | MINH2GBT | Green hydrogen production, Bhutan | 1 | CapitalCost | USD/kW | User defined | 0
52 | MINH2GBT | Green hydrogen production, Bhutan | 2 | FixedCost | USD/kW/yr | User defined | 0
52 | MINH2GBT | Green hydrogen production, Bhutan | 3 | ResidualCapacity | GW | User defined | 0
52 | MINH2GBT | Green hydrogen production, Bhutan | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
52 | MINH2GBT | Green hydrogen production, Bhutan | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
53 | MINH2GIN_N | Green hydrogen production, India – North | 1 | CapitalCost | USD/kW | User defined | 0
53 | MINH2GIN_N | Green hydrogen production, India – North | 2 | FixedCost | USD/kW/yr | User defined | 0
53 | MINH2GIN_N | Green hydrogen production, India – North | 3 | ResidualCapacity | GW | User defined | 0
53 | MINH2GIN_N | Green hydrogen production, India – North | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
53 | MINH2GIN_N | Green hydrogen production, India – North | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
54 | MINH2GIN_S | Green hydrogen production, India – South | 1 | CapitalCost | USD/kW | User defined | 0
54 | MINH2GIN_S | Green hydrogen production, India – South | 2 | FixedCost | USD/kW/yr | User defined | 0
54 | MINH2GIN_S | Green hydrogen production, India – South | 3 | ResidualCapacity | GW | User defined | 0
54 | MINH2GIN_S | Green hydrogen production, India – South | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
54 | MINH2GIN_S | Green hydrogen production, India – South | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
55 | MINH2GIN_E | Green hydrogen production, India – East | 1 | CapitalCost | USD/kW | User defined | 0
55 | MINH2GIN_E | Green hydrogen production, India – East | 2 | FixedCost | USD/kW/yr | User defined | 0
55 | MINH2GIN_E | Green hydrogen production, India – East | 3 | ResidualCapacity | GW | User defined | 0
55 | MINH2GIN_E | Green hydrogen production, India – East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
55 | MINH2GIN_E | Green hydrogen production, India – East | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
56 | MINH2GIN_W | Green hydrogen production, India – West | 1 | CapitalCost | USD/kW | User defined | 0
56 | MINH2GIN_W | Green hydrogen production, India – West | 2 | FixedCost | USD/kW/yr | User defined | 0
56 | MINH2GIN_W | Green hydrogen production, India – West | 3 | ResidualCapacity | GW | User defined | 0
56 | MINH2GIN_W | Green hydrogen production, India – West | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
56 | MINH2GIN_W | Green hydrogen production, India – West | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
57 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 1 | CapitalCost | USD/kW | User defined | 0
57 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0
57 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 3 | ResidualCapacity | GW | User defined | 0
57 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
57 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
58 | MINH2GNP | Green hydrogen production, Nepal | 1 | CapitalCost | USD/kW | User defined | 0
58 | MINH2GNP | Green hydrogen production, Nepal | 2 | FixedCost | USD/kW/yr | User defined | 0
58 | MINH2GNP | Green hydrogen production, Nepal | 3 | ResidualCapacity | GW | User defined | 0
58 | MINH2GNP | Green hydrogen production, Nepal | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
58 | MINH2GNP | Green hydrogen production, Nepal | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
59 | MINH2GLK | Green hydrogen production, Sri Lanka | 1 | CapitalCost | USD/kW | User defined | 0
59 | MINH2GLK | Green hydrogen production, Sri Lanka | 2 | FixedCost | USD/kW/yr | User defined | 0
59 | MINH2GLK | Green hydrogen production, Sri Lanka | 3 | ResidualCapacity | GW | User defined | 0
59 | MINH2GLK | Green hydrogen production, Sri Lanka | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
59 | MINH2GLK | Green hydrogen production, Sri Lanka | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
60 | MINH2GMV | Green hydrogen production, Maldives | 1 | CapitalCost | USD/kW | User defined | 0
60 | MINH2GMV | Green hydrogen production, Maldives | 2 | FixedCost | USD/kW/yr | User defined | 0
60 | MINH2GMV | Green hydrogen production, Maldives | 3 | ResidualCapacity | GW | User defined | 0
60 | MINH2GMV | Green hydrogen production, Maldives | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
60 | MINH2GMV | Green hydrogen production, Maldives | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0

## Secondary_Techs
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 840 | 822 | 804 | 785.4 | 766.8 | 748.2 | 729.6 | 711 | 692.7 | 674.4 | 656.1 | 637.8 | 619.5 | 609.3 | 599.1 | 588.9 | 578.7 | 568.5 | 558.3 | 548.1 | 537.9 | 527.7 | 517.5 | 507.3 | 497.1 | 486.9 | 476.7 | 466.5
1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 12 | 12 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 10.5 | 10.2 | 9.9 | 9.6 | 9.3 | 9 | 9 | 9 | 9 | 9 | 9 | 8.7 | 8.4 | 8.1 | 7.8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1008 | 986.4 | 964.8 | 942.48 | 920.16 | 897.84 | 875.52 | 853.2 | 831.24 | 809.28 | 787.32 | 765.36 | 743.4 | 731.16 | 718.92 | 706.68 | 694.44 | 682.2 | 669.96 | 657.72 | 645.48 | 633.24 | 621 | 608.76 | 596.52 | 584.28 | 572.04 | 559.8
2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 14.4 | 14.4 | 14.4 | 14.04 | 13.68 | 13.32 | 12.96 | 12.6 | 12.24 | 11.88 | 11.52 | 11.16 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.44 | 10.08 | 9.72 | 9.36 | 9 | 9 | 9 | 9 | 9 | 9
2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 560 | 548 | 536 | 523.6 | 511.2 | 498.8 | 486.4 | 474 | 461.8 | 449.6 | 437.4 | 425.2 | 413 | 406.2 | 399.4 | 392.6 | 385.8 | 379 | 372.2 | 365.4 | 358.6 | 351.8 | 345 | 338.2 | 331.4 | 324.6 | 317.8 | 311
7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8 | 8 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6 | 5.8 | 5.6 | 5.4 | 5.2 | 5 | 5 | 5 | 5 | 5 | 5
7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 896 | 876.8 | 857.6 | 837.76 | 817.92 | 798.08 | 778.24 | 758.4 | 738.88 | 719.36 | 699.84 | 680.32 | 660.8 | 649.92 | 639.04 | 628.16 | 617.28 | 606.4 | 595.52 | 584.64 | 573.76 | 562.88 | 552 | 541.12 | 530.24 | 519.36 | 508.48 | 497.6
8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 12.8 | 12.8 | 12.8 | 12.48 | 12.16 | 11.84 | 11.52 | 11.2 | 10.88 | 10.56 | 10.24 | 9.92 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.28 | 8.96 | 8.64 | 8.32 | 8 | 8 | 8 | 8 | 8 | 8
8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 849 | 830.81 | 812.61 | 793.82 | 775.02 | 756.22 | 737.42 | 718.62 | 700.12 | 681.63 | 663.13 | 644.63 | 626.14 | 615.83 | 605.52 | 595.21 | 584.9 | 574.59 | 564.28 | 553.97 | 543.66 | 533.35 | 523.04 | 512.74 | 502.43 | 492.12 | 481.81 | 471.5
9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 12 | 12 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 10.5 | 10.2 | 9.9 | 9.6 | 9.3 | 9 | 9 | 9 | 9 | 9 | 9 | 8.7 | 8.4 | 8.1 | 7.8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1680 | 1644 | 1608 | 1570.8 | 1533.6 | 1496.4 | 1459.2 | 1422 | 1385.4 | 1348.8 | 1312.2 | 1275.6 | 1239 | 1218.6 | 1198.2 | 1177.8 | 1157.4 | 1137 | 1116.6 | 1096.2 | 1075.8 | 1055.4 | 1035 | 1014.6 | 994.2 | 973.8 | 953.4 | 933
10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 24 | 24 | 24 | 23.4 | 22.8 | 22.2 | 21.6 | 21 | 20.4 | 19.8 | 19.2 | 18.6 | 18 | 18 | 18 | 18 | 18 | 18 | 17.4 | 16.8 | 16.2 | 15.6 | 15 | 15 | 15 | 15 | 15 | 15
10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1275 | 1247.25 | 1219.5 | 1191.6 | 1163.7 | 1135.8 | 1107.9 | 1080 | 1052.1 | 1024.2 | 996.3 | 968.4 | 940.5 | 925.2 | 909.9 | 894.6 | 879.3 | 864 | 848.4 | 832.8 | 817.2 | 801.6 | 786 | 770.4 | 754.8 | 739.2 | 723.6 | 708
11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 13.5 | 13.5 | 13.5 | 13.2 | 12.9 | 12.6 | 12.3 | 12 | 11.7 | 11.4 | 11.1 | 10.8 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.2 | 9.9 | 9.6 | 9.3 | 9 | 9 | 9 | 9 | 9 | 9
11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1530 | 1496.7 | 1463.4 | 1429.92 | 1396.44 | 1362.96 | 1329.48 | 1296 | 1262.52 | 1229.04 | 1195.56 | 1162.08 | 1128.6 | 1110.24 | 1091.88 | 1073.52 | 1055.16 | 1036.8 | 1018.08 | 999.36 | 980.64 | 961.92 | 943.2 | 924.48 | 905.76 | 887.04 | 868.32 | 849.6
12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 16.2 | 16.2 | 16.2 | 15.84 | 15.48 | 15.12 | 14.76 | 14.4 | 14.04 | 13.68 | 13.32 | 12.96 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.24 | 11.88 | 11.52 | 11.16 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 850 | 831.5 | 813 | 794.4 | 775.8 | 757.2 | 738.6 | 720 | 701.4 | 682.8 | 664.2 | 645.6 | 627 | 616.8 | 606.6 | 596.4 | 586.2 | 576 | 565.6 | 555.2 | 544.8 | 534.4 | 524 | 513.6 | 503.2 | 492.8 | 482.4 | 472
13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 9 | 9 | 9 | 8.8 | 8.6 | 8.4 | 8.2 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 7 | 7 | 7 | 7 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6
13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 850 | 831.5 | 813 | 794.4 | 775.8 | 757.2 | 738.6 | 720 | 701.4 | 682.8 | 664.2 | 645.6 | 627 | 616.8 | 606.6 | 596.4 | 586.2 | 576 | 565.6 | 555.2 | 544.8 | 534.4 | 524 | 513.6 | 503.2 | 492.8 | 482.4 | 472
14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 9 | 9 | 9 | 8.8 | 8.6 | 8.4 | 8.2 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 7 | 7 | 7 | 7 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6
14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 850 | 831.5 | 813 | 794.4 | 775.8 | 757.2 | 738.6 | 720 | 701.4 | 682.8 | 664.2 | 645.6 | 627 | 616.8 | 606.6 | 596.4 | 586.2 | 576 | 565.6 | 555.2 | 544.8 | 534.4 | 524 | 513.6 | 503.2 | 492.8 | 482.4 | 472
15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 9 | 9 | 9 | 8.8 | 8.6 | 8.4 | 8.2 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 7 | 7 | 7 | 7 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6
15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 850 | 831.5 | 813 | 794.4 | 775.8 | 757.2 | 738.6 | 720 | 701.4 | 682.8 | 664.2 | 645.6 | 627 | 616.8 | 606.6 | 596.4 | 586.2 | 576 | 565.6 | 555.2 | 544.8 | 534.4 | 524 | 513.6 | 503.2 | 492.8 | 482.4 | 472
16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 9 | 9 | 9 | 8.8 | 8.6 | 8.4 | 8.2 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 7 | 7 | 7 | 7 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6
16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 850 | 831.5 | 813 | 794.4 | 775.8 | 757.2 | 738.6 | 720 | 701.4 | 682.8 | 664.2 | 645.6 | 627 | 616.8 | 606.6 | 596.4 | 586.2 | 576 | 565.6 | 555.2 | 544.8 | 534.4 | 524 | 513.6 | 503.2 | 492.8 | 482.4 | 472
17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 9 | 9 | 9 | 8.8 | 8.6 | 8.4 | 8.2 | 8 | 7.8 | 7.6 | 7.4 | 7.2 | 7 | 7 | 7 | 7 | 7 | 7 | 6.8 | 6.6 | 6.4 | 6.2 | 6 | 6 | 6 | 6 | 6 | 6
17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1360 | 1330.4 | 1300.8 | 1271.04 | 1241.28 | 1211.52 | 1181.76 | 1152 | 1122.24 | 1092.48 | 1062.72 | 1032.96 | 1003.2 | 986.88 | 970.56 | 954.24 | 937.92 | 921.6 | 904.96 | 888.32 | 871.68 | 855.04 | 838.4 | 821.76 | 805.12 | 788.48 | 771.84 | 755.2
18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 14.4 | 14.4 | 14.4 | 14.08 | 13.76 | 13.44 | 13.12 | 12.8 | 12.48 | 12.16 | 11.84 | 11.52 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 10.88 | 10.56 | 10.24 | 9.92 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 982 | 960.63 | 939.25 | 917.77 | 896.28 | 874.79 | 853.3 | 831.81 | 810.32 | 788.83 | 767.35 | 745.86 | 724.37 | 712.59 | 700.8 | 689.02 | 677.23 | 665.45 | 653.43 | 641.42 | 629.4 | 617.39 | 605.37 | 593.36 | 581.34 | 569.33 | 557.31 | 545.3
19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 10.8 | 10.8 | 10.8 | 10.56 | 10.32 | 10.08 | 9.84 | 9.6 | 9.36 | 9.12 | 8.88 | 8.64 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.16 | 7.92 | 7.68 | 7.44 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2550 | 2494.5 | 2439 | 2383.2 | 2327.4 | 2271.6 | 2215.8 | 2160 | 2104.2 | 2048.4 | 1992.6 | 1936.8 | 1881 | 1850.4 | 1819.8 | 1789.2 | 1758.6 | 1728 | 1696.8 | 1665.6 | 1634.4 | 1603.2 | 1572 | 1540.8 | 1509.6 | 1478.4 | 1447.2 | 1416
20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 27 | 27 | 27 | 26.4 | 25.8 | 25.2 | 24.6 | 24 | 23.4 | 22.8 | 22.2 | 21.6 | 21 | 21 | 21 | 21 | 21 | 21 | 20.4 | 19.8 | 19.2 | 18.6 | 18 | 18 | 18 | 18 | 18 | 18
20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912
21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849 | 51.849
21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912
22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575 | 48.575
22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912
23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385 | 40.385
23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912
24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671 | 84.671
24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912
25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912
26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1218 | 1158.78 | 1099.56 | 1091.88 | 1084.2 | 1076.51 | 1068.83 | 1061.15 | 1053.79 | 1046.42 | 1039.06 | 1031.7 | 1024.34 | 1016.97 | 1009.61 | 1002.25 | 994.89 | 987.52 | 980.16 | 972.8 | 965.44 | 958.07 | 950.71 | 943.03 | 935.35 | 927.66 | 919.98 | 912.3
27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 35.2 | 35.2 | 35.2 | 34.88 | 34.56 | 34.24 | 33.92 | 33.6 | 33.28 | 32.96 | 32.64 | 32.32 | 32 | 32 | 32 | 32 | 32 | 32 | 31.68 | 31.36 | 31.04 | 30.72 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4
27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002
27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 761 | 724 | 687 | 682.2 | 677.4 | 672.6 | 667.8 | 663 | 658.4 | 653.8 | 649.2 | 644.6 | 640 | 635.4 | 630.8 | 626.2 | 621.6 | 617 | 612.4 | 607.8 | 603.2 | 598.6 | 594 | 589.2 | 584.4 | 579.6 | 574.8 | 570
33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 22 | 22 | 22 | 21.8 | 21.6 | 21.4 | 21.2 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 19.8 | 19.6 | 19.4 | 19.2 | 19 | 19 | 19 | 19 | 19 | 19
33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1391 | 1323.37 | 1255.74 | 1246.96 | 1238.19 | 1229.42 | 1220.64 | 1211.87 | 1203.46 | 1195.05 | 1186.65 | 1178.24 | 1169.83 | 1161.42 | 1153.01 | 1144.6 | 1136.2 | 1127.79 | 1119.38 | 1110.97 | 1102.56 | 1094.16 | 1085.75 | 1076.97 | 1068.2 | 1059.43 | 1050.65 | 1041.88
35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 39.6 | 39.6 | 39.6 | 39.24 | 38.88 | 38.52 | 38.16 | 37.8 | 37.44 | 37.08 | 36.72 | 36.36 | 36 | 36 | 36 | 36 | 36 | 36 | 35.64 | 35.28 | 34.92 | 34.56 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2
35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128 | 0.128
35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | bar: 2023 to 2050
36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3800 | 3784 | 3768 | 3702.8 | 3637.6 | 3572.4 | 3507.2 | 3442 | 3156.4 | 2870.8 | 2585.2 | 2299.6 | 2014 | 2003.2 | 1992.4 | 1981.6 | 1970.8 | 1960 | 1951.8 | 1943.6 | 1935.4 | 1927.2 | 1919 | 1912.4 | 1905.8 | 1899.2 | 1892.6 | 1886
37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114 | 114 | 114 | 112.2 | 110.4 | 108.6 | 106.8 | 105 | 103.4 | 101.8 | 100.2 | 98.6 | 97 | 95.6 | 94.2 | 92.8 | 91.4 | 90 | 88.8 | 87.6 | 86.4 | 85.2 | 84 | 83.2 | 82.4 | 81.6 | 80.8 | 80
37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3800 | 3784 | 3768 | 3702.8 | 3637.6 | 3572.4 | 3507.2 | 3442 | 3156.4 | 2870.8 | 2585.2 | 2299.6 | 2014 | 2003.2 | 1992.4 | 1981.6 | 1970.8 | 1960 | 1951.8 | 1943.6 | 1935.4 | 1927.2 | 1919 | 1912.4 | 1905.8 | 1899.2 | 1892.6 | 1886
38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114 | 114 | 114 | 112.2 | 110.4 | 108.6 | 106.8 | 105 | 103.4 | 101.8 | 100.2 | 98.6 | 97 | 95.6 | 94.2 | 92.8 | 91.4 | 90 | 88.8 | 87.6 | 86.4 | 85.2 | 84 | 83.2 | 82.4 | 81.6 | 80.8 | 80
38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3800 | 3784 | 3768 | 3702.8 | 3637.6 | 3572.4 | 3507.2 | 3442 | 3156.4 | 2870.8 | 2585.2 | 2299.6 | 2014 | 2003.2 | 1992.4 | 1981.6 | 1970.8 | 1960 | 1951.8 | 1943.6 | 1935.4 | 1927.2 | 1919 | 1912.4 | 1905.8 | 1899.2 | 1892.6 | 1886
39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114 | 114 | 114 | 112.2 | 110.4 | 108.6 | 106.8 | 105 | 103.4 | 101.8 | 100.2 | 98.6 | 97 | 95.6 | 94.2 | 92.8 | 91.4 | 90 | 88.8 | 87.6 | 86.4 | 85.2 | 84 | 83.2 | 82.4 | 81.6 | 80.8 | 80
39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 6142.71 | 6116.85 | 6090.98 | 5985.59 | 5880.19 | 5774.79 | 5669.4 | 5564 | 5102.33 | 4640.66 | 4178.98 | 3717.31 | 3255.64 | 3238.18 | 3220.72 | 3203.26 | 3185.8 | 3168.35 | 3155.09 | 3141.83 | 3128.58 | 3115.32 | 3102.07 | 3091.4 | 3080.73 | 3070.06 | 3059.39 | 3048.72
41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 182.4 | 182.4 | 182.4 | 179.52 | 176.64 | 173.76 | 170.88 | 168 | 165.44 | 162.88 | 160.32 | 157.76 | 155.2 | 152.96 | 150.72 | 148.48 | 146.24 | 144 | 142.08 | 140.16 | 138.24 | 136.32 | 134.4 | 133.12 | 131.84 | 130.56 | 129.28 | 128
41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0
42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0
42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0
42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 4601.67 | 4647.68 | 4693.7 | 4721.31 | 4748.92 | 4776.53 | 4804.14 | 4831.75 | 4859.36 | 4886.97 | 4914.58 | 4942.19 | 4969.8 | 4997.41 | 5025.02 | 5052.63 | 5080.24 | 5107.85 | 5135.46 | 5163.07 | 5190.68 | 5218.29 | 5245.9 | 5273.51 | 5301.12 | 5328.73 | 5356.34 | 5383.95
43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4 | 68.4
43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0
43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | bar: 2023 to 2050
44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2000 | 2020 | 2040 | 2052 | 2064 | 2076 | 2088 | 2100 | 2112 | 2124 | 2136 | 2148 | 2160 | 2172 | 2184 | 2196 | 2208 | 2220 | 2232 | 2244 | 2256 | 2268 | 2280 | 2292 | 2304 | 2316 | 2328 | 2340
44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.4
44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2500 | 2525 | 2550 | 2565 | 2580 | 2595 | 2610 | 2625 | 2640 | 2655 | 2670 | 2685 | 2700 | 2715 | 2730 | 2745 | 2760 | 2775 | 2790 | 2805 | 2820 | 2835 | 2850 | 2865 | 2880 | 2895 | 2910 | 2925
45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664 | 21.664
45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2500 | 2525 | 2550 | 2565 | 2580 | 2595 | 2610 | 2625 | 2640 | 2655 | 2670 | 2685 | 2700 | 2715 | 2730 | 2745 | 2760 | 2775 | 2790 | 2805 | 2820 | 2835 | 2850 | 2865 | 2880 | 2895 | 2910 | 2925
46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273 | 2.273
46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2500 | 2525 | 2550 | 2565 | 2580 | 2595 | 2610 | 2625 | 2640 | 2655 | 2670 | 2685 | 2700 | 2715 | 2730 | 2745 | 2760 | 2775 | 2790 | 2805 | 2820 | 2835 | 2850 | 2865 | 2880 | 2895 | 2910 | 2925
47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988 | 5.988
47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 4166.67 | 4208.33 | 4250 | 4275 | 4300 | 4325 | 4350 | 4375 | 4400 | 4425 | 4450 | 4475 | 4500 | 4525 | 4550 | 4575 | 4600 | 4625 | 4650 | 4675 | 4700 | 4725 | 4750 | 4775 | 4800 | 4825 | 4850 | 4875
48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 64.6
48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384 | 1.384
48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2153.85 | 2175.38 | 2196.92 | 2218.58 | 2240.25 | 2261.91 | 2283.57 | 2305.23 | 2326.65 | 2348.06 | 2369.48 | 2390.89 | 2412.31 | 2433.97 | 2455.63 | 2477.29 | 2498.95 | 2520.62 | 2542.03 | 2563.45 | 2584.86 | 2606.28 | 2627.69 | 2649.35 | 2671.02 | 2692.68 | 2714.34 | 2736
49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1480.77 | 1495.58 | 1510.38 | 1525.28 | 1540.17 | 1555.06 | 1569.95 | 1584.85 | 1599.57 | 1614.29 | 1629.02 | 1643.74 | 1658.46 | 1673.35 | 1688.25 | 1703.14 | 1718.03 | 1732.92 | 1747.65 | 1762.37 | 1777.09 | 1791.82 | 1806.54 | 1821.43 | 1836.32 | 1851.22 | 1866.11 | 1881
50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75 | 29.75
50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452 | 1.452
50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1750 | 1767.5 | 1785 | 1802.6 | 1820.2 | 1837.8 | 1855.4 | 1873 | 1890.4 | 1907.8 | 1925.2 | 1942.6 | 1960 | 1977.6 | 1995.2 | 2012.8 | 2030.4 | 2048 | 2065.4 | 2082.8 | 2100.2 | 2117.6 | 2135 | 2152.6 | 2170.2 | 2187.8 | 2205.4 | 2223
51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565 | 1.565
51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1750 | 1767.5 | 1785 | 1802.6 | 1820.2 | 1837.8 | 1855.4 | 1873 | 1890.4 | 1907.8 | 1925.2 | 1942.6 | 1960 | 1977.6 | 1995.2 | 2012.8 | 2030.4 | 2048 | 2065.4 | 2082.8 | 2100.2 | 2117.6 | 2135 | 2152.6 | 2170.2 | 2187.8 | 2205.4 | 2223
52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254 | 0.254
52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7
55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0: 0
56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0: 0
57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415 | 0.415
57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21 | 3359.21
58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
58 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100
59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
59 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100
60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
60 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100
61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
61 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100
62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
62 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76 | 4227.76
63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
63 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250
64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
64 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250
65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
65 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250
66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
66 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250
67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
67 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430 | 1430
68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96 | 14.96
68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
68 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300
69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6
69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
69 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300
70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6
70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
70 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300
71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6
71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
71 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300
72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6
72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
72 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300
73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6
73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
73 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0: 0
74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
74 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29 | 2414.29
75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84 | 25.84
75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
75 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396 | 396
76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47 | 8.47
76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
76 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712 | 5.712
77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
77 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346 | 3.346
78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
78 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
79 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399 | 9.399
80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
80 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360
81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665 | 1.665
81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
81 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0: 0
82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
82 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288
83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16 | 6.16
83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
83 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
84 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100
85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9
85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
85 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57 | 1428.57
86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
86 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0: 0
87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
87 | PWRBIOBDXX01 | Biomass/Bagasse, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
88 | PWRBIOIN_NXX01 | Biomass/Bagasse, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781 | 3.781
89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
89 | PWRBIOIN_SXX01 | Biomass/Bagasse, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576 | 0.576
90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
90 | PWRBIOIN_EXX01 | Biomass/Bagasse, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571 | 3.571
91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
91 | PWRBIOIN_WXX01 | Biomass/Bagasse, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782
92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3
92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016
92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
92 | PWRBIOIN_NEXX01 | Biomass/Bagasse, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0: 0
93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
93 | PWRBIONPXX01 | Biomass/Bagasse, Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67 | 2780.67
94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08 | 114.08
94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
94 | PWRBIOLKXX01 | Biomass/Bagasse, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
95 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
96 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
97 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
98 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
99 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
100 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
101 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22 | 2.22
102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
102 | PWRURNIN_NXX01 | Nuclear, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32 | 3.32
103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
103 | PWRURNIN_SXX01 | Nuclear, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
104 | PWRURNIN_EXX01 | Nuclear, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24 | 3.24
105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
105 | PWRURNIN_WXX01 | Nuclear, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103
106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
106 | PWRURNIN_NEXX01 | Nuclear, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8 | 13267.8
107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4 | 348.4
107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
107 | PWRURNBDXX01 | Nuclear, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 4589 | 4566.5 | 4544 | 4522 | 4500 | 4478 | 4456 | 4434 | 4412.6 | 4391.2 | 4369.8 | 4348.4 | 4327 | 4306 | 4285 | 4264 | 4243 | 4222 | 4201.6 | 4181.2 | 4160.8 | 4140.4 | 4120 | 4100 | 4080 | 4060 | 4040 | 4020
108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
108 | PWRGEOIN_NXX01 | Geothermal, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 24 | 24.6 | 25.2 | 24.24 | 23.28 | 22.32 | 21.36 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.16 | 19.92 | 19.68 | 19.44 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 18.96 | 18.72 | 18.48 | 18.24 | 18
109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 28 | 28.7 | 29.4 | 28.28 | 27.16 | 26.04 | 24.92 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.52 | 23.24 | 22.96 | 22.68 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.12 | 21.84 | 21.56 | 21.28 | 21
110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
110 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
111 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
112 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
113 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 20 | 20.5 | 21 | 20.2 | 19.4 | 18.6 | 17.8 | 17 | 17 | 17 | 17 | 17 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 16 | 16 | 16 | 16 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15
115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
115 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 26 | 26.65 | 27.3 | 26.26 | 25.22 | 24.18 | 23.14 | 22.1 | 22.1 | 22.1 | 22.1 | 22.1 | 22.1 | 21.84 | 21.58 | 21.32 | 21.06 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.54 | 20.28 | 20.02 | 19.76 | 19.5
116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
116 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 30 | 30.75 | 31.5 | 30.3 | 29.1 | 27.9 | 26.7 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.2 | 24.9 | 24.6 | 24.3 | 24 | 24 | 24 | 24 | 24 | 24 | 23.7 | 23.4 | 23.1 | 22.8 | 22.5
117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
117 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 30 | 30.75 | 31.5 | 30.3 | 29.1 | 27.9 | 26.7 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.2 | 24.9 | 24.6 | 24.3 | 24 | 24 | 24 | 24 | 24 | 24 | 23.7 | 23.4 | 23.1 | 22.8 | 22.5
118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
118 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
119 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
120 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
121 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
122 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
123 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
124 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
125 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
126 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
127 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0: 0
128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 45 | 46 | 47 | 45.2 | 43.4 | 41.6 | 39.8 | 38 | 37.8 | 37.6 | 37.4 | 37.2 | 37 | 36.6 | 36.2 | 35.8 | 35.4 | 35 | 34.8 | 34.6 | 34.4 | 34.2 | 34 | 33.8 | 33.6 | 33.4 | 33.2 | 33
128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1244 | 1217 | 1190 | 1162.8 | 1135.6 | 1108.4 | 1081.2 | 1054 | 1026.8 | 999.6 | 972.4 | 945.2 | 918 | 902.8 | 887.6 | 872.4 | 857.2 | 842 | 827 | 812 | 797 | 782 | 767 | 751.8 | 736.6 | 721.4 | 706.2 | 691
129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 19 | 18.5 | 18 | 17.8 | 17.6 | 17.4 | 17.2 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15 | 14.8 | 14.6 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.4 | 13.2 | 13
129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
129 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1244 | 1217 | 1190 | 1162.8 | 1135.6 | 1108.4 | 1081.2 | 1054 | 1026.8 | 999.6 | 972.4 | 945.2 | 918 | 902.8 | 887.6 | 872.4 | 857.2 | 842 | 827 | 812 | 797 | 782 | 767 | 751.8 | 736.6 | 721.4 | 706.2 | 691
130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 19 | 18.5 | 18 | 17.8 | 17.6 | 17.4 | 17.2 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15 | 14.8 | 14.6 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.4 | 13.2 | 13
130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
130 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1244 | 1217 | 1190 | 1162.8 | 1135.6 | 1108.4 | 1081.2 | 1054 | 1026.8 | 999.6 | 972.4 | 945.2 | 918 | 902.8 | 887.6 | 872.4 | 857.2 | 842 | 827 | 812 | 797 | 782 | 767 | 751.8 | 736.6 | 721.4 | 706.2 | 691
131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 19 | 18.5 | 18 | 17.8 | 17.6 | 17.4 | 17.2 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15 | 14.8 | 14.6 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.4 | 13.2 | 13
131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
131 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1244 | 1217 | 1190 | 1162.8 | 1135.6 | 1108.4 | 1081.2 | 1054 | 1026.8 | 999.6 | 972.4 | 945.2 | 918 | 902.8 | 887.6 | 872.4 | 857.2 | 842 | 827 | 812 | 797 | 782 | 767 | 751.8 | 736.6 | 721.4 | 706.2 | 691
132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 19 | 18.5 | 18 | 17.8 | 17.6 | 17.4 | 17.2 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15 | 14.8 | 14.6 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.4 | 13.2 | 13
132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
132 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1244 | 1217 | 1190 | 1162.8 | 1135.6 | 1108.4 | 1081.2 | 1054 | 1026.8 | 999.6 | 972.4 | 945.2 | 918 | 902.8 | 887.6 | 872.4 | 857.2 | 842 | 827 | 812 | 797 | 782 | 767 | 751.8 | 736.6 | 721.4 | 706.2 | 691
133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 19 | 18.5 | 18 | 17.8 | 17.6 | 17.4 | 17.2 | 17 | 16.8 | 16.6 | 16.4 | 16.2 | 16 | 15.8 | 15.6 | 15.4 | 15.2 | 15 | 14.8 | 14.6 | 14.4 | 14.2 | 14 | 13.8 | 13.6 | 13.4 | 13.2 | 13
133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
133 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2200 | 2150 | 2100 | 2040 | 1980 | 1920 | 1860 | 1800 | 1740 | 1680 | 1620 | 1560 | 1500 | 1460 | 1420 | 1380 | 1340 | 1300 | 1260 | 1220 | 1180 | 1140 | 1100 | 1080 | 1060 | 1040 | 1020 | 1000
134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 66 | 64.5 | 63 | 61.2 | 59.4 | 57.6 | 55.8 | 54 | 52.2 | 50.4 | 48.6 | 46.8 | 45 | 43.8 | 42.6 | 41.4 | 40.2 | 39 | 37.8 | 36.6 | 35.4 | 34.2 | 33 | 32.4 | 31.8 | 31.2 | 30.6 | 30
134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
134 | PWRH2GIN_NXX01 | Green Hydrogen Fuel Cell, India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2200 | 2150 | 2100 | 2040 | 1980 | 1920 | 1860 | 1800 | 1740 | 1680 | 1620 | 1560 | 1500 | 1460 | 1420 | 1380 | 1340 | 1300 | 1260 | 1220 | 1180 | 1140 | 1100 | 1080 | 1060 | 1040 | 1020 | 1000
135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 66 | 64.5 | 63 | 61.2 | 59.4 | 57.6 | 55.8 | 54 | 52.2 | 50.4 | 48.6 | 46.8 | 45 | 43.8 | 42.6 | 41.4 | 40.2 | 39 | 37.8 | 36.6 | 35.4 | 34.2 | 33 | 32.4 | 31.8 | 31.2 | 30.6 | 30
135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
135 | PWRH2GIN_SXX01 | Green Hydrogen Fuel Cell, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2200 | 2150 | 2100 | 2040 | 1980 | 1920 | 1860 | 1800 | 1740 | 1680 | 1620 | 1560 | 1500 | 1460 | 1420 | 1380 | 1340 | 1300 | 1260 | 1220 | 1180 | 1140 | 1100 | 1080 | 1060 | 1040 | 1020 | 1000
136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 66 | 64.5 | 63 | 61.2 | 59.4 | 57.6 | 55.8 | 54 | 52.2 | 50.4 | 48.6 | 46.8 | 45 | 43.8 | 42.6 | 41.4 | 40.2 | 39 | 37.8 | 36.6 | 35.4 | 34.2 | 33 | 32.4 | 31.8 | 31.2 | 30.6 | 30
136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
136 | PWRH2GIN_EXX01 | Green Hydrogen Fuel Cell, India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2200 | 2150 | 2100 | 2040 | 1980 | 1920 | 1860 | 1800 | 1740 | 1680 | 1620 | 1560 | 1500 | 1460 | 1420 | 1380 | 1340 | 1300 | 1260 | 1220 | 1180 | 1140 | 1100 | 1080 | 1060 | 1040 | 1020 | 1000
137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 66 | 64.5 | 63 | 61.2 | 59.4 | 57.6 | 55.8 | 54 | 52.2 | 50.4 | 48.6 | 46.8 | 45 | 43.8 | 42.6 | 41.4 | 40.2 | 39 | 37.8 | 36.6 | 35.4 | 34.2 | 33 | 32.4 | 31.8 | 31.2 | 30.6 | 30
137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
137 | PWRH2GIN_WXX01 | Green Hydrogen Fuel Cell, India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 2200 | 2150 | 2100 | 2040 | 1980 | 1920 | 1860 | 1800 | 1740 | 1680 | 1620 | 1560 | 1500 | 1460 | 1420 | 1380 | 1340 | 1300 | 1260 | 1220 | 1180 | 1140 | 1100 | 1080 | 1060 | 1040 | 1020 | 1000
138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 66 | 64.5 | 63 | 61.2 | 59.4 | 57.6 | 55.8 | 54 | 52.2 | 50.4 | 48.6 | 46.8 | 45 | 43.8 | 42.6 | 41.4 | 40.2 | 39 | 37.8 | 36.6 | 35.4 | 34.2 | 33 | 32.4 | 31.8 | 31.2 | 30.6 | 30
138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
138 | PWRH2GIN_NEXX01 | Green Hydrogen Fuel Cell, India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
139 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
140 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
141 | PWRBCKBDXX01 | Backstop (penalty generator), Bangladesh, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | PWRBCKBTXX01 | Backstop (penalty generator), Bhutan, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
143 | PWRBCKIN_NXX01 | Backstop (penalty generator), India – North, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
144 | PWRBCKIN_SXX01 | Backstop (penalty generator), India – South, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
145 | PWRBCKIN_EXX01 | Backstop (penalty generator), India – East, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
146 | PWRBCKIN_WXX01 | Backstop (penalty generator), India – West, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
147 | PWRBCKIN_NEXX01 | Backstop (penalty generator), India – Northeast, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
148 | PWRBCKNPXX01 | Backstop (penalty generator), Nepal, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
149 | PWRBCKLKXX01 | Backstop (penalty generator), Sri Lanka, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 1 | CapitalCost | USD/kW | User defined | 0 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000
150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 3 | ResidualCapacity | GW | User defined | 0: 0
150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0: 0
150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0: 0
150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 6 | TotalAnnualMinCapacity | GW | User defined | 0: 0
150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 7 | AvailabilityFactor | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
150 | PWRBCKMVXX01 | Backstop (penalty generator), Maldives, region XX (investable) | 8 | Efficiency | fraction | User defined | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Note on I2: CostDB PWRSPV CAPEX (Conservative) ¦ BD=$840/kW (×1.5)
Note on I3: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I4: ResidualCapacity (GW): BGD solar ~750 MW. Source: BPDB 2024; Bangladesh_Power_Sector.xlsx ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I8: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I9: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I10: CostDB PWRSPV CAPEX (Conservative) ¦ BT=$1008/kW (×1.8)
Note on I11: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I12: ResidualCapacity (GW): BTN solar ~1 MW (negligible). Source: BPC ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I16: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I17: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I18: CostDB PWRSPV CAPEX (Conservative) ¦ IN base=$560/kW
Note on I19: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I20: ResidualCapacity (GW): IND North solar ~22 GW. Source: CEA Monthly RE Installed Capacity ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I24: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I25: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I26: CostDB PWRSPV CAPEX (Conservative) ¦ IN base=$560/kW
Note on I27: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I28: ResidualCapacity (GW): IND South solar ~25 GW. Source: CEA Monthly RE Installed Capacity ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I32: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I33: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I34: CostDB PWRSPV CAPEX (Conservative) ¦ IN base=$560/kW
Note on I35: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I36: ResidualCapacity (GW): IND East solar ~5 GW. Source: CEA Monthly RE Installed Capacity ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I40: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I41: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I42: CostDB PWRSPV CAPEX (Conservative) ¦ IN base=$560/kW
Note on I43: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I44: ResidualCapacity (GW): IND West solar ~28 GW (Rajasthan+Gujarat). Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I48: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I49: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I50: CostDB PWRSPV CAPEX (Conservative) ¦ IN base=$560/kW
Note on I51: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I52: ResidualCapacity (GW): IND NE solar ~0.5 GW. Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I56: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I57: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I58: CostDB PWRSPV CAPEX (Conservative) ¦ NP=$896/kW (×1.6)
Note on I59: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I60: ResidualCapacity (GW): NPL solar ~50 MW. Source: NEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I64: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I65: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I66: CostDB PWRSPV CAPEX (Conservative) ¦ LK=$849/kW (×1.5)
Note on I67: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I68: ResidualCapacity (GW): LKA grid-scale solar 200 MW. Source: CEB Statistical Digest 2023 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I72: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I73: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I74: CostDB PWRSPV CAPEX (Conservative) ¦ MV=$1680/kW (×3.0)
Note on I75: CostDB PWRSPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I76: ResidualCapacity (GW): MDV solar ~20 MW. Source: IRENA 2023; Maldives Energy Roadmap 2024-2033 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I80: AvailabilityFactor=1.0 PWRSPV standard availability factor
Note on I81: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I82: CostDB PWRSPR CAPEX (Conservative) ¦ BD=$1275/kW (×1.5)
Note on I83: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I88: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I89: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I90: CostDB PWRSPR CAPEX (Conservative) ¦ BT=$1530/kW (×1.8)
Note on I91: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I96: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I97: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I98: CostDB PWRSPR CAPEX (Conservative) ¦ IN base=$850/kW
Note on I99: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I104: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I105: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I106: CostDB PWRSPR CAPEX (Conservative) ¦ IN base=$850/kW
Note on I107: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I112: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I113: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I114: CostDB PWRSPR CAPEX (Conservative) ¦ IN base=$850/kW
Note on I115: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I120: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I121: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I122: CostDB PWRSPR CAPEX (Conservative) ¦ IN base=$850/kW
Note on I123: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I128: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I129: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I130: CostDB PWRSPR CAPEX (Conservative) ¦ IN base=$850/kW
Note on I131: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I136: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I137: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I138: CostDB PWRSPR CAPEX (Conservative) ¦ NP=$1360/kW (×1.6)
Note on I139: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I144: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I145: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I146: CostDB PWRSPR CAPEX (Conservative) ¦ LK=$982/kW (×1.2)
Note on I147: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I152: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I153: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I154: CostDB PWRSPR CAPEX (Conservative) ¦ MV=$2550/kW (×3.0)
Note on I155: CostDB PWRSPR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I160: AvailabilityFactor=1.0 PWRSPR standard availability factor
Note on I161: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I162: CostDB PWRCSP CAPEX (Conservative)
Note on I163: CostDB PWRCSP Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I164: ResidualCapacity=51.849 GW (51849 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Coal ¦ Node: IN_N (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I168: AvailabilityFactor=0.95 PWRCSP standard availability factor
Note on I169: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I170: CostDB PWRCSP CAPEX (Conservative)
Note on I171: CostDB PWRCSP Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I172: ResidualCapacity=48.575 GW (48575 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Coal ¦ Node: IN_S (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I176: AvailabilityFactor=0.95 PWRCSP standard availability factor
Note on I177: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I178: CostDB PWRCSP CAPEX (Conservative)
Note on I179: CostDB PWRCSP Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I180: ResidualCapacity=40.385 GW (40385 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Coal ¦ Node: IN_E (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I184: AvailabilityFactor=0.95 PWRCSP standard availability factor
Note on I185: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I186: CostDB PWRCSP CAPEX (Conservative)
Note on I187: CostDB PWRCSP Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I188: ResidualCapacity=84.671 GW (84671 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Coal ¦ Node: IN_W (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I192: AvailabilityFactor=0.95 PWRCSP standard availability factor
Note on I193: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I194: CostDB PWRCSP CAPEX (Conservative)
Note on I195: CostDB PWRCSP Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I196: ResidualCapacity=0.750 GW (750 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Coal ¦ Node: IN_NE (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I200: AvailabilityFactor=0.95 PWRCSP standard availability factor
Note on I201: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I202: CostDB PWRCSP CAPEX (Conservative)
Note on I203: CostDB PWRCSP Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I204: ResidualCapacity (GW): LKA coal 900 MW (Norochcholai 3×300). Source: CEB Statistical Digest 2023 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I208: AvailabilityFactor=0.95 PWRCSP standard availability factor
Note on I209: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I210: CostDB PWRWON CAPEX (Conservative) ¦ BD=$1218/kW (×1.6)
Note on I211: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I212: ResidualCapacity (GW): BGD wind ~2 MW. Source: BPDB ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I216: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I217: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I224: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I225: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I226: CostDB PWRWON CAPEX (Conservative) ¦ IN base=$761/kW
Note on I227: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I228: ResidualCapacity (GW): IND North onshore wind ~5 GW. Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I232: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I233: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I234: CostDB PWRWON CAPEX (Conservative) ¦ IN base=$761/kW
Note on I235: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I236: ResidualCapacity (GW): IND South onshore wind ~15 GW (Tamil Nadu+Karnataka). Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I240: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I241: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I242: CostDB PWRWON CAPEX (Conservative) ¦ IN base=$761/kW
Note on I243: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I244: ResidualCapacity (GW): IND East onshore wind ~0.5 GW. Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I248: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I249: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I250: CostDB PWRWON CAPEX (Conservative) ¦ IN base=$761/kW
Note on I251: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I252: ResidualCapacity (GW): IND West onshore wind ~20 GW (Gujarat+Maharashtra). Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I256: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I257: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I258: CostDB PWRWON CAPEX (Conservative) ¦ IN base=$761/kW
Note on I259: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I260: ResidualCapacity (GW): IND NE wind ~0.1 GW. Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I264: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I265: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I272: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I273: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I274: CostDB PWRWON CAPEX (Conservative) ¦ LK=$1391/kW (×1.8)
Note on I275: CostDB PWRWON Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I276: ResidualCapacity (GW): LKA wind 128 MW. Source: CEB Statistical Digest 2023 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I280: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I281: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I288: AvailabilityFactor=1.0 PWRWON standard availability factor
Note on I289: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I290: CostDB PWRWOF CAPEX (Conservative) ¦ IN base=$2339/kW
Note on I291: CostDB PWRWOF Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I296: AvailabilityFactor=0.95 PWRWOF standard availability factor
Note on I297: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I298: CostDB PWRWOF CAPEX (Conservative) ¦ IN base=$2339/kW
Note on I299: CostDB PWRWOF Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I304: AvailabilityFactor=0.95 PWRWOF standard availability factor
Note on I305: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I306: CostDB PWRWOF CAPEX (Conservative) ¦ IN base=$2339/kW
Note on I307: CostDB PWRWOF Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I312: AvailabilityFactor=0.95 PWRWOF standard availability factor
Note on I313: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I320: AvailabilityFactor=0.95 PWRWOF standard availability factor
Note on I321: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I322: CostDB PWRWOF CAPEX (Conservative) ¦ LK=$3781/kW (×1.6)
Note on I323: CostDB PWRWOF Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I328: AvailabilityFactor=0.95 PWRWOF standard availability factor
Note on I329: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I336: AvailabilityFactor=0.95 PWRWOF standard availability factor
Note on I337: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I338: CostDB PWRHDR CAPEX (Conservative) ¦ NP=$2761/kW (×1.8)
Note on I339: CostDB PWRHDR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I340: ResidualCapacity (GW): NPL storage hydro ~100 MW (Kulekhani). Source: NEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I344: AvailabilityFactor=0.95 Reservoir hydro — high mechanical availability. Source: BPC PDB 2024, NEA
Note on I345: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I346: CostDB PWRHDR CAPEX (Conservative) ¦ BT=$1200/kW (×0.8)
Note on I347: CostDB PWRHDR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I348: ResidualCapacity (GW): BTN reservoir hydro ~1000 MW (Tala, Chukha). Source: BPC PDB 2024 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I352: AvailabilityFactor=0.95 Reservoir hydro — high mechanical availability. Source: BPC PDB 2024, NEA
Note on I353: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I354: CostDB PWRHDR CAPEX (Conservative) ¦ IN base=$1500/kW
Note on I355: CostDB PWRHDR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I356: ResidualCapacity=21.664 GW (21664 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Hydro ¦ Node: IN_N (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I360: AvailabilityFactor=0.95 Reservoir hydro — high mechanical availability. Source: BPC PDB 2024, NEA
Note on I361: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I362: CostDB PWRHDR CAPEX (Conservative) ¦ IN base=$1500/kW
Note on I363: CostDB PWRHDR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I364: ResidualCapacity=2.273 GW (2273 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Hydro ¦ Node: IN_NE (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I368: AvailabilityFactor=0.95 Reservoir hydro — high mechanical availability. Source: BPC PDB 2024, NEA
Note on I369: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I370: CostDB PWRHDR CAPEX (Conservative) ¦ IN base=$1500/kW
Note on I371: CostDB PWRHDR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I372: ResidualCapacity=5.988 GW (5988 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Hydro ¦ Node: IN_E (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I376: AvailabilityFactor=0.95 Reservoir hydro — high mechanical availability. Source: BPC PDB 2024, NEA
Note on I377: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I378: CostDB PWRHDR CAPEX (Conservative) ¦ LK=$2500/kW (×1.7)
Note on I379: CostDB PWRHDR Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I380: ResidualCapacity (GW): LKA major hydro 1384 MW (15 plants). Source: CEB Statistical Digest 2023 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I384: AvailabilityFactor=0.95 Reservoir hydro — high mechanical availability. Source: BPC PDB 2024, NEA
Note on I385: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I386: CostDB PWRHRO CAPEX (Conservative) ¦ NP=$1600/kW (×1.2)
Note on I387: CostDB PWRHRO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I388: ResidualCapacity (GW): NPL RoR hydro ~2200 MW. Source: NEA Yearly Summary FY2079/80 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I392: AvailabilityFactor=0.95 Run-of-river — high availability but seasonal flow constrains CF. Source: NEA/BPC
Note on I393: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I394: CostDB PWRHRO CAPEX (Conservative) ¦ BT=$1100/kW (×0.85)
Note on I395: CostDB PWRHRO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I396: ResidualCapacity (GW): BTN RoR hydro ~1452 MW (Mangdechhu etc). Source: BPC PDB 2024 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I400: AvailabilityFactor=0.95 Run-of-river — high availability but seasonal flow constrains CF. Source: NEA/BPC
Note on I401: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I402: CostDB PWRHRO CAPEX (Conservative) ¦ IN base=$1300/kW
Note on I403: CostDB PWRHRO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I404: ResidualCapacity=1.565 GW (1565 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Small Hydro ¦ Node: IN_N (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I408: AvailabilityFactor=0.95 Run-of-river — high availability but seasonal flow constrains CF. Source: NEA/BPC
Note on I409: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I410: CostDB PWRHRO CAPEX (Conservative) ¦ IN base=$1300/kW
Note on I411: CostDB PWRHRO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I412: ResidualCapacity=0.254 GW (254 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Small Hydro ¦ Node: IN_NE (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I416: AvailabilityFactor=0.95 Run-of-river — high availability but seasonal flow constrains CF. Source: NEA/BPC
Note on I417: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I418: CostDB PWRHPS CAPEX (Conservative) ¦ IN base=$635/kW
Note on I419: CostDB PWRHPS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I420: ResidualCapacity (GW): IND South pumped storage ~1 GW (Kadamparai etc). Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I424: AvailabilityFactor=0.92 Pumped storage. Source: CEA NEP
Note on I425: InputActivityRatio/Efficiency=0.8 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I426: CostDB PWRHPS CAPEX (Conservative) ¦ IN base=$635/kW
Note on I427: CostDB PWRHPS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I428: ResidualCapacity (GW): IND West pumped storage ~0.9 GW (Ghatghar). Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I432: AvailabilityFactor=0.92 Pumped storage. Source: CEA NEP
Note on I433: InputActivityRatio/Efficiency=0.8 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I434: CostDB PWRHPS CAPEX (Conservative) ¦ IN base=$635/kW
Note on I435: CostDB PWRHPS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I436: ResidualCapacity (GW): IND North pumped storage ~4.7 GW. Source: CEA ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I440: AvailabilityFactor=0.92 Pumped storage. Source: CEA NEP
Note on I441: InputActivityRatio/Efficiency=0.8 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I444: ResidualCapacity (GW): NPL pumped storage — none existing
Note on I448: AvailabilityFactor=0.92 Pumped storage. Source: CEA NEP
Note on I449: InputActivityRatio/Efficiency=0.8 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I452: ResidualCapacity (GW): LKA mini hydro 415 MW. Source: CEB Statistical Digest 2023 ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I456: AvailabilityFactor=0.92 Pumped storage. Source: CEA NEP
Note on I457: InputActivityRatio/Efficiency=0.8 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I458: CostDB PWRCOASCPC CAPEX (Conservative) ¦ BD=$1694/kW (×1.6)
Note on I459: CostDB PWRCOASCPC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I464: AvailabilityFactor=0.85 India CEA fleet PLF ~60-65%; AF allows ~85% availability. Source: IND_DA_Final Daily PLF sheet (NITI Aayog ICED)
Note on I465: InputActivityRatio/Efficiency=0.38 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I466: CostDB PWRCOASCPC CAPEX (Conservative) ¦ IN base=$1059/kW
Note on I467: CostDB PWRCOASCPC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I472: AvailabilityFactor=0.85 India CEA fleet PLF ~60-65%; AF allows ~85% availability. Source: IND_DA_Final Daily PLF sheet (NITI Aayog ICED)
Note on I473: InputActivityRatio/Efficiency=0.38 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I474: CostDB PWRCOASCPC CAPEX (Conservative) ¦ IN base=$1059/kW
Note on I475: CostDB PWRCOASCPC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I480: AvailabilityFactor=0.85 India CEA fleet PLF ~60-65%; AF allows ~85% availability. Source: IND_DA_Final Daily PLF sheet (NITI Aayog ICED)
Note on I481: InputActivityRatio/Efficiency=0.38 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I482: CostDB PWRCOASCPC CAPEX (Conservative) ¦ IN base=$1059/kW
Note on I483: CostDB PWRCOASCPC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I488: AvailabilityFactor=0.85 India CEA fleet PLF ~60-65%; AF allows ~85% availability. Source: IND_DA_Final Daily PLF sheet (NITI Aayog ICED)
Note on I489: InputActivityRatio/Efficiency=0.38 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I490: CostDB PWRCOASCPC CAPEX (Conservative) ¦ IN base=$1059/kW
Note on I491: CostDB PWRCOASCPC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I496: AvailabilityFactor=0.85 India CEA fleet PLF ~60-65%; AF allows ~85% availability. Source: IND_DA_Final Daily PLF sheet (NITI Aayog ICED)
Note on I497: InputActivityRatio/Efficiency=0.38 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I498: CostDB PWRCOASCPC CAPEX (Conservative) ¦ LK=$2132/kW (×2.0)
Note on I499: CostDB PWRCOASCPC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I504: AvailabilityFactor=0.85 India CEA fleet PLF ~60-65%; AF allows ~85% availability. Source: IND_DA_Final Daily PLF sheet (NITI Aayog ICED)
Note on I505: InputActivityRatio/Efficiency=0.38 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I506: CostDB PWRCOAUSC CAPEX (Conservative)
Note on I507: CostDB PWRCOAUSC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I512: AvailabilityFactor=0.87 USC plants newer, higher availability. Source: CEA NEP
Note on I513: InputActivityRatio/Efficiency=0.42 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I514: CostDB PWRCOAUSC CAPEX (Conservative)
Note on I515: CostDB PWRCOAUSC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I520: AvailabilityFactor=0.87 USC plants newer, higher availability. Source: CEA NEP
Note on I521: InputActivityRatio/Efficiency=0.42 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I522: CostDB PWRCOAUSC CAPEX (Conservative)
Note on I523: CostDB PWRCOAUSC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I528: AvailabilityFactor=0.87 USC plants newer, higher availability. Source: CEA NEP
Note on I529: InputActivityRatio/Efficiency=0.42 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I530: CostDB PWRCOAUSC CAPEX (Conservative)
Note on I531: CostDB PWRCOAUSC Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I536: AvailabilityFactor=0.87 USC plants newer, higher availability. Source: CEA NEP
Note on I537: InputActivityRatio/Efficiency=0.42 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I538: CostDB PWRCCG CAPEX (Conservative) ¦ BD=$770/kW (×1.1)
Note on I539: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I544: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on I545: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I546: CostDB PWRCCG CAPEX (Conservative) ¦ IN base=$700/kW
Note on I547: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I552: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on I553: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I554: CostDB PWRCCG CAPEX (Conservative) ¦ IN base=$700/kW
Note on I555: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I560: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on I561: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I562: CostDB PWRCCG CAPEX (Conservative) ¦ IN base=$700/kW
Note on I563: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I568: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on I569: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I570: CostDB PWRCCG CAPEX (Conservative) ¦ IN base=$700/kW
Note on I571: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I576: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on I577: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I578: CostDB PWRCCG CAPEX (Conservative) ¦ IN base=$700/kW
Note on I579: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I584: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on I585: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I592: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on I593: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I594: CostDB PWRCCG CAPEX (Conservative) ¦ LK=$1300/kW (×1.9)
Note on I595: CostDB PWRCCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I600: AvailabilityFactor=0.9 India CCGT PLF ~24% (low utilization, not low availability). AF=0.90. Source: NITI Aayog ICED PLF data
Note on I601: InputActivityRatio/Efficiency=0.55 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I602: CostDB PWROCG CAPEX (Conservative) ¦ BD=$495/kW (×1.1)
Note on I603: CostDB PWROCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I608: AvailabilityFactor=0.92 Peaking — high availability but low utilization. Source: industry standard
Note on I609: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I610: CostDB PWROCG CAPEX (Conservative) ¦ IN base=$450/kW
Note on I611: CostDB PWROCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I612: ResidualCapacity=5.712 GW (5712 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Oil & Gas ¦ Node: IN_N (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I616: AvailabilityFactor=0.92 Peaking — high availability but low utilization. Source: industry standard
Note on I617: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I618: CostDB PWROCG CAPEX (Conservative) ¦ IN base=$450/kW
Note on I619: CostDB PWROCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I620: ResidualCapacity=3.346 GW (3346 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Oil & Gas ¦ Node: IN_S (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I624: AvailabilityFactor=0.92 Peaking — high availability but low utilization. Source: industry standard
Note on I625: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I626: CostDB PWROCG CAPEX (Conservative) ¦ IN base=$450/kW
Note on I627: CostDB PWROCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I632: AvailabilityFactor=0.92 Peaking — high availability but low utilization. Source: industry standard
Note on I633: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I634: CostDB PWROCG CAPEX (Conservative) ¦ IN base=$450/kW
Note on I635: CostDB PWROCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I636: ResidualCapacity=9.399 GW (9399 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Oil & Gas ¦ Node: IN_W (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I640: AvailabilityFactor=0.92 Peaking — high availability but low utilization. Source: industry standard
Note on I641: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I642: CostDB PWROCG CAPEX (Conservative) ¦ IN base=$450/kW
Note on I643: CostDB PWROCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I644: ResidualCapacity=1.665 GW (1665 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Oil & Gas ¦ Node: IN_NE (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I648: AvailabilityFactor=0.92 Peaking — high availability but low utilization. Source: industry standard
Note on I649: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I656: AvailabilityFactor=0.92 Peaking — high availability but low utilization. Source: industry standard
Note on I657: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I658: CostDB PWROCG CAPEX (Conservative) ¦ LK=$360/kW (×0.8)
Note on I659: CostDB PWROCG Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I664: AvailabilityFactor=0.92 Peaking — high availability but low utilization. Source: industry standard
Note on I665: InputActivityRatio/Efficiency=0.35 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I666: CostDB PWROIL CAPEX (Conservative) ¦ MV=$700/kW (×1.0)
Note on I667: CostDB PWROIL Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I672: AvailabilityFactor=0.9 Oil/diesel backup. Source: CEB LTGEP, BPDB fleet data
Note on I673: InputActivityRatio/Efficiency=0.32 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I674: CostDB PWROIL CAPEX (Conservative) ¦ BD=$770/kW (×1.1)
Note on I675: CostDB PWROIL Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I680: AvailabilityFactor=0.9 Oil/diesel backup. Source: CEB LTGEP, BPDB fleet data
Note on I681: InputActivityRatio/Efficiency=0.32 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I682: CostDB PWROIL CAPEX (Conservative) ¦ LK=$1000/kW (×1.4)
Note on I683: CostDB PWROIL Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I688: AvailabilityFactor=0.9 Oil/diesel backup. Source: CEB LTGEP, BPDB fleet data
Note on I689: InputActivityRatio/Efficiency=0.32 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I696: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on I697: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I698: CostDB PWRBIO CAPEX (Conservative) ¦ IN base=$1142/kW
Note on I699: CostDB PWRBIO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I700: ResidualCapacity=3.670 GW (3670 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Bio Power ¦ Node: IN_N (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I704: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on I705: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I706: CostDB PWRBIO CAPEX (Conservative) ¦ IN base=$1142/kW
Note on I707: CostDB PWRBIO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I708: ResidualCapacity=3.781 GW (3781 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Bio Power ¦ Node: IN_S (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I712: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on I713: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I714: CostDB PWRBIO CAPEX (Conservative) ¦ IN base=$1142/kW
Note on I715: CostDB PWRBIO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I716: ResidualCapacity=0.576 GW (576 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Bio Power ¦ Node: IN_E (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I720: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on I721: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I722: CostDB PWRBIO CAPEX (Conservative) ¦ IN base=$1142/kW
Note on I723: CostDB PWRBIO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I724: ResidualCapacity=3.571 GW (3571 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Bio Power ¦ Node: IN_W (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I728: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on I729: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I730: CostDB PWRBIO CAPEX (Conservative) ¦ IN base=$1142/kW
Note on I731: CostDB PWRBIO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I732: ResidualCapacity=0.016 GW (16 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Bio Power ¦ Node: IN_NE (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I736: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on I737: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I744: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on I745: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I746: CostDB PWRBIO CAPEX (Conservative) ¦ LK=$1782/kW (×1.6)
Note on I747: CostDB PWRBIO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I752: AvailabilityFactor=0.8 Fuel supply seasonality reduces availability. Source: CERC benchmarks
Note on I753: InputActivityRatio/Efficiency=0.3 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I754: CostDB PWRWTE CAPEX (Conservative)
Note on I755: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I760: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on I761: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I762: CostDB PWRWTE CAPEX (Conservative)
Note on I763: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I768: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on I769: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I770: CostDB PWRWTE CAPEX (Conservative)
Note on I771: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I776: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on I777: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I778: CostDB PWRWTE CAPEX (Conservative)
Note on I779: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I784: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on I785: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I786: CostDB PWRWTE CAPEX (Conservative)
Note on I787: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I792: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on I793: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I794: CostDB PWRWTE CAPEX (Conservative)
Note on I795: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I800: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on I801: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I802: CostDB PWRWTE CAPEX (Conservative)
Note on I803: CostDB PWRWTE Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I808: AvailabilityFactor=0.85 PWRWTE standard availability factor
Note on I809: InputActivityRatio/Efficiency=0.25 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I810: CostDB PWRURN CAPEX (Conservative) ¦ IN base=$2000/kW
Note on I811: CostDB PWRURN Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I812: ResidualCapacity=2.220 GW (2220 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Nuclear ¦ Node: IN_N (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I816: AvailabilityFactor=0.9 India nuclear fleet AF ~80-90%. Source: NPCIL annual reports
Note on I817: InputActivityRatio/Efficiency=0.33 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I818: CostDB PWRURN CAPEX (Conservative) ¦ IN base=$2000/kW
Note on I819: CostDB PWRURN Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I820: ResidualCapacity=3.320 GW (3320 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Nuclear ¦ Node: IN_S (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I824: AvailabilityFactor=0.9 India nuclear fleet AF ~80-90%. Source: NPCIL annual reports
Note on I825: InputActivityRatio/Efficiency=0.33 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I826: CostDB PWRURN CAPEX (Conservative) ¦ IN base=$2000/kW
Note on I827: CostDB PWRURN Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I832: AvailabilityFactor=0.9 India nuclear fleet AF ~80-90%. Source: NPCIL annual reports
Note on I833: InputActivityRatio/Efficiency=0.33 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I834: CostDB PWRURN CAPEX (Conservative) ¦ IN base=$2000/kW
Note on I835: CostDB PWRURN Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I836: ResidualCapacity=3.240 GW (3240 MW) Aggregated from India_Electricity_Infrastructure.xlsx Existing Generation Fuel: Nuclear ¦ Node: IN_W (Zone-based mapping) Source: CEA plant database via Infrastructure file ⚠ ASSUMPTION: ResidualCapacity held flat (2023 value) across all years. No retirement or decommissioning modeled. This overstates available capacity in later years for aging plants. To improve: build retirement profiles from commissioning dates (available in Existing_Generation sheet) and typical plant lifetimes.
Note on I840: AvailabilityFactor=0.9 India nuclear fleet AF ~80-90%. Source: NPCIL annual reports
Note on I841: InputActivityRatio/Efficiency=0.33 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I842: CostDB PWRURN CAPEX (Conservative) ¦ IN base=$2000/kW
Note on I843: CostDB PWRURN Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I848: AvailabilityFactor=0.9 India nuclear fleet AF ~80-90%. Source: NPCIL annual reports
Note on I849: InputActivityRatio/Efficiency=0.33 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I850: CostDB PWRURN CAPEX (Conservative) ¦ BD=$5200/kW (×2.6)
Note on I851: CostDB PWRURN Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I856: AvailabilityFactor=0.9 India nuclear fleet AF ~80-90%. Source: NPCIL annual reports
Note on I857: InputActivityRatio/Efficiency=0.33 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I858: CostDB PWRGEO CAPEX (Conservative)
Note on I859: CostDB PWRGEO Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I864: AvailabilityFactor=0.9 PWRGEO standard availability factor
Note on I865: InputActivityRatio/Efficiency=0.15 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I867: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I872: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I873: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I875: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I880: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I881: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I883: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I888: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I889: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I891: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I896: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I897: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I899: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I904: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I905: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I907: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I912: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I913: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I915: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I920: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I921: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I923: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I928: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I929: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I931: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I936: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I937: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I939: CostDB PWRSDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I944: AvailabilityFactor=1.0 PWRSDS standard availability factor
Note on I945: InputActivityRatio/Efficiency=0.9 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I947: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I952: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I953: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I955: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I960: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I961: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I963: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I968: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I969: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I971: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I976: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I977: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I979: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I984: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I985: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I987: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I992: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I993: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I995: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1000: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I1001: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1003: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1008: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I1009: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1011: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1016: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I1017: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1019: CostDB PWRLDS Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1024: AvailabilityFactor=1.0 PWRLDS standard availability factor
Note on I1025: InputActivityRatio/Efficiency=0.85 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1026: CostDB PWRFPV CAPEX (Conservative)
Note on I1027: CostDB PWRFPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1032: AvailabilityFactor=1.0 PWRFPV standard availability factor
Note on I1033: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1034: CostDB PWRFPV CAPEX (Conservative)
Note on I1035: CostDB PWRFPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1040: AvailabilityFactor=1.0 PWRFPV standard availability factor
Note on I1041: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1042: CostDB PWRFPV CAPEX (Conservative)
Note on I1043: CostDB PWRFPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1048: AvailabilityFactor=1.0 PWRFPV standard availability factor
Note on I1049: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1050: CostDB PWRFPV CAPEX (Conservative)
Note on I1051: CostDB PWRFPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1056: AvailabilityFactor=1.0 PWRFPV standard availability factor
Note on I1057: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1058: CostDB PWRFPV CAPEX (Conservative)
Note on I1059: CostDB PWRFPV Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1064: AvailabilityFactor=1.0 PWRFPV standard availability factor
Note on I1065: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1066: CostDB PWRH2G CAPEX (Conservative)
Note on I1067: CostDB PWRH2G Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1072: AvailabilityFactor=0.95 PWRH2G standard availability factor
Note on I1073: InputActivityRatio/Efficiency=0.5 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1074: CostDB PWRH2G CAPEX (Conservative)
Note on I1075: CostDB PWRH2G Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1080: AvailabilityFactor=0.95 PWRH2G standard availability factor
Note on I1081: InputActivityRatio/Efficiency=0.5 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1082: CostDB PWRH2G CAPEX (Conservative)
Note on I1083: CostDB PWRH2G Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1088: AvailabilityFactor=0.95 PWRH2G standard availability factor
Note on I1089: InputActivityRatio/Efficiency=0.5 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1090: CostDB PWRH2G CAPEX (Conservative)
Note on I1091: CostDB PWRH2G Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1096: AvailabilityFactor=0.95 PWRH2G standard availability factor
Note on I1097: InputActivityRatio/Efficiency=0.5 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1098: CostDB PWRH2G CAPEX (Conservative)
Note on I1099: CostDB PWRH2G Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1104: AvailabilityFactor=0.95 PWRH2G standard availability factor
Note on I1105: InputActivityRatio/Efficiency=0.5 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1106: CostDB PWRTDL CAPEX (Conservative)
Note on I1107: CostDB PWRTDL Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1112: AvailabilityFactor=0.35 PWRTDL standard availability factor
Note on I1113: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1114: CostDB PWRTDL CAPEX (Conservative)
Note on I1115: CostDB PWRTDL Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1120: AvailabilityFactor=0.35 PWRTDL standard availability factor
Note on I1121: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1122: CostDB PWRBCK CAPEX (Conservative)
Note on I1123: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1128: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1129: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1130: CostDB PWRBCK CAPEX (Conservative)
Note on I1131: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1136: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1137: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1138: CostDB PWRBCK CAPEX (Conservative)
Note on I1139: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1144: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1145: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1146: CostDB PWRBCK CAPEX (Conservative)
Note on I1147: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1152: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1153: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1154: CostDB PWRBCK CAPEX (Conservative)
Note on I1155: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1160: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1161: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1162: CostDB PWRBCK CAPEX (Conservative)
Note on I1163: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1168: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1169: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1170: CostDB PWRBCK CAPEX (Conservative)
Note on I1171: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1176: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1177: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1178: CostDB PWRBCK CAPEX (Conservative)
Note on I1179: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1184: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1185: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1186: CostDB PWRBCK CAPEX (Conservative)
Note on I1187: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1192: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1193: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.
Note on I1194: CostDB PWRBCK CAPEX (Conservative)
Note on I1195: CostDB PWRBCK Fixed O&M (Conservative) (FOM scaled by node multiplier)
Note on I1200: AvailabilityFactor=1.0 PWRBCK standard availability factor
Note on I1201: InputActivityRatio/Efficiency=1.0 Source: OSTRAM_Consolidated_CostDB_v2 Heat Rate where available, otherwise industry standard.

## Capacities_CF
Timeslices | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
S1D1 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524
S1D3 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06
S2D2 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975
S2D3 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05
S3D2 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906
S3D3 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05
S4D1 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214
S4D3 | 1 | PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867 | 0.47867
S1D3 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05 | 8.3e-05
S2D2 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 0.46229
S2D3 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05
S3D1 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255 | 0.000255
S3D2 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641 | 0.33641
S3D3 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219 | 0.000219
S4D1 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333 | 0.44333
S4D3 | 2 | PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739 | 0.34739
S1D3 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505 | 0.000505
S2D2 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961 | 0.41961
S2D3 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06 | 2e-06
S3D1 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265 | 0.001265
S3D2 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564 | 0.37564
S3D3 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05 | 6.3e-05
S4D1 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027 | 0.35027
S4D3 | 3 | PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069
S1D3 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575
S2D3 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231
S3D3 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418
S4D3 | 4 | PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05
S1D2 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516
S1D3 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502
S2D2 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663
S2D3 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638
S3D2 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446
S3D3 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298
S4D2 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348
S4D3 | 5 | PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004 | 0.40004
S1D3 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844 | 0.42844
S2D3 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06
S3D1 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349 | 0.32349
S3D3 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05 | 3.7e-05
S4D1 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875 | 0.35875
S4D3 | 6 | PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052 | 0.00052
S1D2 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035 | 0.36035
S1D3 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261 | 0.012261
S2D2 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286 | 0.38286
S2D3 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121 | 0.01121
S3D2 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959 | 0.28959
S3D3 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785 | 0.001785
S4D2 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601 | 0.35601
S4D3 | 7 | PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06
S1D2 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422 | 0.422
S1D3 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412 | 0.005412
S2D2 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512 | 0.44512
S2D3 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955 | 0.005955
S3D2 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487 | 0.34487
S3D3 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05 | 3.4e-05
S4D2 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533 | 0.42533
S4D3 | 8 | PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578
S1D3 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074
S2D3 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361
S3D3 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418
S4D3 | 9 | PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331
S1D3 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719
S2D3 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146
S3D3 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984
S4D3 | 10 | PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954 | 0.29954
S1D3 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06
S2D2 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278 | 0.32278
S2D3 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05 | 4.4e-05
S3D2 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457 | 0.2457
S3D3 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06 | 9e-06
S4D1 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082 | 0.29082
S4D3 | 11 | PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687 | 0.40687
S1D3 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05 | 7e-05
S2D2 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295 | 0.39295
S2D3 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05
S3D1 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216 | 0.000216
S3D2 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594 | 0.28594
S3D3 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186 | 0.000186
S4D1 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683 | 0.37683
S4D3 | 12 | PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528 | 0.29528
S1D3 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429 | 0.000429
S2D2 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667 | 0.35667
S2D3 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06 | 1e-06
S3D1 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075 | 0.001075
S3D2 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193 | 0.3193
S3D3 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05 | 5.4e-05
S4D1 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773 | 0.29773
S4D3 | 13 | PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608 | 0.36608
S1D3 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639 | 0.33639
S2D3 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464 | 0.27464
S3D3 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955 | 0.30955
S4D3 | 14 | PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05 | 5.6e-05
S1D2 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886 | 0.29886
S1D3 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527 | 0.005527
S2D2 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863 | 0.32863
S2D3 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792 | 0.004792
S3D2 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479 | 0.22479
S3D3 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253 | 0.000253
S4D2 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458 | 0.28458
S4D3 | 15 | PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004 | 0.34004
S1D3 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417 | 0.36417
S2D3 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06 | 8e-06
S3D1 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497 | 0.27497
S3D3 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05 | 3.1e-05
S4D1 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494 | 0.30494
S4D3 | 16 | PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442 | 0.000442
S1D2 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629 | 0.30629
S1D3 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422 | 0.010422
S2D2 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543 | 0.32543
S2D3 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529 | 0.009529
S3D2 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616 | 0.24616
S3D3 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517 | 0.001517
S4D2 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261 | 0.30261
S4D3 | 17 | PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06 | 4e-06
S1D2 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587 | 0.3587
S1D3 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046 | 0.0046
S2D2 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835 | 0.37835
S2D3 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062 | 0.005062
S3D2 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314 | 0.29314
S3D3 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05 | 2.9e-05
S4D2 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153 | 0.36153
S4D3 | 18 | PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942 | 0.31942
S1D3 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113 | 0.28113
S2D3 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807 | 0.25807
S3D3 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006 | 0.25006
S4D3 | 19 | PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031 | 0.30031
S1D3 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661 | 0.28661
S2D3 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774 | 0.24774
S3D3 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337 | 0.26337
S4D3 | 20 | PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232 | 0.4232
S1D3 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508
S2D3 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368
S3D3 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414
S4D3 | 21 | PWRCSPIN_NXX01 | Concentrated Solar Power, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46
S1D3 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784 | 0.4784
S2D3 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864 | 0.3864
S3D3 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437 | 0.437
S4D3 | 22 | PWRCSPIN_SXX01 | Concentrated Solar Power, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048
S1D3 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324
S2D3 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 0.3496
S3D3 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956 | 0.3956
S4D3 | 23 | PWRCSPIN_EXX01 | Concentrated Solar Power, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508 | 0.4508
S1D3 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692
S2D3 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818 | 0.3818
S3D3 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324 | 0.4324
S4D3 | 24 | PWRCSPIN_WXX01 | Concentrated Solar Power, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772 | 0.3772
S1D3 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048 | 0.4048
S2D3 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404 | 0.3404
S3D3 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726 | 0.3726
S4D3 | 25 | PWRCSPIN_NEXX01 | Concentrated Solar Power, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718 | 0.5718
S1D2 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606 | 0.606
S1D3 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074 | 0.6074
S2D1 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451 | 0.7451
S2D2 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529 | 0.7529
S2D3 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646 | 0.7646
S3D1 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281 | 0.5281
S3D2 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393 | 0.5393
S3D3 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511 | 0.5511
S4D1 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871 | 0.3871
S4D2 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607 | 0.4607
S4D3 | 26 | PWRCSPLKXX01 | Concentrated Solar Power, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692 | 0.4692
S1D1 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271 | 0.18271
S1D2 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973 | 0.072973
S1D3 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761 | 0.17761
S2D1 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216 | 0.31216
S2D2 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854 | 0.18854
S2D3 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451 | 0.40451
S3D1 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614 | 0.34614
S3D2 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055 | 0.31055
S3D3 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914 | 0.39914
S4D1 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462 | 0.12462
S4D2 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134 | 0.06134
S4D3 | 27 | PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855 | 0.10855
S1D1 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887 | 0.014887
S1D2 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763 | 0.089763
S1D3 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784 | 0.008784
S2D1 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788 | 0.021788
S2D2 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705 | 0.15705
S2D3 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576 | 0.037576
S3D1 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479 | 0.050479
S3D2 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703 | 0.14703
S3D3 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201 | 0.090201
S4D1 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296 | 0.012296
S4D2 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323 | 0.060323
S4D3 | 28 | PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816 | 0.017816
S1D1 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525 | 0.3525
S1D2 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302 | 0.19302
S1D3 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968 | 0.36968
S2D1 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756 | 0.3756
S2D2 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531 | 0.23531
S2D3 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589 | 0.41589
S3D1 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612 | 0.26612
S3D2 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239 | 0.20239
S3D3 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488 | 0.24488
S4D1 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002 | 0.24002
S4D2 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386 | 0.14386
S4D3 | 29 | PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234 | 0.25234
S1D1 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063 | 0.30063
S1D2 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601 | 0.23601
S1D3 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015 | 0.60015
S2D1 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216 | 0.30216
S2D2 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781 | 0.19781
S2D3 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301 | 0.49301
S3D1 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136 | 0.47136
S3D2 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091 | 0.58091
S3D3 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757 | 0.48757
S4D1 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011 | 0.26011
S4D2 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464 | 0.26464
S4D3 | 30 | PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699 | 0.3699
S1D1 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451 | 0.2451
S1D2 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909 | 0.11909
S1D3 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672 | 0.1672
S2D1 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438 | 0.34438
S2D2 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886 | 0.26886
S2D3 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172 | 0.47172
S3D1 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549 | 0.33549
S3D2 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303 | 0.32303
S3D3 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717 | 0.43717
S4D1 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851
S4D2 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597 | 0.087597
S4D3 | 31 | PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278 | 0.1278
S1D1 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383 | 0.31383
S1D2 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478 | 0.17478
S1D3 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659 | 0.33659
S2D1 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236 | 0.12236
S2D2 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744 | 0.21744
S2D3 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218 | 0.26218
S3D1 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917 | 0.46917
S3D2 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679 | 0.49679
S3D3 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838 | 0.45838
S4D1 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023 | 0.31023
S4D2 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604 | 0.14604
S4D3 | 32 | PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678 | 0.21678
S1D1 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174 | 0.31174
S1D2 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372 | 0.14372
S1D3 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786 | 0.31786
S2D1 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554 | 0.42554
S2D2 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016 | 0.28016
S2D3 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981 | 0.39981
S3D1 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423 | 0.22423
S3D2 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192 | 0.17192
S3D3 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299 | 0.2299
S4D1 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868 | 0.22868
S4D2 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137 | 0.096137
S4D3 | 33 | PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112 | 0.2112
S1D1 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158 | 0.011158
S1D2 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806 | 0.035806
S1D3 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569 | 0.010569
S2D1 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244 | 0.023244
S2D2 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086 | 0.07086
S2D3 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415 | 0.02415
S3D1 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318 | 0.01318
S3D2 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821 | 0.045821
S3D3 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758 | 0.027758
S4D1 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716 | 0.005716
S4D2 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307 | 0.01307
S4D3 | 34 | PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756 | 0.006756
S1D1 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017 | 0.36017
S1D2 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575 | 0.26575
S1D3 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039 | 0.37039
S2D1 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541 | 0.24541
S2D2 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144 | 0.2144
S2D3 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453 | 0.2453
S3D1 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862 | 0.63862
S3D2 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108 | 0.59108
S3D3 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255 | 0.59255
S4D1 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973 | 0.2973
S4D2 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404 | 0.27404
S4D3 | 35 | PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799 | 0.28799
S1D1 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967 | 0.21967
S1D2 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357 | 0.23357
S1D3 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032 | 0.24032
S2D1 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355 | 0.2355
S2D2 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542
S2D3 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464 | 0.23464
S3D1 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581 | 0.23581
S3D2 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062 | 0.23062
S3D3 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914 | 0.22914
S4D1 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934 | 0.30934
S4D2 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462 | 0.31462
S4D3 | 36 | PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016 | 0.30016
S1D1 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195
S1D2 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195
S1D3 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195
S2D1 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
S2D2 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
S2D3 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
S3D1 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429
S3D2 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429
S3D3 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429 | 0.429
S4D1 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S4D2 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S4D3 | 37 | PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S1D1 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275
S1D2 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275
S1D3 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275 | 0.275
S2D1 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375
S2D2 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375
S2D3 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375 | 0.3375
S3D1 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D2 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D3 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S4D1 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S4D2 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S4D3 | 38 | PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D1 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D2 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D3 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D1 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D2 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D3 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D1 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D2 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D3 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D1 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D2 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D3 | 39 | PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D1 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
S1D2 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
S1D3 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
S2D1 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
S2D2 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
S2D3 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
S3D1 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D2 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D3 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S4D1 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
S4D2 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
S4D3 | 40 | PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175 | 0.175
S1D1 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
S1D2 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
S1D3 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288 | 0.288
S2D1 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S2D2 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S2D3 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S3D1 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624
S3D2 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624
S3D3 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624 | 0.624
S4D1 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
S4D2 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
S4D3 | 41 | PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
S1D1 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S1D2 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S1D3 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S2D1 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S2D2 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S2D3 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S3D1 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S3D2 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S3D3 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S4D1 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S4D2 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S4D3 | 42 | PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
S1D1 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D2 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S1D3 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S2D1 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
S2D2 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S2D3 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S3D1 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
S3D2 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
S3D3 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
S4D1 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58
S4D2 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D3 | 43 | PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S1D1 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952
S1D2 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096
S1D3 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117
S2D1 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851
S2D2 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988
S2D3 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007
S3D1 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201
S3D2 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805
S3D3 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891
S4D1 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986
S4D2 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427
S4D3 | 44 | PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649
S1D1 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D2 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D3 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S2D1 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S2D2 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S2D3 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 | 0.45
S3D1 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
S3D2 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
S3D3 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
S4D1 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D2 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D3 | 45 | PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S1D1 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
S1D2 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
S1D3 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
S2D1 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S2D2 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S2D3 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
S3D1 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
S3D2 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
S3D3 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
S4D1 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S4D2 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S4D3 | 46 | PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S1D1 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D2 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S1D3 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
S2D1 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D2 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D3 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S3D1 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S3D2 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S3D3 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S4D1 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S4D2 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S4D3 | 47 | PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S1D1 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357 | 0.3357
S1D2 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808 | 0.4808
S1D3 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507 | 0.507
S2D1 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692 | 0.1692
S2D2 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895 | 0.2895
S2D3 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754 | 0.3754
S3D1 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814 | 0.1814
S3D2 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702 | 0.2702
S3D3 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278 | 0.3278
S4D1 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793 | 0.4793
S4D2 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477 | 0.6477
S4D3 | 48 | PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914 | 0.6914
S1D1 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D2 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S1D3 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
S2D1 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
S2D2 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S2D3 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S3D1 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
S3D2 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
S3D3 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
S4D1 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58 | 0.58
S4D2 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D3 | 49 | PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S1D1 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952 | 0.1952
S1D2 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096 | 0.2096
S1D3 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117 | 0.2117
S2D1 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851 | 0.1851
S2D2 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988 | 0.1988
S2D3 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007 | 0.2007
S3D1 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201 | 0.8201
S3D2 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805 | 0.8805
S3D3 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891 | 0.8891
S4D1 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986 | 0.5986
S4D2 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427 | 0.6427
S4D3 | 50 | PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649 | 0.649
S1D1 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
S1D2 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
S1D3 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
S2D1 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
S2D2 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
S2D3 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38
S3D1 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
S3D2 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
S3D3 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
S4D1 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D2 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S4D3 | 51 | PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S1D1 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
S1D2 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
S1D3 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
S2D1 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D2 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D3 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S3D1 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
S3D2 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
S3D3 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82 | 0.82
S4D1 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S4D2 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S4D3 | 52 | PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62
S1D1 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 53 | PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 54 | PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 55 | PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
S1D2 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
S1D3 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S2D1 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D2 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S2D3 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
S3D1 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S3D2 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S3D3 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
S4D1 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
S4D2 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
S4D3 | 56 | PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
S1D1 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235 | 0.3235
S1D2 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | 0.315
S1D3 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131 | 0.3131
S2D1 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188 | 0.188
S2D2 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833 | 0.1833
S2D3 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877 | 0.1877
S3D1 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503 | 0.3503
S3D2 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457 | 0.3457
S3D3 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542 | 0.3542
S4D1 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778 | 0.2778
S4D2 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854 | 0.2854
S4D3 | 57 | PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029 | 0.3029
S1D1 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 58 | PWRSDSBDXX01 | Short-duration storage (Li-ion 4h), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 59 | PWRSDSBTXX01 | Short-duration storage (Li-ion 4h), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 60 | PWRSDSIN_NXX01 | Short-duration storage (Li-ion 4h), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 61 | PWRSDSIN_SXX01 | Short-duration storage (Li-ion 4h), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 62 | PWRSDSIN_EXX01 | Short-duration storage (Li-ion 4h), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 63 | PWRSDSIN_WXX01 | Short-duration storage (Li-ion 4h), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 64 | PWRSDSIN_NEXX01 | Short-duration storage (Li-ion 4h), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 65 | PWRSDSNPXX01 | Short-duration storage (Li-ion 4h), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 66 | PWRSDSLKXX01 | Short-duration storage (Li-ion 4h), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 67 | PWRSDSMVXX01 | Short-duration storage (Li-ion 4h), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 68 | PWRLDSBDXX01 | Long-duration storage (8h+), Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 69 | PWRLDSBTXX01 | Long-duration storage (8h+), Bhutan, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 70 | PWRLDSIN_NXX01 | Long-duration storage (8h+), India – North, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 71 | PWRLDSIN_SXX01 | Long-duration storage (8h+), India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 72 | PWRLDSIN_EXX01 | Long-duration storage (8h+), India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 73 | PWRLDSIN_WXX01 | Long-duration storage (8h+), India – West, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 74 | PWRLDSIN_NEXX01 | Long-duration storage (8h+), India – Northeast, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 75 | PWRLDSNPXX01 | Long-duration storage (8h+), Nepal, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 76 | PWRLDSLKXX01 | Long-duration storage (8h+), Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D2 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D3 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D1 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D2 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S2D3 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D1 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D2 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S3D3 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D1 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D2 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S4D3 | 77 | PWRLDSMVXX01 | Long-duration storage (8h+), Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023 to 2050
S1D1 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069 | 0.43069
S1D3 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575 | 0.39575
S2D3 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231 | 0.3231
S3D3 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418 | 0.36418
S4D3 | 78 | PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05 | 6.6e-05
S1D2 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516 | 0.3516
S1D3 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502 | 0.006502
S2D2 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663 | 0.38663
S2D3 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638 | 0.005638
S3D2 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446 | 0.26446
S3D3 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298 | 0.000298
S4D2 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348 | 0.3348
S4D3 | 79 | PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524 | 0.3524
S1D3 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06 | 5e-06
S2D2 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975 | 0.37975
S2D3 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05 | 5.2e-05
S3D2 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906 | 0.28906
S3D3 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05 | 1.1e-05
S4D1 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214
S4D3 | 80 | PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578 | 0.37578
S1D3 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074 | 0.33074
S2D3 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361 | 0.30361
S3D3 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418 | 0.29418
S4D3 | 81 | PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D2 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331 | 0.35331
S1D3 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D1 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S2D2 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719 | 0.33719
S2D3 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D1 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S3D2 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146 | 0.29146
S3D3 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D1 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S4D2 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984 | 0.30984
S4D3 | 82 | PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
S1D1 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D2 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D3 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D1 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D2 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D3 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D1 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D2 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D3 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D1 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D2 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D3 | 83 | PWRTDLIN_SXX01 | Tidal / Marine, India – South, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D1 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D2 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S1D3 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D1 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D2 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S2D3 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D1 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D2 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S3D3 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D1 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D2 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
S4D3 | 84 | PWRTDLLKXX01 | Tidal / Marine, Sri Lanka, region XX (investable) | 13 | CapacityFactor | fraction | User defined | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Note on J2: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J3: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3524 Previous template value: 0.2480 (replaced)
Note on J4: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J5: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J6: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3797 Previous template value: 0.3240 (replaced)
Note on J7: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J8: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0001
Note on J9: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.2891 Previous template value: 0.2990 (replaced)
Note on J10: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J11: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J12: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3421 Previous template value: 0.3600 (replaced)
Note on J13: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J14: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0000
Note on J15: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.4787 Previous template value: 0.1600 (replaced)
Note on J16: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0000
Note on J17: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0001
Note on J18: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.4623 Previous template value: 0.1800 (replaced)
Note on J19: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0001
Note on J20: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0003
Note on J21: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.3364 Previous template value: 0.1450 (replaced)
Note on J22: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0002
Note on J23: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0000
Note on J24: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.4433 Previous template value: 0.1700 (replaced)
Note on J25: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0000
Note on J26: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000
Note on J27: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.3474 Previous template value: 0.4600 (replaced)
Note on J28: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000
Note on J29: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0005
Note on J30: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.4196 Previous template value: 0.4900 (replaced)
Note on J31: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000
Note on J32: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0013
Note on J33: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.3756 Previous template value: 0.4000 (replaced)
Note on J34: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0001
Note on J35: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000
Note on J36: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.3503 Previous template value: 0.4500 (replaced)
Note on J37: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000
Note on J38: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J39: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.4307 Previous template value: 0.5000 (replaced)
Note on J40: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J41: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J42: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3957 Previous template value: 0.5200 (replaced)
Note on J43: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J44: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J45: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3231 Previous template value: 0.4200 (replaced)
Note on J46: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J47: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J48: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3642 Previous template value: 0.4750 (replaced)
Note on J49: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J50: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0001
Note on J51: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3516 Previous template value: 0.4400 (replaced)
Note on J52: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on J53: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0065
Note on J54: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3866 Previous template value: 0.4700 (replaced)
Note on J55: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on J56: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0056
Note on J57: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2645 Previous template value: 0.3800 (replaced)
Note on J58: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on J59: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0003
Note on J60: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3348 Previous template value: 0.4300 (replaced)
Note on J61: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on J62: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000
Note on J63: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.4000 Previous template value: 0.4900 (replaced)
Note on J64: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000
Note on J65: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000
Note on J66: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.4284 Previous template value: 0.5100 (replaced)
Note on J67: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000
Note on J68: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000
Note on J69: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.3235 Previous template value: 0.4150 (replaced)
Note on J70: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000
Note on J71: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000
Note on J72: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.3588 Previous template value: 0.4700 (replaced)
Note on J73: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000
Note on J74: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0005
Note on J75: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3603 Previous template value: 0.4100 (replaced)
Note on J76: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0000
Note on J77: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0123
Note on J78: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3829 Previous template value: 0.4400 (replaced)
Note on J79: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0000
Note on J80: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0112
Note on J81: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.2896 Previous template value: 0.3700 (replaced)
Note on J82: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0000
Note on J83: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0018
Note on J84: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3560 Previous template value: 0.4050 (replaced)
Note on J85: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0000
Note on J86: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000
Note on J87: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.4220 Previous template value: 0.2620 (replaced)
Note on J88: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000
Note on J89: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0054
Note on J90: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.4451 Previous template value: 0.2620 (replaced)
Note on J91: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000
Note on J92: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0060
Note on J93: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.3449 Previous template value: 0.2620 (replaced)
Note on J94: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000
Note on J95: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000
Note on J96: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.4253 Previous template value: 0.2620 (replaced)
Note on J97: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000
Note on J98: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J99: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3758 Previous template value: 0.4300 (replaced)
Note on J100: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J101: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J102: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3307 Previous template value: 0.4500 (replaced)
Note on J103: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J104: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J105: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3036 Previous template value: 0.3400 (replaced)
Note on J106: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J107: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J108: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2942 Previous template value: 0.3800 (replaced)
Note on J109: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J110: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J111: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3533 Previous template value: 0.3930 (replaced)
Note on J112: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J113: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J114: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3372 Previous template value: 0.3930 (replaced)
Note on J115: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J116: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J117: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2915 Previous template value: 0.3930 (replaced)
Note on J118: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J119: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J120: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3098 Previous template value: 0.3930 (replaced)
Note on J121: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J122: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale Previous template value: 0.0271 (replaced)
Note on J123: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.2995 Rooftop: 0.85× utility-scale Previous template value: 0.2108 (replaced)
Note on J124: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale Previous template value: 0.2030 (replaced)
Note on J125: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J126: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3228 Rooftop: 0.85× utility-scale Previous template value: 0.2754 (replaced)
Note on J127: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale Previous template value: 0.3873 (replaced)
Note on J128: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J129: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.2457 Rooftop: 0.85× utility-scale Previous template value: 0.2541 (replaced)
Note on J130: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J131: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale Previous template value: 0.1232 (replaced)
Note on J132: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.2908 Rooftop: 0.85× utility-scale Previous template value: 0.3060 (replaced)
Note on J133: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale Previous template value: 0.3136 (replaced)
Note on J134: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J135: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.4069 Rooftop: 0.85× utility-scale Previous template value: 0.1360 (replaced)
Note on J136: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J137: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0001 Rooftop: 0.85× utility-scale
Note on J138: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.3929 Rooftop: 0.85× utility-scale Previous template value: 0.1530 (replaced)
Note on J139: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0001 Rooftop: 0.85× utility-scale
Note on J140: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0002 Rooftop: 0.85× utility-scale
Note on J141: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.2859 Rooftop: 0.85× utility-scale Previous template value: 0.1232 (replaced)
Note on J142: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0002 Rooftop: 0.85× utility-scale
Note on J143: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J144: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.3768 Rooftop: 0.85× utility-scale Previous template value: 0.1445 (replaced)
Note on J145: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=solar Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J146: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J147: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.2953 Rooftop: 0.85× utility-scale Previous template value: 0.3910 (replaced)
Note on J148: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J149: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0004 Rooftop: 0.85× utility-scale
Note on J150: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.3567 Rooftop: 0.85× utility-scale Previous template value: 0.4165 (replaced)
Note on J151: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J152: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0011 Rooftop: 0.85× utility-scale
Note on J153: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.3193 Rooftop: 0.85× utility-scale Previous template value: 0.3400 (replaced)
Note on J154: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0001 Rooftop: 0.85× utility-scale
Note on J155: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J156: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.2977 Rooftop: 0.85× utility-scale Previous template value: 0.3825 (replaced)
Note on J157: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=solar Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J158: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J159: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3661 Rooftop: 0.85× utility-scale Previous template value: 0.4250 (replaced)
Note on J160: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J161: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J162: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3364 Rooftop: 0.85× utility-scale Previous template value: 0.4420 (replaced)
Note on J163: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J164: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J165: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.2746 Rooftop: 0.85× utility-scale Previous template value: 0.3570 (replaced)
Note on J166: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J167: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J168: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3095 Rooftop: 0.85× utility-scale Previous template value: 0.4037 (replaced)
Note on J169: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J170: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0001 Rooftop: 0.85× utility-scale
Note on J171: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2989 Rooftop: 0.85× utility-scale Previous template value: 0.3740 (replaced)
Note on J172: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J173: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0055 Rooftop: 0.85× utility-scale
Note on J174: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3286 Rooftop: 0.85× utility-scale Previous template value: 0.3995 (replaced)
Note on J175: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J176: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0048 Rooftop: 0.85× utility-scale
Note on J177: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2248 Rooftop: 0.85× utility-scale Previous template value: 0.3230 (replaced)
Note on J178: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J179: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0003 Rooftop: 0.85× utility-scale
Note on J180: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2846 Rooftop: 0.85× utility-scale Previous template value: 0.3655 (replaced)
Note on J181: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J182: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J183: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.3400 Rooftop: 0.85× utility-scale Previous template value: 0.4165 (replaced)
Note on J184: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J185: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J186: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.3642 Rooftop: 0.85× utility-scale Previous template value: 0.4335 (replaced)
Note on J187: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J188: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J189: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.2750 Rooftop: 0.85× utility-scale Previous template value: 0.3528 (replaced)
Note on J190: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J191: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J192: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.3049 Rooftop: 0.85× utility-scale Previous template value: 0.3995 (replaced)
Note on J193: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=solar Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J194: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0004 Rooftop: 0.85× utility-scale
Note on J195: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3063 Rooftop: 0.85× utility-scale Previous template value: 0.3485 (replaced)
Note on J196: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J197: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0104 Rooftop: 0.85× utility-scale
Note on J198: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3254 Rooftop: 0.85× utility-scale Previous template value: 0.3740 (replaced)
Note on J199: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J200: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0095 Rooftop: 0.85× utility-scale
Note on J201: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.2462 Rooftop: 0.85× utility-scale Previous template value: 0.3145 (replaced)
Note on J202: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J203: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0015 Rooftop: 0.85× utility-scale
Note on J204: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3026 Rooftop: 0.85× utility-scale Previous template value: 0.3443 (replaced)
Note on J205: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=solar Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J206: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J207: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.3587 Rooftop: 0.85× utility-scale Previous template value: 0.2227 (replaced)
Note on J208: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J209: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0046 Rooftop: 0.85× utility-scale
Note on J210: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.3784 Rooftop: 0.85× utility-scale Previous template value: 0.2227 (replaced)
Note on J211: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J212: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0051 Rooftop: 0.85× utility-scale
Note on J213: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.2931 Rooftop: 0.85× utility-scale Previous template value: 0.2227 (replaced)
Note on J214: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J215: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J216: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.3615 Rooftop: 0.85× utility-scale Previous template value: 0.2227 (replaced)
Note on J217: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=solar Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J218: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J219: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3194 Rooftop: 0.85× utility-scale Previous template value: 0.3655 (replaced)
Note on J220: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J221: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J222: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2811 Rooftop: 0.85× utility-scale Previous template value: 0.3825 (replaced)
Note on J223: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J224: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J225: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2581 Rooftop: 0.85× utility-scale Previous template value: 0.2890 (replaced)
Note on J226: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J227: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J228: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2501 Rooftop: 0.85× utility-scale Previous template value: 0.3230 (replaced)
Note on J229: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J230: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J231: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3003 Rooftop: 0.85× utility-scale Previous template value: 0.3341 (replaced)
Note on J232: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J233: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J234: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2866 Rooftop: 0.85× utility-scale Previous template value: 0.3341 (replaced)
Note on J235: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J236: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J237: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2477 Rooftop: 0.85× utility-scale Previous template value: 0.3341 (replaced)
Note on J238: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J239: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J240: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2634 Rooftop: 0.85× utility-scale Previous template value: 0.3341 (replaced)
Note on J241: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000 Rooftop: 0.85× utility-scale
Note on J242: ⚠ MISSING: No data source identified. All year values are 0.
Note on J243: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J246: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J249: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J252: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J254: ⚠ MISSING: No data source identified. All year values are 0.
Note on J255: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J258: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J261: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J264: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J266: ⚠ MISSING: No data source identified. All year values are 0.
Note on J267: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J270: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J273: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J276: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J278: ⚠ MISSING: No data source identified. All year values are 0.
Note on J279: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J282: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J285: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J288: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J290: ⚠ MISSING: No data source identified. All year values are 0.
Note on J291: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J294: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J297: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J300: Pre-integration value. Likely derived from DNI/solar resource data. ⚠ SOURCE UNKNOWN — verify against Solargis or NREL NSRDB.
Note on J302: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J303: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J304: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J305: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J306: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J307: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J308: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J309: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J310: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J311: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J312: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J313: Coal CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J314: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1827 Previous template value: 0.1200 (replaced)
Note on J315: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0730 Previous template value: 0.1200 (replaced)
Note on J316: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1776 Previous template value: 0.1200 (replaced)
Note on J317: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3122 Previous template value: 0.1800 (replaced)
Note on J318: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1885 Previous template value: 0.1800 (replaced)
Note on J319: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.4045 Previous template value: 0.1800 (replaced)
Note on J320: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3461 Previous template value: 0.3600 (replaced)
Note on J321: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3106 Previous template value: 0.3600 (replaced)
Note on J322: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3991 Previous template value: 0.3600 (replaced)
Note on J323: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1246 Previous template value: 0.1400 (replaced)
Note on J324: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0613 Previous template value: 0.1400 (replaced)
Note on J325: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=wind Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.1085 Previous template value: 0.1400 (replaced)
Note on J326: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0149 Previous template value: 0.2000 (replaced)
Note on J327: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0898 Previous template value: 0.2000 (replaced)
Note on J328: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0088 Previous template value: 0.2000 (replaced)
Note on J329: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0218 Previous template value: 0.2000 (replaced)
Note on J330: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.1570 Previous template value: 0.2000 (replaced)
Note on J331: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0376 Previous template value: 0.2000 (replaced)
Note on J332: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0505 Previous template value: 0.2000 (replaced)
Note on J333: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.1470 Previous template value: 0.2000 (replaced)
Note on J334: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0902 Previous template value: 0.2000 (replaced)
Note on J335: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0123 Previous template value: 0.2000 (replaced)
Note on J336: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0603 Previous template value: 0.2000 (replaced)
Note on J337: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BTNXX ¦ resource=wind Coordinates: lat=27.473, lon=89.639 9-year mean CF=0.0178 Previous template value: 0.2000 (replaced)
Note on J338: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.3525 Previous template value: 0.1800 (replaced)
Note on J339: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.1930 Previous template value: 0.1800 (replaced)
Note on J340: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.3697 Previous template value: 0.1800 (replaced)
Note on J341: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.3756 Previous template value: 0.2500 (replaced)
Note on J342: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.2353 Previous template value: 0.2500 (replaced)
Note on J343: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.4159 Previous template value: 0.2500 (replaced)
Note on J344: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.2661 Previous template value: 0.3200 (replaced)
Note on J345: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.2024 Previous template value: 0.3200 (replaced)
Note on J346: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.2449 Previous template value: 0.3200 (replaced)
Note on J347: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.2400 Previous template value: 0.2200 (replaced)
Note on J348: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.1439 Previous template value: 0.2200 (replaced)
Note on J349: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNO ¦ resource=wind Coordinates: lat=28.67, lon=77.23 9-year mean CF=0.2523 Previous template value: 0.2200 (replaced)
Note on J350: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3006 Previous template value: 0.1500 (replaced)
Note on J351: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.2360 Previous template value: 0.1500 (replaced)
Note on J352: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.6001 Previous template value: 0.1500 (replaced)
Note on J353: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3022 Previous template value: 0.2400 (replaced)
Note on J354: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.1978 Previous template value: 0.2400 (replaced)
Note on J355: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.4930 Previous template value: 0.2400 (replaced)
Note on J356: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.4714 Previous template value: 0.3300 (replaced)
Note on J357: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.5809 Previous template value: 0.3300 (replaced)
Note on J358: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.4876 Previous template value: 0.3300 (replaced)
Note on J359: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.2601 Previous template value: 0.2000 (replaced)
Note on J360: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.2646 Previous template value: 0.2000 (replaced)
Note on J361: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=wind Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3699 Previous template value: 0.2000 (replaced)
Note on J362: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2451 Previous template value: 0.2000 (replaced)
Note on J363: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.1191 Previous template value: 0.2000 (replaced)
Note on J364: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.1672 Previous template value: 0.2000 (replaced)
Note on J365: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3444 Previous template value: 0.2000 (replaced)
Note on J366: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2689 Previous template value: 0.2000 (replaced)
Note on J367: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.4717 Previous template value: 0.2000 (replaced)
Note on J368: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3355 Previous template value: 0.2000 (replaced)
Note on J369: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3230 Previous template value: 0.2000 (replaced)
Note on J370: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.4372 Previous template value: 0.2000 (replaced)
Note on J371: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.1851 Previous template value: 0.2000 (replaced)
Note on J372: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0876 Previous template value: 0.2000 (replaced)
Note on J373: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=wind Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.1278 Previous template value: 0.2000 (replaced)
Note on J374: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.3138 Previous template value: 0.2200 (replaced)
Note on J375: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.1748 Previous template value: 0.2200 (replaced)
Note on J376: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.3366 Previous template value: 0.2200 (replaced)
Note on J377: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.1224 Previous template value: 0.2700 (replaced)
Note on J378: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.2174 Previous template value: 0.2700 (replaced)
Note on J379: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.2622 Previous template value: 0.2700 (replaced)
Note on J380: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.4692 Previous template value: 0.3600 (replaced)
Note on J381: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.4968 Previous template value: 0.3600 (replaced)
Note on J382: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.4584 Previous template value: 0.3600 (replaced)
Note on J383: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.3102 Previous template value: 0.2400 (replaced)
Note on J384: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.1460 Previous template value: 0.2400 (replaced)
Note on J385: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDWE ¦ resource=wind Coordinates: lat=19.017, lon=72.857 9-year mean CF=0.2168 Previous template value: 0.2400 (replaced)
Note on J386: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3117 Previous template value: 0.2000 (replaced)
Note on J387: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.1437 Previous template value: 0.2000 (replaced)
Note on J388: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3179 Previous template value: 0.2000 (replaced)
Note on J389: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.4255 Previous template value: 0.2000 (replaced)
Note on J390: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.2802 Previous template value: 0.2000 (replaced)
Note on J391: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.3998 Previous template value: 0.2000 (replaced)
Note on J392: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.2242 Previous template value: 0.2000 (replaced)
Note on J393: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.1719 Previous template value: 0.2000 (replaced)
Note on J394: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.2299 Previous template value: 0.2000 (replaced)
Note on J395: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.2287 Previous template value: 0.2000 (replaced)
Note on J396: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.0961 Previous template value: 0.2000 (replaced)
Note on J397: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDNE ¦ resource=wind Coordinates: lat=26.16, lon=91.77 9-year mean CF=0.2112 Previous template value: 0.2000 (replaced)
Note on J398: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0112 Previous template value: 0.2000 (replaced)
Note on J399: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0358 Previous template value: 0.2000 (replaced)
Note on J400: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0106 Previous template value: 0.2000 (replaced)
Note on J401: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0232 Previous template value: 0.2000 (replaced)
Note on J402: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0709 Previous template value: 0.2000 (replaced)
Note on J403: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0242 Previous template value: 0.2000 (replaced)
Note on J404: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0132 Previous template value: 0.2000 (replaced)
Note on J405: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0458 Previous template value: 0.2000 (replaced)
Note on J406: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0278 Previous template value: 0.2000 (replaced)
Note on J407: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0057 Previous template value: 0.2000 (replaced)
Note on J408: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0131 Previous template value: 0.2000 (replaced)
Note on J409: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=NPLXX ¦ resource=wind Coordinates: lat=27.7167, lon=85.3166 9-year mean CF=0.0068 Previous template value: 0.2000 (replaced)
Note on J410: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3602 Previous template value: 0.2400 (replaced)
Note on J411: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2657 Previous template value: 0.2400 (replaced)
Note on J412: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3704 Previous template value: 0.2400 (replaced)
Note on J413: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2454 Previous template value: 0.3500 (replaced)
Note on J414: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2144 Previous template value: 0.3500 (replaced)
Note on J415: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2453 Previous template value: 0.3500 (replaced)
Note on J416: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.6386 Previous template value: 0.5200 (replaced)
Note on J417: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.5911 Previous template value: 0.5200 (replaced)
Note on J418: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.5925 Previous template value: 0.5200 (replaced)
Note on J419: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2973
Note on J420: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2740 Previous template value: 0.3000 (replaced)
Note on J421: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=wind Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2880 Previous template value: 0.3000 (replaced)
Note on J422: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2197 Previous template value: 0.2000 (replaced)
Note on J423: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2336 Previous template value: 0.2000 (replaced)
Note on J424: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2403 Previous template value: 0.2000 (replaced)
Note on J425: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2355 Previous template value: 0.2000 (replaced)
Note on J426: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2354 Previous template value: 0.2000 (replaced)
Note on J427: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2346 Previous template value: 0.2000 (replaced)
Note on J428: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2358 Previous template value: 0.2000 (replaced)
Note on J429: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2306 Previous template value: 0.2000 (replaced)
Note on J430: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2291 Previous template value: 0.2000 (replaced)
Note on J431: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3093 Previous template value: 0.2000 (replaced)
Note on J432: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3146 Previous template value: 0.2000 (replaced)
Note on J433: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=wind Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3002 Previous template value: 0.2000 (replaced)
Note on J434: AMBIGUITY: Existing=0.1950, Renewables.ninja (2014-2022 mean)=0.3006 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration) Pre-integration value (~0.35-0.43). Plausible for Gulf of Mannar/Tamil Nadu coast. Cross-ref: CEA NEP offshore wind assessment; WB/NREL offshore wind roadmap.
Note on J435: AMBIGUITY: Existing=0.1950, Renewables.ninja (2014-2022 mean)=0.2360 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration)
Note on J436: AMBIGUITY: Existing=0.1950, Renewables.ninja (2014-2022 mean)=0.6001 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration)
Note on J437: Confirmed by Renewables.ninja (2014-2022 mean)=0.3022 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806
Note on J438: AMBIGUITY: Existing=0.3120, Renewables.ninja (2014-2022 mean)=0.1978 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration)
Note on J439: AMBIGUITY: Existing=0.3120, Renewables.ninja (2014-2022 mean)=0.4930 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration)
Note on J440: AMBIGUITY: Existing=0.4290, Renewables.ninja (2014-2022 mean)=0.4714 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration)
Note on J441: AMBIGUITY: Existing=0.4290, Renewables.ninja (2014-2022 mean)=0.5809 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration)
Note on J442: AMBIGUITY: Existing=0.4290, Renewables.ninja (2014-2022 mean)=0.4876 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration)
Note on J443: Confirmed by Renewables.ninja (2014-2022 mean)=0.2601 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806
Note on J444: Confirmed by Renewables.ninja (2014-2022 mean)=0.2646 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806
Note on J445: AMBIGUITY: Existing=0.2600, Renewables.ninja (2014-2022 mean)=0.3699 Source: compiled_reninja_ts.csv ¦ region=INDSO ¦ lat=12.9724, lon=77.5806 Existing source: unknown (pre-integration)
Note on J446: AMBIGUITY: Existing=0.2750, Renewables.ninja (2014-2022 mean)=0.3138 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration) Pre-integration value (~0.35-0.45). Plausible for Gujarat coast. Cross-ref: MNRE offshore wind assessment; India's 37 GW offshore wind target.
Note on J447: AMBIGUITY: Existing=0.2750, Renewables.ninja (2014-2022 mean)=0.1748 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J448: AMBIGUITY: Existing=0.2750, Renewables.ninja (2014-2022 mean)=0.3366 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J449: AMBIGUITY: Existing=0.3375, Renewables.ninja (2014-2022 mean)=0.1224 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J450: AMBIGUITY: Existing=0.3375, Renewables.ninja (2014-2022 mean)=0.2174 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J451: AMBIGUITY: Existing=0.3375, Renewables.ninja (2014-2022 mean)=0.2622 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J452: AMBIGUITY: Existing=0.4500, Renewables.ninja (2014-2022 mean)=0.4692 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J453: AMBIGUITY: Existing=0.4500, Renewables.ninja (2014-2022 mean)=0.4968 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J454: Confirmed by Renewables.ninja (2014-2022 mean)=0.4584 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857
Note on J455: AMBIGUITY: Existing=0.3000, Renewables.ninja (2014-2022 mean)=0.3102 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J456: AMBIGUITY: Existing=0.3000, Renewables.ninja (2014-2022 mean)=0.1460 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J457: AMBIGUITY: Existing=0.3000, Renewables.ninja (2014-2022 mean)=0.2168 Source: compiled_reninja_ts.csv ¦ region=INDWE ¦ lat=19.017, lon=72.857 Existing source: unknown (pre-integration)
Note on J458: Confirmed by Renewables.ninja (2014-2022 mean)=0.2451 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Pre-integration value (~0.20-0.25). Lower CF consistent with Bay of Bengal wind resource.
Note on J459: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.1191 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J460: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.1672 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J461: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.3444 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J462: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.2689 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J463: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.4717 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J464: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.3355 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J465: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.3230 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J466: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.4372 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J467: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.1851 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J468: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.0876 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J469: AMBIGUITY: Existing=0.2500, Renewables.ninja (2014-2022 mean)=0.1278 Source: compiled_reninja_ts.csv ¦ region=INDEA ¦ lat=22.495, lon=88.3247 Existing source: unknown (pre-integration)
Note on J470: AMBIGUITY: Existing=0.1500, Renewables.ninja (2014-2022 mean)=0.1827 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration) Pre-integration value (~0.35-0.45). Bay of Bengal. Limited offshore wind data for BD.
Note on J471: AMBIGUITY: Existing=0.1500, Renewables.ninja (2014-2022 mean)=0.0730 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J472: AMBIGUITY: Existing=0.1500, Renewables.ninja (2014-2022 mean)=0.1776 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J473: AMBIGUITY: Existing=0.2250, Renewables.ninja (2014-2022 mean)=0.3122 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J474: AMBIGUITY: Existing=0.2250, Renewables.ninja (2014-2022 mean)=0.1885 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J475: AMBIGUITY: Existing=0.2250, Renewables.ninja (2014-2022 mean)=0.4045 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J476: AMBIGUITY: Existing=0.4500, Renewables.ninja (2014-2022 mean)=0.3461 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J477: AMBIGUITY: Existing=0.4500, Renewables.ninja (2014-2022 mean)=0.3106 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J478: AMBIGUITY: Existing=0.4500, Renewables.ninja (2014-2022 mean)=0.3991 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J479: AMBIGUITY: Existing=0.1750, Renewables.ninja (2014-2022 mean)=0.1246 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J480: AMBIGUITY: Existing=0.1750, Renewables.ninja (2014-2022 mean)=0.0613 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J481: AMBIGUITY: Existing=0.1750, Renewables.ninja (2014-2022 mean)=0.1085 Source: compiled_reninja_ts.csv ¦ region=BGDXX ¦ lat=23.7231, lon=90.4086 Existing source: unknown (pre-integration)
Note on J482: AMBIGUITY: Existing=0.2880, Renewables.ninja (2014-2022 mean)=0.3602 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration) Pre-integration value (~0.48-0.62). Consistent with Mannar Basin wind resource (ADB Mannar Wind study). Higher CFs than typical due to narrow strait acceleration.
Note on J483: AMBIGUITY: Existing=0.2880, Renewables.ninja (2014-2022 mean)=0.2657 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J484: AMBIGUITY: Existing=0.2880, Renewables.ninja (2014-2022 mean)=0.3704 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J485: AMBIGUITY: Existing=0.4200, Renewables.ninja (2014-2022 mean)=0.2454 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J486: AMBIGUITY: Existing=0.4200, Renewables.ninja (2014-2022 mean)=0.2144 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J487: AMBIGUITY: Existing=0.4200, Renewables.ninja (2014-2022 mean)=0.2453 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J488: AMBIGUITY: Existing=0.6240, Renewables.ninja (2014-2022 mean)=0.6386 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J489: AMBIGUITY: Existing=0.6240, Renewables.ninja (2014-2022 mean)=0.5911 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J490: AMBIGUITY: Existing=0.6240, Renewables.ninja (2014-2022 mean)=0.5925 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J491: AMBIGUITY: Existing=0.3600, Renewables.ninja (2014-2022 mean)=0.2973 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J492: AMBIGUITY: Existing=0.3600, Renewables.ninja (2014-2022 mean)=0.2740 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J493: AMBIGUITY: Existing=0.3600, Renewables.ninja (2014-2022 mean)=0.2880 Source: compiled_reninja_ts.csv ¦ region=LKAXX ¦ lat=6.932, lon=79.8578 Existing source: unknown (pre-integration)
Note on J494: AMBIGUITY: Existing=0.2400, Renewables.ninja (2014-2022 mean)=0.2197 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997 Existing source: unknown (pre-integration) Pre-integration value (~0.19-0.24). Low — consistent with equatorial location. Limited offshore wind potential.
Note on J495: Confirmed by Renewables.ninja (2014-2022 mean)=0.2336 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997
Note on J496: Confirmed by Renewables.ninja (2014-2022 mean)=0.2403 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997
Note on J497: Confirmed by Renewables.ninja (2014-2022 mean)=0.2355 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997
Note on J498: Confirmed by Renewables.ninja (2014-2022 mean)=0.2354 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997
Note on J499: Confirmed by Renewables.ninja (2014-2022 mean)=0.2346 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997
Note on J500: Confirmed by Renewables.ninja (2014-2022 mean)=0.2358 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997
Note on J501: Confirmed by Renewables.ninja (2014-2022 mean)=0.2306 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997
Note on J502: AMBIGUITY: Existing=0.2400, Renewables.ninja (2014-2022 mean)=0.2291 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997 Existing source: unknown (pre-integration)
Note on J503: AMBIGUITY: Existing=0.2400, Renewables.ninja (2014-2022 mean)=0.3093 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997 Existing source: unknown (pre-integration)
Note on J504: AMBIGUITY: Existing=0.2400, Renewables.ninja (2014-2022 mean)=0.3146 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997 Existing source: unknown (pre-integration)
Note on J505: AMBIGUITY: Existing=0.2400, Renewables.ninja (2014-2022 mean)=0.3002 Source: compiled_reninja_ts.csv ¦ region=MDVXX ¦ lat=1.925, lon=73.3997 Existing source: unknown (pre-integration)
Note on J506: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J507: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J508: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J509: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J510: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J511: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J512: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J513: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J514: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J515: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J516: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J517: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J518: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC IRENA cross-check: weighted annual CF=0.453. IRENA 2023 reports 52%. Difference=0.067. Source: IRENA Energy Profile Bhutan (Sep 2025), Bhutan_new_data_v2 6_IRENA_Capacity_Factors.
Note on J519: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2406 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J520: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2430 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J521: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2125 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J522: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2282 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J523: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2304 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J524: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.9414 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J525: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=1.0000 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J526: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=1.0000 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J527: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.6871 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J528: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.7378 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J529: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.7450 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J530: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J531: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J532: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J533: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J534: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J535: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J536: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J537: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J538: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J539: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J540: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J541: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J542: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J543: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J544: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J545: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J546: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J547: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J548: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J549: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J550: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J551: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J552: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J553: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J554: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J555: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J556: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J557: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J558: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J559: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J560: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J561: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J562: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J563: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J564: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J565: Pre-integration value. Likely from OSeMOSYS Global seasonal hydro profile or literature estimate. ⚠ NOT YET VERIFIED against DA_Final or national statistics.
Note on J566: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants). IRENA cross-check: weighted annual CF=0.404. IRENA 2023 hydro/marine=37%. Diff=0.034. Source: IRENA Energy Profile Sri Lanka, SriLanka__new_data_v2 IRENA–Capacity Factors.
Note on J567: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J568: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J569: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J570: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J571: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J572: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J573: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J574: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J575: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J576: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J577: Major Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023 (15 plants).
Note on J578: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J579: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J580: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J581: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J582: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J583: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J584: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J585: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J586: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J587: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J588: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J589: RoR Hydro CF from NP_DA_Final. Source: NEA FY2079/80 gen + NREL hourly shape [DATA+EST]
Note on J590: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2241 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J591: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2406 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J592: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2430 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J593: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2125 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J594: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2282 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J595: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.2304 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J596: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.9414 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J597: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=1.0000 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J598: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=1.0000 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J599: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.6871 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J600: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.7378 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J601: Hydro CF from BTN_DA_Final. Source: BPSO Q1-Q4 2024 ex-bus + quarterly IC ⚠ DUAL OPTION: Current uses BPSO 2024 (annual CF≈0.453). Alternative IRENA-scaled value=0.7450 (annual CF≈0.52). See Capacities_CF_Options sheet for full comparison.
Note on J602: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J603: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J604: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J605: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J606: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J607: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J608: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J609: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J610: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J611: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J612: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J613: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J614: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J615: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J616: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J617: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J618: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J619: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J620: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J621: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J622: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J623: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J624: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J625: Pre-integration value. Likely from OSeMOSYS Global RoR profile. ⚠ NOT YET VERIFIED.
Note on J626: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J627: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J628: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J629: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J630: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J631: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J632: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J633: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J634: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J635: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J636: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J637: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J638: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J639: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J640: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J641: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J642: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J643: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J644: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J645: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J646: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J647: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J648: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J649: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J650: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J651: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J652: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J653: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J654: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J655: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J656: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J657: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J658: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J659: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J660: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J661: Pre-integration value (1.0 = fully available). Pumped storage availability — verify if seasonal constraint needed.
Note on J662: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J663: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J664: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J665: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J666: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J667: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J668: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J669: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J670: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J671: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J672: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J673: Storage Hydro CF from NP_DA_Final. Source: Kulekhani dispatch pattern [ESTIMATED] ⚠ ESTIMATED — confidence: MEDIUM
Note on J674: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J675: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J676: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J677: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J678: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J679: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J680: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J681: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J682: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J683: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J684: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J685: Mini Hydro CF from LKA_DA_Final. Source: PUCSL 15-min dispatch 2023.
Note on J686: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J687: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J688: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J689: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J690: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J691: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J692: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J693: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J694: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J695: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J696: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J697: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J698: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J699: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J700: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J701: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J702: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J703: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J704: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J705: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J706: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J707: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J708: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J709: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J710: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J711: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J712: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J713: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J714: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J715: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J716: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J717: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J718: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J719: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J720: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J721: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J722: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J723: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J724: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J725: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J726: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J727: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J728: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J729: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J730: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J731: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J732: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J733: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J734: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J735: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J736: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J737: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J738: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J739: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J740: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J741: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J742: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J743: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J744: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J745: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J746: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J747: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J748: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J749: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J750: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J751: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J752: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J753: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J754: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J755: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J756: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J757: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J758: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J759: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J760: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J761: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J762: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J763: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J764: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J765: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J766: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J767: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J768: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J769: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J770: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J771: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J772: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J773: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J774: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J775: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J776: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J777: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J778: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J779: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J780: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J781: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J782: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J783: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J784: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J785: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J786: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J787: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J788: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J789: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J790: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J791: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J792: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J793: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J794: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J795: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J796: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J797: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J798: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J799: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J800: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J801: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J802: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J803: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J804: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J805: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J806: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J807: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J808: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J809: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J810: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J811: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J812: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J813: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J814: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J815: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J816: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J817: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J818: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J819: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J820: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J821: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J822: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J823: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J824: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J825: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J826: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J827: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J828: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J829: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J830: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J831: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J832: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J833: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J834: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J835: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J836: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J837: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J838: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J839: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J840: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J841: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J842: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J843: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J844: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J845: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J846: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J847: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J848: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J849: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J850: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J851: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J852: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J853: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J854: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J855: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J856: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J857: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J858: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J859: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J860: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J861: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J862: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J863: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J864: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J865: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J866: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J867: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J868: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J869: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J870: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J871: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J872: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J873: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J874: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J875: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J876: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J877: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J878: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J879: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J880: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J881: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J882: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J883: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J884: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J885: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J886: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J887: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J888: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J889: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J890: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J891: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J892: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J893: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J894: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J895: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J896: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J897: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J898: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J899: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J900: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J901: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J902: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J903: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J904: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J905: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J906: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J907: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J908: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J909: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J910: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J911: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J912: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J913: Storage CF=1.0 (available all timeslices; optimizer decides charge/discharge). Corrected: was erroneously zeroed during thermal CF cleanup.
Note on J914: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J915: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J916: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J917: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J918: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J919: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J920: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J921: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J922: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J923: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J924: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J925: Storage tech — CF=1.0 by design (optimizer decides charge/discharge).
Note on J926: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J927: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.4307 Previous template value: 0.5000 (replaced)
Note on J928: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J929: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J930: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3957 Previous template value: 0.5200 (replaced)
Note on J931: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J932: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J933: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3231 Previous template value: 0.4200 (replaced)
Note on J934: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J935: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J936: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.3642 Previous template value: 0.4750 (replaced)
Note on J937: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDSO ¦ resource=solar Coordinates: lat=12.9724, lon=77.5806 9-year mean CF=0.0000
Note on J938: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0001
Note on J939: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3516 Previous template value: 0.4400 (replaced)
Note on J940: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on J941: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0065
Note on J942: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3866 Previous template value: 0.4700 (replaced)
Note on J943: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on J944: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0056
Note on J945: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.2645 Previous template value: 0.3800 (replaced)
Note on J946: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on J947: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0003
Note on J948: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.3348 Previous template value: 0.4300 (replaced)
Note on J949: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=INDEA ¦ resource=solar Coordinates: lat=22.495, lon=88.3247 9-year mean CF=0.0000
Note on J950: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J951: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3524 Previous template value: 0.2480 (replaced)
Note on J952: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J953: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J954: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3797 Previous template value: 0.3240 (replaced)
Note on J955: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J956: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0001
Note on J957: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.2891 Previous template value: 0.2990 (replaced)
Note on J958: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J959: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J960: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.3421 Previous template value: 0.3600 (replaced)
Note on J961: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=BGDXX ¦ resource=solar Coordinates: lat=23.7231, lon=90.4086 9-year mean CF=0.0000
Note on J962: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J963: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3758 Previous template value: 0.4300 (replaced)
Note on J964: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J965: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J966: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3307 Previous template value: 0.4500 (replaced)
Note on J967: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J968: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J969: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.3036 Previous template value: 0.3400 (replaced)
Note on J970: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J971: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J972: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.2942 Previous template value: 0.3800 (replaced)
Note on J973: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=LKAXX ¦ resource=solar Coordinates: lat=6.932, lon=79.8578 9-year mean CF=0.0000
Note on J974: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J975: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3533 Previous template value: 0.3930 (replaced)
Note on J976: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J977: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J978: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3372 Previous template value: 0.3930 (replaced)
Note on J979: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J980: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J981: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.2915 Previous template value: 0.3930 (replaced)
Note on J982: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J983: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J984: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.3098 Previous template value: 0.3930 (replaced)
Note on J985: Source: Renewables.ninja (2014-2022 mean) File: compiled_reninja_ts.csv ¦ region=MDVXX ¦ resource=solar Coordinates: lat=1.925, lon=73.3997 9-year mean CF=0.0000
Note on J986: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J987: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J988: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J989: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J990: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J991: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J992: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J993: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J994: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J995: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J996: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J997: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J998: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J999: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1000: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1001: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1002: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1003: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1004: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1005: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1006: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1007: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1008: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.
Note on J1009: Pre-integration value. Tidal CF estimate. ⚠ SOURCE UNKNOWN — limited tidal deployment in region.

## VariableCost
Mode.Operation | Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Parameter | Projection.Mode | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | 1 | MINCOABD | Coal mining/import, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.28 | 4.26 | 4.24 | 4.22 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
1 | 2 | MINCOABT | Coal mining/import, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.28 | 4.26 | 4.24 | 4.22 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
1 | 3 | MINCOAIN_N | Coal mining/import, India – North | 12 | VariableCost | USD/GJ | 0 | User defined | 2.2 | 2.2 | 2.2 | 2.24 | 2.28 | 2.32 | 2.36 | 2.4 | 2.42 | 2.44 | 2.46 | 2.48 | 2.5 | 2.52 | 2.54 | 2.56 | 2.58 | 2.6 | 2.62 | 2.64 | 2.66 | 2.68 | 2.7 | 2.72 | 2.74 | 2.76 | 2.78 | 2.8
1 | 4 | MINCOAIN_S | Coal mining/import, India – South | 12 | VariableCost | USD/GJ | 0 | User defined | 2.2 | 2.2 | 2.2 | 2.24 | 2.28 | 2.32 | 2.36 | 2.4 | 2.42 | 2.44 | 2.46 | 2.48 | 2.5 | 2.52 | 2.54 | 2.56 | 2.58 | 2.6 | 2.62 | 2.64 | 2.66 | 2.68 | 2.7 | 2.72 | 2.74 | 2.76 | 2.78 | 2.8
1 | 5 | MINCOAIN_E | Coal mining/import, India – East | 12 | VariableCost | USD/GJ | 0 | User defined | 2.2 | 2.2 | 2.2 | 2.24 | 2.28 | 2.32 | 2.36 | 2.4 | 2.42 | 2.44 | 2.46 | 2.48 | 2.5 | 2.52 | 2.54 | 2.56 | 2.58 | 2.6 | 2.62 | 2.64 | 2.66 | 2.68 | 2.7 | 2.72 | 2.74 | 2.76 | 2.78 | 2.8
1 | 6 | MINCOAIN_W | Coal mining/import, India – West | 12 | VariableCost | USD/GJ | 0 | User defined | 2.2 | 2.2 | 2.2 | 2.24 | 2.28 | 2.32 | 2.36 | 2.4 | 2.42 | 2.44 | 2.46 | 2.48 | 2.5 | 2.52 | 2.54 | 2.56 | 2.58 | 2.6 | 2.62 | 2.64 | 2.66 | 2.68 | 2.7 | 2.72 | 2.74 | 2.76 | 2.78 | 2.8
1 | 7 | MINCOAIN_NE | Coal mining/import, India – Northeast | 12 | VariableCost | USD/GJ | 0 | User defined | 2.2 | 2.2 | 2.2 | 2.24 | 2.28 | 2.32 | 2.36 | 2.4 | 2.42 | 2.44 | 2.46 | 2.48 | 2.5 | 2.52 | 2.54 | 2.56 | 2.58 | 2.6 | 2.62 | 2.64 | 2.66 | 2.68 | 2.7 | 2.72 | 2.74 | 2.76 | 2.78 | 2.8
1 | 8 | MINCOANP | Coal mining/import, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.28 | 4.26 | 4.24 | 4.22 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
1 | 9 | MINCOALK | Coal mining/import, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.28 | 4.26 | 4.24 | 4.22 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
1 | 10 | MINCOAMV | Coal mining/import, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 6.9 | 5.6 | 4.3 | 4.28 | 4.26 | 4.24 | 4.22 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
1 | 11 | MINGASBD | Natural Gas supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 5.5 | 5.5 | 5.5 | 5.7 | 5.9 | 6.1 | 6.3 | 6.5 | 6.8 | 7.1 | 7.4 | 7.7 | 8 | 8.2 | 8.4 | 8.6 | 8.8 | 9 | 9.1 | 9.2 | 9.3 | 9.4 | 9.5 | 9.6 | 9.7 | 9.8 | 9.9 | 10
1 | 12 | MINGASBT | Natural Gas supply, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.2 | 10.3 | 10.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
1 | 13 | MINGASIN_N | Natural Gas supply, India – North | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.2 | 10.3 | 10.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
1 | 14 | MINGASIN_S | Natural Gas supply, India – South | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.2 | 10.3 | 10.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
1 | 15 | MINGASIN_E | Natural Gas supply, India – East | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.2 | 10.3 | 10.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
1 | 16 | MINGASIN_W | Natural Gas supply, India – West | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.2 | 10.3 | 10.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
1 | 17 | MINGASIN_NE | Natural Gas supply, India – Northeast | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.2 | 10.3 | 10.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
1 | 18 | MINGASNP | Natural Gas supply, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.2 | 10.3 | 10.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
1 | 19 | MINGASLK | Natural Gas supply, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 13.6 | 12.75 | 11.9 | 11.52 | 11.14 | 10.76 | 10.38 | 10 | 10 | 10 | 10 | 10 | 10 | 10.1 | 10.2 | 10.3 | 10.4 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
1 | 20 | MINGASMV | Natural Gas supply, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 24.5 | 22.75 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
1 | 21 | MINOILBD | Oil supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.74 | 14.68 | 14.62 | 14.56 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
1 | 22 | MINOILBT | Oil supply, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.74 | 14.68 | 14.62 | 14.56 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
1 | 23 | MINOILIN_N | Oil supply, India – North | 12 | VariableCost | USD/GJ | 0 | User defined | 13.562 | 13.317 | 13.072 | 13.137 | 13.203 | 13.268 | 13.333 | 13.399 | 13.66 | 13.922 | 14.183 | 14.444 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706
1 | 24 | MINOILIN_S | Oil supply, India – South | 12 | VariableCost | USD/GJ | 0 | User defined | 13.562 | 13.317 | 13.072 | 13.137 | 13.203 | 13.268 | 13.333 | 13.399 | 13.66 | 13.922 | 14.183 | 14.444 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706
1 | 25 | MINOILIN_E | Oil supply, India – East | 12 | VariableCost | USD/GJ | 0 | User defined | 13.562 | 13.317 | 13.072 | 13.137 | 13.203 | 13.268 | 13.333 | 13.399 | 13.66 | 13.922 | 14.183 | 14.444 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706
1 | 26 | MINOILIN_W | Oil supply, India – West | 12 | VariableCost | USD/GJ | 0 | User defined | 13.562 | 13.317 | 13.072 | 13.137 | 13.203 | 13.268 | 13.333 | 13.399 | 13.66 | 13.922 | 14.183 | 14.444 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706
1 | 27 | MINOILIN_NE | Oil supply, India – Northeast | 12 | VariableCost | USD/GJ | 0 | User defined | 13.562 | 13.317 | 13.072 | 13.137 | 13.203 | 13.268 | 13.333 | 13.399 | 13.66 | 13.922 | 14.183 | 14.444 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706 | 14.706
1 | 28 | MINOILNP | Oil supply, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.74 | 14.68 | 14.62 | 14.56 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
1 | 29 | MINOILLK | Oil supply, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 18 | 16.4 | 14.8 | 14.74 | 14.68 | 14.62 | 14.56 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
1 | 30 | MINOILMV | Oil supply, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 24.5 | 22.75 | 21 | 20.8 | 20.6 | 20.4 | 20.2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
1 | 31 | MINURNBD | Uranium supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 32 | MINURNBT | Uranium supply, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 33 | MINURNIN_N | Uranium supply, India – North | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 34 | MINURNIN_S | Uranium supply, India – South | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 35 | MINURNIN_E | Uranium supply, India – East | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 36 | MINURNIN_W | Uranium supply, India – West | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 37 | MINURNIN_NE | Uranium supply, India – Northeast | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 38 | MINURNNP | Uranium supply, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 39 | MINURNLK | Uranium supply, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 40 | MINURNMV | Uranium supply, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
1 | 41 | MINBIOBD | Biomass supply, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 42 | MINBIOBT | Biomass supply, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 43 | MINBIOIN_N | Biomass supply, India – North | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 44 | MINBIOIN_S | Biomass supply, India – South | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 45 | MINBIOIN_E | Biomass supply, India – East | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 46 | MINBIOIN_W | Biomass supply, India – West | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 47 | MINBIOIN_NE | Biomass supply, India – Northeast | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 48 | MINBIONP | Biomass supply, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 49 | MINBIOLK | Biomass supply, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 50 | MINBIOMV | Biomass supply, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined | 4 | 4 | 4 | 4.04 | 4.08 | 4.12 | 4.16 | 4.2 | 4.24 | 4.28 | 4.32 | 4.36 | 4.4 | 4.44 | 4.48 | 4.52 | 4.56 | 4.6 | 4.64 | 4.68 | 4.72 | 4.76 | 4.8 | 4.84 | 4.88 | 4.92 | 4.96 | 5
1 | 51 | MINH2GBD | Green hydrogen production, Bangladesh | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 52 | MINH2GBT | Green hydrogen production, Bhutan | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 53 | MINH2GIN_N | Green hydrogen production, India – North | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 54 | MINH2GIN_S | Green hydrogen production, India – South | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 55 | MINH2GIN_E | Green hydrogen production, India – East | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 56 | MINH2GIN_W | Green hydrogen production, India – West | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 57 | MINH2GIN_NE | Green hydrogen production, India – Northeast | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 58 | MINH2GNP | Green hydrogen production, Nepal | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 59 | MINH2GLK | Green hydrogen production, Sri Lanka | 12 | VariableCost | USD/GJ | 0 | User defined
1 | 60 | MINH2GMV | Green hydrogen production, Maldives | 12 | VariableCost | USD/GJ | 0 | User defined
Note on J2: Fuel: Imported coal (FOB Aus) ¦ Nodes: BD,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 ($107/t FOB, 25 GJ/t) Projection: WEO 2025 + DESNZ Low/Central/High ¦ https://assets.publishing.service.gov.uk/media/66f3e1a8080bdf716392e855/2024-Fossil-Fuel-price-Assumptions-Publication.pdf Unit in CostDB: USD/GJ Notes: 2023 was anomalous (Ukraine war). C=flat real post-2027. A=NZE mine closures.
Note on J3: Fuel: Imported coal (FOB Aus) ¦ Nodes: BD,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 ($107/t FOB, 25 GJ/t) Projection: WEO 2025 + DESNZ Low/Central/High ¦ https://assets.publishing.service.gov.uk/media/66f3e1a8080bdf716392e855/2024-Fossil-Fuel-price-Assumptions-Publication.pdf Unit in CostDB: USD/GJ Notes: 2023 was anomalous (Ukraine war). C=flat real post-2027. A=NZE mine closures.
Note on J4: Fuel: India domestic coal ¦ Nodes: IN_all ¦ Scenario: Conservative Source: Coal India grade pricing + transport Projection: Modest real increase (C/M); decline if demand drops (A) Unit in CostDB: USD/GJ Notes: Pithead cost + rail transport. IN_E lowest, IN_S/W highest.
Note on J5: Fuel: India domestic coal ¦ Nodes: IN_all ¦ Scenario: Conservative Source: Coal India grade pricing + transport Projection: Modest real increase (C/M); decline if demand drops (A) Unit in CostDB: USD/GJ Notes: Pithead cost + rail transport. IN_E lowest, IN_S/W highest.
Note on J6: Fuel: India domestic coal ¦ Nodes: IN_all ¦ Scenario: Conservative Source: Coal India grade pricing + transport Projection: Modest real increase (C/M); decline if demand drops (A) Unit in CostDB: USD/GJ Notes: Pithead cost + rail transport. IN_E lowest, IN_S/W highest.
Note on J7: Fuel: India domestic coal ¦ Nodes: IN_all ¦ Scenario: Conservative Source: Coal India grade pricing + transport Projection: Modest real increase (C/M); decline if demand drops (A) Unit in CostDB: USD/GJ Notes: Pithead cost + rail transport. IN_E lowest, IN_S/W highest.
Note on J8: Fuel: India domestic coal ¦ Nodes: IN_all ¦ Scenario: Conservative Source: Coal India grade pricing + transport Projection: Modest real increase (C/M); decline if demand drops (A) Unit in CostDB: USD/GJ Notes: Pithead cost + rail transport. IN_E lowest, IN_S/W highest.
Note on J9: Fuel: Imported coal (FOB Aus) ¦ Nodes: BD,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 ($107/t FOB, 25 GJ/t) Projection: WEO 2025 + DESNZ Low/Central/High ¦ https://assets.publishing.service.gov.uk/media/66f3e1a8080bdf716392e855/2024-Fossil-Fuel-price-Assumptions-Publication.pdf Unit in CostDB: USD/GJ Notes: 2023 was anomalous (Ukraine war). C=flat real post-2027. A=NZE mine closures.
Note on J10: Fuel: Imported coal (FOB Aus) ¦ Nodes: BD,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 ($107/t FOB, 25 GJ/t) Projection: WEO 2025 + DESNZ Low/Central/High ¦ https://assets.publishing.service.gov.uk/media/66f3e1a8080bdf716392e855/2024-Fossil-Fuel-price-Assumptions-Publication.pdf Unit in CostDB: USD/GJ Notes: 2023 was anomalous (Ukraine war). C=flat real post-2027. A=NZE mine closures.
Note on J11: Fuel: Imported coal (FOB Aus) ¦ Nodes: BD,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 ($107/t FOB, 25 GJ/t) Projection: WEO 2025 + DESNZ Low/Central/High ¦ https://assets.publishing.service.gov.uk/media/66f3e1a8080bdf716392e855/2024-Fossil-Fuel-price-Assumptions-Publication.pdf Unit in CostDB: USD/GJ Notes: 2023 was anomalous (Ukraine war). C=flat real post-2027. A=NZE mine closures.
Note on J12: Fuel: Bangladesh piped gas ¦ Nodes: BD ¦ Scenario: Conservative Source: WB BD ESSEP (~$5.79/MMBtu) ¦ https://www.worldbank.org Projection: C=LNG convergence; M=WB anchor; A=subsidy continuation Unit in CostDB: USD/GJ Notes: Most consequential fuel uncertainty for BD node. C models rapid LNG convergence.
Note on J13: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on J14: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on J15: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on J16: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on J17: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on J18: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on J19: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on J20: Fuel: LNG (Asia/JKM) ¦ Nodes: IN_W,IN_S,LK ¦ Scenario: Conservative Source: WB CMO Oct 2025 (JKM CIF) Projection: WEO 2025 STEPS/NZE + DESNZ Unit in CostDB: USD/GJ Notes: WEO: EU LNG STEPS 2035=$6.2/MBtu; Asia +$1-2 premium. A=NZE $4/MBtu.
Note on J21: Fuel: Diesel (Maldives) ¦ Nodes: MV ¦ Scenario: Conservative Source: ADB Maldives Energy Roadmap ¦ https://www.environment.gov.mv/v2/wp-content/files/publications/20241107-pub-energy-roadmap-maldives-2024-2033-.pdf Projection: Island premium + oil scenario Unit in CostDB: USD/GJ Notes: Fuel =~13.5% of GDP. $0.30-0.70/kWh generation cost. Island logistics premium.
Note on J22: Fuel: Diesel / HFO ¦ Nodes: LK,MV ¦ Scenario: Conservative Source: CEB LTGEP + WB Brent trajectory ¦ https://www.ceb.lk Projection: Scaled from oil price scenarios Unit in CostDB: USD/GJ Notes: MV add $4-7/GJ island delivery premium. C=flat post-2027. A=NZE oil collapse.
Note on J23: Fuel: Diesel / HFO ¦ Nodes: LK,MV ¦ Scenario: Conservative Source: CEB LTGEP + WB Brent trajectory ¦ https://www.ceb.lk Projection: Scaled from oil price scenarios Unit in CostDB: USD/GJ Notes: MV add $4-7/GJ island delivery premium. C=flat post-2027. A=NZE oil collapse.
Note on J24: Fuel: Crude oil (Brent) ¦ Nodes: All ¦ Scenario: Conservative Source: WB CMO Oct 2025 Projection: IEA WEO 2025 STEPS/CPS/NZE ¦ https://www.iea.org/reports/world-energy-outlook-2025 Unit in CostDB: USD/bbl → converted to USD/GJ (÷6.12 GJ/bbl) Notes: C=CPS ~10% above STEPS. M=STEPS verified IISD. A=NZE verified IISD. 2023 USD.
Note on J25: Fuel: Crude oil (Brent) ¦ Nodes: All ¦ Scenario: Conservative Source: WB CMO Oct 2025 Projection: IEA WEO 2025 STEPS/CPS/NZE ¦ https://www.iea.org/reports/world-energy-outlook-2025 Unit in CostDB: USD/bbl → converted to USD/GJ (÷6.12 GJ/bbl) Notes: C=CPS ~10% above STEPS. M=STEPS verified IISD. A=NZE verified IISD. 2023 USD.
Note on J26: Fuel: Crude oil (Brent) ¦ Nodes: All ¦ Scenario: Conservative Source: WB CMO Oct 2025 Projection: IEA WEO 2025 STEPS/CPS/NZE ¦ https://www.iea.org/reports/world-energy-outlook-2025 Unit in CostDB: USD/bbl → converted to USD/GJ (÷6.12 GJ/bbl) Notes: C=CPS ~10% above STEPS. M=STEPS verified IISD. A=NZE verified IISD. 2023 USD.
Note on J27: Fuel: Crude oil (Brent) ¦ Nodes: All ¦ Scenario: Conservative Source: WB CMO Oct 2025 Projection: IEA WEO 2025 STEPS/CPS/NZE ¦ https://www.iea.org/reports/world-energy-outlook-2025 Unit in CostDB: USD/bbl → converted to USD/GJ (÷6.12 GJ/bbl) Notes: C=CPS ~10% above STEPS. M=STEPS verified IISD. A=NZE verified IISD. 2023 USD.
Note on J28: Fuel: Crude oil (Brent) ¦ Nodes: All ¦ Scenario: Conservative Source: WB CMO Oct 2025 Projection: IEA WEO 2025 STEPS/CPS/NZE ¦ https://www.iea.org/reports/world-energy-outlook-2025 Unit in CostDB: USD/bbl → converted to USD/GJ (÷6.12 GJ/bbl) Notes: C=CPS ~10% above STEPS. M=STEPS verified IISD. A=NZE verified IISD. 2023 USD.
Note on J29: Fuel: Diesel / HFO ¦ Nodes: LK,MV ¦ Scenario: Conservative Source: CEB LTGEP + WB Brent trajectory ¦ https://www.ceb.lk Projection: Scaled from oil price scenarios Unit in CostDB: USD/GJ Notes: MV add $4-7/GJ island delivery premium. C=flat post-2027. A=NZE oil collapse.
Note on J30: Fuel: Diesel / HFO ¦ Nodes: LK,MV ¦ Scenario: Conservative Source: CEB LTGEP + WB Brent trajectory ¦ https://www.ceb.lk Projection: Scaled from oil price scenarios Unit in CostDB: USD/GJ Notes: MV add $4-7/GJ island delivery premium. C=flat post-2027. A=NZE oil collapse.
Note on J31: Fuel: Diesel (Maldives) ¦ Nodes: MV ¦ Scenario: Conservative Source: ADB Maldives Energy Roadmap ¦ https://www.environment.gov.mv/v2/wp-content/files/publications/20241107-pub-energy-roadmap-maldives-2024-2033-.pdf Projection: Island premium + oil scenario Unit in CostDB: USD/GJ Notes: Fuel =~13.5% of GDP. $0.30-0.70/kWh generation cost. Island logistics premium.
Note on J32: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J33: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J34: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J35: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J36: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J37: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J38: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J39: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J40: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J41: Fuel: Uranium ¦ Nodes: IN,BD,LK ¦ Scenario: Conservative Source: WNA; NEI 2025 ($5.40/MWh US fleet) ¦ https://world-nuclear.org/information-library/economic-aspects/economics-of-nuclear-power Projection: Flat (not scenario-sensitive) Unit in CostDB: USD/GJ Notes: ATB: $9.1-11.3/MWh. WNA: $5.0-7.1/MWh. ~17% of total nuclear gen cost.
Note on J42: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J43: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J44: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J45: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J46: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J47: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J48: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J49: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J50: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on J51: Fuel: Biomass ¦ Nodes: IN,LK ¦ Scenario: Conservative Source: CERC FY2024-25 benchmark (GCV 3,100 kcal/kg) Projection: C=scarcity premium; M=modest increase; A=supply chain improvement Unit in CostDB: USD/GJ Notes: SL: coconut shell/wood waste $2-3.5/GJ. India CERC normative price.
Note on AK52: ⚠ No fuel cost mapping for MINH2GBD
Note on AK53: ⚠ No fuel cost mapping for MINH2GBT
Note on AK54: ⚠ No fuel cost mapping for MINH2GIN_N
Note on AK55: ⚠ No fuel cost mapping for MINH2GIN_S
Note on AK56: ⚠ No fuel cost mapping for MINH2GIN_E
Note on AK57: ⚠ No fuel cost mapping for MINH2GIN_W
Note on AK58: ⚠ No fuel cost mapping for MINH2GIN_NE
Note on AK59: ⚠ No fuel cost mapping for MINH2GNP
Note on AK60: ⚠ No fuel cost mapping for MINH2GLK
Note on AK61: ⚠ No fuel cost mapping for MINH2GMV

## Demand_Projection
Demand/Share | Fuel/Tech | Name | Ref.Cap.BY | Ref.OAR.BY | Ref.km.BY | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Improvement_Notes
Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 310.5 | 332.18 | 355.37 | 380.18 | 406.72 | 435.12 | 465.5 | 498 | 526.86 | 557.38 | 589.68 | 623.85 | 660 | 698.29 | 738.8 | 781.67 | 827.02 | 875 | 908.36 | 942.99 | 978.94 | 1016.26 | 1055 | 1094.87 | 1136.25 | 1179.19 | 1223.75 | 1270 | Could be improved: IEPMP 2023 has year-by-year projections under 3 GDP scenarios (7%, 5.8%, 3.8%). Current values use interpolated growth rates. Consider replacing with exact IEPMP year-by-year values. Source: BGD_DA_Final 2_Demand_Forecasts (IEPMP table rows 20-27).
Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 20.5 | 21.54 | 22.64 | 23.79 | 24.99 | 26.26 | 27.6 | 29 | 30.45 | 31.97 | 33.56 | 35.24 | 37 | 38.81 | 40.72 | 42.71 | 44.8 | 47 | 49.35 | 51.82 | 54.42 | 57.14 | 60 | 63.07 | 66.3 | 69.69 | 73.25 | 77 | Could be improved: BPC demand projections have specific year-by-year values. Bhutan_new_data_v2 3_Demand sheet has IRENA demand data through 2023 + BPC forecast. Current growth rate (~5%/yr) is approximate.
Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 1555.2 | 1625.1 | 1698.2 | 1774.6 | 1854.4 | 1953.2 | 2057.4 | 2167.1 | 2282.6 | 2404.4 | 2508.1 | 2616.4 | 2729.3 | 2847.1 | 2970 | 3094.2 | 3223.5 | 3358.3 | 3498.7 | 3645 | 3751.6 | 3861.2 | 3974.1 | 4090.3 | 4209.9 | 4333 | 4459.6 | 4590 | Source: Long_Term_Electricity_Demand_Forecasting_Report.pdf (KPMG/CEA), Table A5.2: Forecasted Electrical Energy Requirement (PAM Baseline Scenario) in MUs. Regional total = sum of state-level forecasts (Delhi+Haryana+HP+J&K+Punjab+Rajasthan+UP+Uttarakhand+Chandigarh). Could be improved: Table A5.2 has values for FY2017-FY2037 — current template may use interpolation beyond 2037.
Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 1324.8 | 1384.4 | 1446.6 | 1511.7 | 1579.6 | 1663.9 | 1752.6 | 1846 | 1944.5 | 2048.2 | 2136.6 | 2228.8 | 2325 | 2425.3 | 2530 | 2635.8 | 2746 | 2860.8 | 2980.4 | 3105 | 3195.8 | 3289.2 | 3385.4 | 3484.3 | 3586.2 | 3691 | 3798.9 | 3910 | Source: Same PDF Table A5.2. Southern Region = AP+Telangana+Karnataka+Kerala+Tamil Nadu+Puducherry. Could be improved: replace interpolated values with exact Table A5.2 year-by-year numbers.
Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 1036.8 | 1083.4 | 1132.1 | 1183 | 1236.2 | 1302.2 | 1371.6 | 1444.7 | 1521.8 | 1602.9 | 1672.1 | 1744.3 | 1819.5 | 1898.1 | 1980 | 2062.8 | 2149 | 2238.9 | 2332.5 | 2430 | 2501 | 2574.2 | 2649.4 | 2726.9 | 2806.6 | 2888.6 | 2973.1 | 3060 | Source: Same PDF Table A5.2. Eastern Region = Bihar+Jharkhand+Odisha+West Bengal+Sikkim. Could be improved: replace interpolated values with exact Table A5.2 year-by-year numbers.
Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 1555.2 | 1625.1 | 1698.2 | 1774.6 | 1854.4 | 1953.2 | 2057.4 | 2167.1 | 2282.6 | 2404.4 | 2508.1 | 2616.4 | 2729.3 | 2847.1 | 2970 | 3094.2 | 3223.5 | 3358.3 | 3498.7 | 3645 | 3751.6 | 3861.2 | 3974.1 | 4090.3 | 4209.9 | 4333 | 4459.6 | 4590 | Source: Same PDF Table A5.2. Western Region = Goa+Gujarat+Chhattisgarh+MP+Maharashtra+DNH+DD. ⚠ NOTE: IN_W and IN_N show identical 2023 values (1555.2 PJ) — verify this is correct from Table A5.2. Could be improved: replace with exact Table A5.2 values.
Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 288 | 301 | 314.5 | 328.6 | 343.4 | 361.7 | 381 | 401.3 | 422.7 | 445.2 | 464.5 | 484.5 | 505.4 | 527.2 | 550 | 573 | 597 | 621.9 | 647.9 | 675 | 694.7 | 715 | 735.9 | 757.5 | 779.6 | 802.4 | 825.9 | 850 | Source: Same PDF Table A5.2. NE Region = Assam+Manipur+Meghalaya+Nagaland+Tripura+Arunachal+Mizoram. Could be improved: replace interpolated values with exact Table A5.2 year-by-year numbers.
Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 40.7 | 42.15 | 43.65 | 45.21 | 46.82 | 48.48 | 50.21 | 52 | 54.37 | 56.85 | 59.45 | 62.16 | 65 | 68.58 | 72.36 | 76.35 | 80.56 | 85 | 89.5 | 94.23 | 99.22 | 104.47 | 110 | 115.44 | 121.14 | 127.13 | 133.41 | 140 | Could be improved: Nepal_new_data Demand Forecasts has CES/LTS study projections under 3 scenarios (High=10.3% GDP, Reference=7%, Low=4.5%). TWh values for 2020-2050 in 5-year increments. WECS/NEA forecast also available (higher growth). Replace interpolation with scenario-specific values.
Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 53.3 | 55.9 | 58.7 | 61.9 | 65.3 | 68.8 | 72.6 | 76.5 | 80.2 | 84 | 88 | 92.2 | 96.6 | 101.5 | 106.6 | 112.1 | 117.7 | 123.6 | 129.8 | 136.1 | 142.5 | 149.1 | 155.6 | 162.2 | 168.9 | 175.4 | 182.1 | 188.9 | Could be improved: SriLanka__new_data_v2 Demand Forecast has CEB LTGEP Table E1 with exact year-by-year demand (GWh), net generation (GWh), T&D loss (%), and peak demand (MW) for 2025-2049. ⚠ Reconcile generation-side vs demand-side definition (see reconciliation note in cell comment). Replace interpolated trajectory with exact LTGEP Table E1 values.
Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 4.62 | 4.95 | 5.3 | 5.67 | 6.07 | 6.5 | 6.86 | 7.24 | 7.65 | 8.07 | 8.52 | 9 | 9.5 | 9.95 | 10.43 | 10.93 | 11.45 | 12 | 12.55 | 13.12 | 13.72 | 14.35 | 15 | 15.64 | 16.31 | 17.01 | 17.74 | 18.5 | Could be improved: Maldives_new_data Demand Forecasts has MCCEE Roadmap segment-level projections (Greater Malé, other inhabited islands, resort islands) through 2033. National 5%/yr vs Greater Malé 7.9%/yr tension noted in Maldives_Timeslice_README.md.
Note on I2: BGD: base=86,255 GWh→310.5 PJ (BPDB 2023-24). Growth: IEPMP 2023 7%→5.8%→3.8%/yr. Sources: BGD_DA_Final, Bangladesh_new_data_v2_REV. CROSS-CHECK: Template=310.5 PJ → 86,250 GWh. Source=86,255 GWh (BPDB 2023-24). Diff=< 0.01%. MATCH
Note on I3: BTN: base=5,744 GWh→20.5 PJ (BPSO 2023). Growth: ~5%/yr (BPC). Sources: BTN_DA_Final, Bhutan_new_data_v2. CROSS-CHECK: Template=20.5 PJ → 5,694 GWh. Source=5,744 GWh (BPSO 2023). Diff=~1%. CLOSE — round to 20.7 PJ
Note on I4: IND_N: CEA 20th EPS by state. Sources: India_new_data_v2, IND_DA_Final.
Note on I5: IND_S: CEA 20th EPS by state. Sources: India_new_data_v2.
Note on I6: IND_E: CEA 20th EPS by state. Sources: India_new_data_v2.
Note on I7: IND_W: CEA 20th EPS by state. Sources: India_new_data_v2.
Note on I8: IND_NE: CEA 20th EPS by state. Sources: India_new_data_v2.
Note on I9: NPL: base=11,548 GWh→40.7 PJ (NEA FY2079/80). Growth: ~8.4%/yr. Sources: NP_DA_Final, Nepal_new_data. CROSS-CHECK: Template=40.7 PJ → 11,306 GWh. Source=11,548 GWh (NEA FY2079/80). Diff=~2%. CLOSE — round to 41.6 PJ
Note on I10: LKA: base=15,274 GWh→53.3 PJ (PUCSL 2023). Growth: CEB LTGEP. Sources: LKA_DA_Final, SriLanka__new_data_v2. CROSS-CHECK: Template=53.3 PJ → 14,806 GWh. Source=15,274 GWh (PUCSL 2023). Diff=~3%. ⚠ REVIEW: 468 GWh gap. T&D losses? RECONCILIATION: PUCSL 2023 total generation: 15,274 GWh = 55.0 PJ CEB LTGEP T&D losses: ~7.9% (2023-2025) Implied demand: 15,274 × 0.921 = 14,067 GWh = 50.6 PJ Template value: 53.3 PJ = 14,806 GWh → Template appears to use a ~3% loss (generation-side minus small adjustment). ⚠ DECISION: Use 55.0 PJ (generation-side, consistent with PUCSL) or 50.6 PJ (demand-side)? Source: LKA_DA_Final; SriLanka__new_data_v2 Demand Forecast (CEB LTGEP Table E1).
Note on I11: MDV: base=~1,300 GWh→4.62 PJ (STELCO+FENAKA). Growth: 5-7.9%/yr (MCCEE). Sources: Maldives_new_data, Maldives_Timeslice_README. CROSS-CHECK: Template=4.62 PJ → 1,283 GWh. Source=~1,300 GWh (IRENA 2023). Diff=~1%. CLOSE

## Demand_Profiles
Timeslices | Demand/Share | Fuel/Tech | Name | Ref.Cap.BY | Ref.OAR.BY | Ref.km.BY | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
S1D1 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691 | 0.039691
S1D2 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911 | 0.09911
S1D3 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581 | 0.051581
S2D1 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407 | 0.06407
S2D2 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106 | 0.13106
S2D3 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101 | 0.073101
S3D1 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481 | 0.09481
S3D2 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232 | 0.18232
S3D3 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388 | 0.10388
S4D1 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289 | 0.037289
S4D2 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386 | 0.079386
S4D3 | Demand | ELCBDXX02 | Output demand of transmission lines in Bangladesh | not needed | not needed | not needed | User defined | 0 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437 | 0.0437
S1D1 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974 | 0.034974
S1D2 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287 | 0.12287
S1D3 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996 | 0.072996
S2D1 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086 | 0.043086
S2D2 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688 | 0.11688
S2D3 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711 | 0.065711
S3D1 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967 | 0.074967
S3D2 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545 | 0.17545
S3D3 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739 | 0.094739
S4D1 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526 | 0.03526
S4D2 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366 | 0.10366
S4D3 | Demand | ELCBTXX02 | Output demand of transmission lines in Bhutan | not needed | not needed | not needed | User defined | 0 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406 | 0.059406
S1D1 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999 | 0.03999
S1D2 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685 | 0.11685
S1D3 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356 | 0.05356
S2D1 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519 | 0.0519
S2D2 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239 | 0.12239
S2D3 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888 | 0.05888
S3D1 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746 | 0.09746
S3D2 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004 | 0.20004
S3D3 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334 | 0.10334
S4D1 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431 | 0.03431
S4D2 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165 | 0.08165
S4D3 | Demand | ELCIN_NXX02 | Output demand of transmission lines in India – North | not needed | not needed | not needed | User defined | 0 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962 | 0.03962
S1D1 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288 | 0.05288
S1D2 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709 | 0.13709
S1D3 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586 | 0.05586
S2D1 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484 | 0.06484
S2D2 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064 | 0.15064
S2D3 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608 | 0.06608
S3D1 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159 | 0.07159
S3D2 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989 | 0.16989
S3D3 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843 | 0.07843
S4D1 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319 | 0.03319
S4D2 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214 | 0.08214
S4D3 | Demand | ELCIN_SXX02 | Output demand of transmission lines in India – South | not needed | not needed | not needed | User defined | 0 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738 | 0.03738
S1D1 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448 | 0.04448
S1D2 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493 | 0.10493
S1D3 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355 | 0.05355
S2D1 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608 | 0.0608
S2D2 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377 | 0.12377
S2D3 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643 | 0.06643
S3D1 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683 | 0.09683
S3D2 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517 | 0.18517
S3D3 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176 | 0.10176
S4D1 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389 | 0.0389
S4D2 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987 | 0.07987
S4D3 | Demand | ELCIN_EXX02 | Output demand of transmission lines in India – East | not needed | not needed | not needed | User defined | 0 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351 | 0.04351
S1D1 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402 | 0.05402
S1D2 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672 | 0.13672
S1D3 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999 | 0.05999
S2D1 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323 | 0.06323
S2D2 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801 | 0.13801
S2D3 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569 | 0.06569
S3D1 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555 | 0.07555
S3D2 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107 | 0.16107
S3D3 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052 | 0.08052
S4D1 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732 | 0.03732
S4D2 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706 | 0.08706
S4D3 | Demand | ELCIN_WXX02 | Output demand of transmission lines in India – West | not needed | not needed | not needed | User defined | 0 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082 | 0.04082
S1D1 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086 | 0.04086
S1D2 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095 | 0.1095
S1D3 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025 | 0.06025
S2D1 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992 | 0.04992
S2D2 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163 | 0.1163
S2D3 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658 | 0.06658
S3D1 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416 | 0.09416
S3D2 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696 | 0.18696
S3D3 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595 | 0.11595
S4D1 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292 | 0.03292
S4D2 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078 | 0.08078
S4D3 | Demand | ELCIN_NEXX02 | Output demand of transmission lines in India – Northeast | not needed | not needed | not needed | User defined | 0 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581 | 0.04581
S1D1 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918 | 0.045918
S1D2 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214 | 0.1214
S1D3 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488 | 0.057488
S2D1 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068 | 0.059068
S2D2 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | 0.1335
S2D3 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326 | 0.070326
S3D1 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379 | 0.09379
S3D2 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753 | 0.18753
S3D3 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213 | 0.096213
S4D1 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377 | 0.032377
S4D2 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598 | 0.068598
S4D3 | Demand | ELCNPXX02 | Output demand of transmission lines in Nepal | not needed | not needed | not needed | User defined | 0 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789 | 0.033789
S1D1 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317 | 0.048317
S1D2 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308 | 0.12308
S1D3 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397 | 0.062397
S2D1 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457 | 0.052457
S2D2 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898 | 0.12898
S2D3 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015 | 0.070015
S3D1 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649 | 0.073649
S3D2 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064 | 0.18064
S3D3 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028 | 0.098028
S4D1 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725 | 0.032725
S4D2 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501 | 0.08501
S4D3 | Demand | ELCLKXX02 | Output demand of transmission lines in Sri Lanka | not needed | not needed | not needed | User defined | 0 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706 | 0.044706
S1D1 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256 | 0.051256
S1D2 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183 | 0.11183
S1D3 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895 | 0.069895
S2D1 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715 | 0.058715
S2D2 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281 | 0.1281
S2D3 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066 | 0.080066
S3D1 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387 | 0.07387
S3D2 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117 | 0.16117
S3D3 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073 | 0.10073
S4D1 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159 | 0.036159
S4D2 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892 | 0.078892
S4D3 | Demand | ELCMVXX02 | Output demand of transmission lines in Maldives | not needed | not needed | not needed | User defined | 0 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307 | 0.049307
Note on J2: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J3: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J4: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J5: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J6: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J7: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J8: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J9: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J10: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J11: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J12: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J13: Source: BGD_DA_Final, 2024 PGCB hourly data. Cross-validated 2023 & 2025.
Note on J14: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024).
Note on J15: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024).
Note on J16: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024).
Note on J17: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024). ⚠ ASSUMPTION: Daypart splits for S2 (pre-monsoon) and S4 (post-monsoon) are interpolated 60/40 summer/winter from verified Dec and Jun hourly profiles (BPC Table 5.20). Not from measured hourly data for these seasons. Source: BTN_DA_Final 1_OSTRAM_Profiles — see Daypart Source column.
Note on J18: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024). ⚠ ASSUMPTION: Daypart splits for S2 (pre-monsoon) and S4 (post-monsoon) are interpolated 60/40 summer/winter from verified Dec and Jun hourly profiles (BPC Table 5.20). Not from measured hourly data for these seasons. Source: BTN_DA_Final 1_OSTRAM_Profiles — see Daypart Source column.
Note on J19: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024). ⚠ ASSUMPTION: Daypart splits for S2 (pre-monsoon) and S4 (post-monsoon) are interpolated 60/40 summer/winter from verified Dec and Jun hourly profiles (BPC Table 5.20). Not from measured hourly data for these seasons. Source: BTN_DA_Final 1_OSTRAM_Profiles — see Daypart Source column.
Note on J20: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024).
Note on J21: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024).
Note on J22: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024).
Note on J23: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024). ⚠ ASSUMPTION: Daypart splits for S2 (pre-monsoon) and S4 (post-monsoon) are interpolated 60/40 summer/winter from verified Dec and Jun hourly profiles (BPC Table 5.20). Not from measured hourly data for these seasons. Source: BTN_DA_Final 1_OSTRAM_Profiles — see Daypart Source column.
Note on J24: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024). ⚠ ASSUMPTION: Daypart splits for S2 (pre-monsoon) and S4 (post-monsoon) are interpolated 60/40 summer/winter from verified Dec and Jun hourly profiles (BPC Table 5.20). Not from measured hourly data for these seasons. Source: BTN_DA_Final 1_OSTRAM_Profiles — see Daypart Source column.
Note on J25: Source: BTN_DA_Final, BPSO 2023 actual + BPC Table 5.20 hourly (Dec/Jun 2024). ⚠ ASSUMPTION: Daypart splits for S2 (pre-monsoon) and S4 (post-monsoon) are interpolated 60/40 summer/winter from verified Dec and Jun hourly profiles (BPC Table 5.20). Not from measured hourly data for these seasons. Source: BTN_DA_Final 1_OSTRAM_Profiles — see Daypart Source column.
Note on J26: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J27: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J28: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J29: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J30: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J31: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J32: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J33: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J34: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J35: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J36: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J37: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_North.
Note on J38: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J39: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J40: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J41: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J42: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J43: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J44: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J45: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J46: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J47: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J48: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J49: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_South.
Note on J50: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J51: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J52: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J53: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J54: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J55: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J56: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J57: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J58: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J59: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J60: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J61: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_East.
Note on J62: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J63: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J64: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J65: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J66: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J67: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J68: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J69: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J70: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J71: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J72: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J73: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_West.
Note on J74: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J75: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J76: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J77: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J78: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J79: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J80: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J81: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J82: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J83: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J84: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J85: Source: IND_DA_Final, Grid-India hourly demand 2023-2024. Region: India_Northeast.
Note on J86: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J87: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J88: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J89: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J90: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J91: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J92: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J93: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J94: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J95: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J96: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J97: Source: NP_DA_Final, NEA FY2079/80 monthly + NREL Table 1 hourly shape.
Note on J98: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J99: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J100: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J101: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J102: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J103: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J104: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J105: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J106: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J107: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J108: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on J109: Source: LKA_DA_Final, PUCSL 15-min dispatch 2023 (363 daily sheets).
Note on I110: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J110: Maldives demand fraction=0.051256 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I111: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J111: Maldives demand fraction=0.111832 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I112: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J112: Maldives demand fraction=0.069895 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I113: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J113: Maldives demand fraction=0.058715 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I114: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J114: Maldives demand fraction=0.128105 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I115: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J115: Maldives demand fraction=0.080066 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I116: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J116: Maldives demand fraction=0.073870 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I117: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J117: Maldives demand fraction=0.161171 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I118: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J118: Maldives demand fraction=0.100732 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I119: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J119: Maldives demand fraction=0.036159 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I120: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J120: Maldives demand fraction=0.078892 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.
Note on I121: ⚠ Maldives demand fractions pending. Yearbook monthly production data available (STELCO Table 12.2, ~60 localities). Daypart splits must be estimated (no hourly data; STELCO dashboard covers only Malé). See Maldives_Timeslice_README.md for full assessment. Recommended: build from monthly production + tropical island diurnal profile from literature.
Note on J121: Maldives demand fraction=0.049307 Seasonal: STELCO Yearbook Table 12.2 (monthly production, ~60 localities, 2024) Daypart: Estimated — tropical island profile (D1=22%, D2=48%, D3=30%) Source: Maldives_new_data.xlsx Seasonality sheet ⚠ Daypart splits are ESTIMATED, not from measured hourly data. See Maldives_Timeslice_README.md. ⚠ ASSUMPTION: All daypart splits (D1=22%, D2=48%, D3=30%) are estimated from a generic tropical island diurnal profile. No measured hourly demand data available for Maldives. Seasonal fractions are from STELCO metered monthly production (Table 12.2). See Maldives_Timeslice_README.md for full assessment and justification.

## Demand_Techs
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
1 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
1 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
1 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
1 | PWRTRNBDXX | Existing internal transmission (non-RE), Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
2 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 1 | CapitalCost | USD/kW | User defined | 0
2 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
2 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 3 | ResidualCapacity | GW | User defined | 0
2 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
2 | PWRTRNBTXX | Existing internal transmission (non-RE), Bhutan, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
3 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 1 | CapitalCost | USD/kW | User defined | 0
3 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
3 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 3 | ResidualCapacity | GW | User defined | 0
3 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
3 | PWRTRNIN_NXX | Existing internal transmission (non-RE), India – North, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
4 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 1 | CapitalCost | USD/kW | User defined | 0
4 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
4 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 3 | ResidualCapacity | GW | User defined | 0
4 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
4 | PWRTRNIN_SXX | Existing internal transmission (non-RE), India – South, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
5 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
5 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
5 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
5 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
5 | PWRTRNIN_EXX | Existing internal transmission (non-RE), India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
6 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 1 | CapitalCost | USD/kW | User defined | 0
6 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
6 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 3 | ResidualCapacity | GW | User defined | 0
6 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
6 | PWRTRNIN_WXX | Existing internal transmission (non-RE), India – West, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
7 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 1 | CapitalCost | USD/kW | User defined | 0
7 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
7 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 3 | ResidualCapacity | GW | User defined | 0
7 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
7 | PWRTRNIN_NEXX | Existing internal transmission (non-RE), India – Northeast, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
8 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 1 | CapitalCost | USD/kW | User defined | 0
8 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
8 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 3 | ResidualCapacity | GW | User defined | 0
8 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
8 | PWRTRNNPXX | Existing internal transmission (non-RE), Nepal, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
9 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 1 | CapitalCost | USD/kW | User defined | 0
9 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
9 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 3 | ResidualCapacity | GW | User defined | 0
9 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
9 | PWRTRNLKXX | Existing internal transmission (non-RE), Sri Lanka, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
10 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 1 | CapitalCost | USD/kW | User defined | 0
10 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
10 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 3 | ResidualCapacity | GW | User defined | 0
10 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
10 | PWRTRNMVXX | Existing internal transmission (non-RE), Maldives, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
11 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
11 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
11 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
11 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
11 | RNWTRNBDXX | Existing internal transmission (RE), Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
12 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 1 | CapitalCost | USD/kW | User defined | 0
12 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
12 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 3 | ResidualCapacity | GW | User defined | 0
12 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
12 | RNWTRNBTXX | Existing internal transmission (RE), Bhutan, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
13 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 1 | CapitalCost | USD/kW | User defined | 0
13 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
13 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 3 | ResidualCapacity | GW | User defined | 0
13 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
13 | RNWTRNIN_NXX | Existing internal transmission (RE), India – North, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
14 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 1 | CapitalCost | USD/kW | User defined | 0
14 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
14 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 3 | ResidualCapacity | GW | User defined | 0
14 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
14 | RNWTRNIN_SXX | Existing internal transmission (RE), India – South, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
15 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
15 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
15 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
15 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
15 | RNWTRNIN_EXX | Existing internal transmission (RE), India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
16 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 1 | CapitalCost | USD/kW | User defined | 0
16 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
16 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 3 | ResidualCapacity | GW | User defined | 0
16 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
16 | RNWTRNIN_WXX | Existing internal transmission (RE), India – West, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
17 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 1 | CapitalCost | USD/kW | User defined | 0
17 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
17 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 3 | ResidualCapacity | GW | User defined | 0
17 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
17 | RNWTRNIN_NEXX | Existing internal transmission (RE), India – Northeast, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
18 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 1 | CapitalCost | USD/kW | User defined | 0
18 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
18 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 3 | ResidualCapacity | GW | User defined | 0
18 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
18 | RNWTRNNPXX | Existing internal transmission (RE), Nepal, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
19 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 1 | CapitalCost | USD/kW | User defined | 0
19 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
19 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 3 | ResidualCapacity | GW | User defined | 0
19 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
19 | RNWTRNLKXX | Existing internal transmission (RE), Sri Lanka, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
20 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 1 | CapitalCost | USD/kW | User defined | 0
20 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
20 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 3 | ResidualCapacity | GW | User defined | 0
20 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
20 | RNWTRNMVXX | Existing internal transmission (RE), Maldives, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
21 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
21 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
21 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
21 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
21 | TRNNLIBDXX | New internal transmission line, Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
22 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 1 | CapitalCost | USD/kW | User defined | 0
22 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
22 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 3 | ResidualCapacity | GW | User defined | 0
22 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
22 | TRNNLIBTXX | New internal transmission line, Bhutan, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
23 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 1 | CapitalCost | USD/kW | User defined | 0
23 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
23 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 3 | ResidualCapacity | GW | User defined | 0
23 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
23 | TRNNLIIN_NXX | New internal transmission line, India – North, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
24 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 1 | CapitalCost | USD/kW | User defined | 0
24 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
24 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 3 | ResidualCapacity | GW | User defined | 0
24 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
24 | TRNNLIIN_SXX | New internal transmission line, India – South, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
25 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
25 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
25 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
25 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
25 | TRNNLIIN_EXX | New internal transmission line, India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
26 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 1 | CapitalCost | USD/kW | User defined | 0
26 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
26 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 3 | ResidualCapacity | GW | User defined | 0
26 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
26 | TRNNLIIN_WXX | New internal transmission line, India – West, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
27 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 1 | CapitalCost | USD/kW | User defined | 0
27 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
27 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 3 | ResidualCapacity | GW | User defined | 0
27 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
27 | TRNNLIIN_NEXX | New internal transmission line, India – Northeast, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
28 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 1 | CapitalCost | USD/kW | User defined | 0
28 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
28 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 3 | ResidualCapacity | GW | User defined | 0
28 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
28 | TRNNLINPXX | New internal transmission line, Nepal, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
29 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 1 | CapitalCost | USD/kW | User defined | 0
29 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
29 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 3 | ResidualCapacity | GW | User defined | 0
29 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
29 | TRNNLILKXX | New internal transmission line, Sri Lanka, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
30 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 1 | CapitalCost | USD/kW | User defined | 0
30 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
30 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 3 | ResidualCapacity | GW | User defined | 0
30 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
30 | TRNNLIMVXX | New internal transmission line, Maldives, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
31 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 1 | CapitalCost | USD/kW | User defined | 0
31 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
31 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 3 | ResidualCapacity | GW | User defined | 0
31 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
31 | TRNRPOBDXX | Repower/upgrade internal transmission, Bangladesh, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
32 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 1 | CapitalCost | USD/kW | User defined | 0
32 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
32 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 3 | ResidualCapacity | GW | User defined | 0
32 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
32 | TRNRPOBTXX | Repower/upgrade internal transmission, Bhutan, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
33 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 1 | CapitalCost | USD/kW | User defined | 0
33 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
33 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 3 | ResidualCapacity | GW | User defined | 0
33 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
33 | TRNRPOIN_NXX | Repower/upgrade internal transmission, India – North, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
34 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 1 | CapitalCost | USD/kW | User defined | 0
34 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
34 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 3 | ResidualCapacity | GW | User defined | 0
34 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
34 | TRNRPOIN_SXX | Repower/upgrade internal transmission, India – South, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
35 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 1 | CapitalCost | USD/kW | User defined | 0
35 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
35 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 3 | ResidualCapacity | GW | User defined | 0
35 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
35 | TRNRPOIN_EXX | Repower/upgrade internal transmission, India – East, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
36 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 1 | CapitalCost | USD/kW | User defined | 0
36 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
36 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 3 | ResidualCapacity | GW | User defined | 0
36 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
36 | TRNRPOIN_WXX | Repower/upgrade internal transmission, India – West, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
37 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 1 | CapitalCost | USD/kW | User defined | 0
37 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
37 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 3 | ResidualCapacity | GW | User defined | 0
37 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
37 | TRNRPOIN_NEXX | Repower/upgrade internal transmission, India – Northeast, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
38 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 1 | CapitalCost | USD/kW | User defined | 0
38 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
38 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 3 | ResidualCapacity | GW | User defined | 0
38 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
38 | TRNRPONPXX | Repower/upgrade internal transmission, Nepal, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
39 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 1 | CapitalCost | USD/kW | User defined | 0
39 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
39 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 3 | ResidualCapacity | GW | User defined | 0
39 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
39 | TRNRPOLKXX | Repower/upgrade internal transmission, Sri Lanka, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0
40 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 1 | CapitalCost | USD/kW | User defined | 0
40 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 2 | FixedCost | USD/kW/yr | User defined | 0
40 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 3 | ResidualCapacity | GW | User defined | 0
40 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 4 | TotalAnnualMaxCapacity | GW | User defined | 0
40 | TRNRPOMVXX | Repower/upgrade internal transmission, Maldives, region XX | 5 | TotalTechnologyAnnualActivityUpperLimit | PJ | User defined | 0

## Yearsplit_Template
Timeslices | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
S1D1 | 14 | YearSplit | fraction | User defined | 0 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556
S1D2 | 14 | YearSplit | fraction | User defined | 0 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389
S1D3 | 14 | YearSplit | fraction | User defined | 0 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722
S2D1 | 14 | YearSplit | fraction | User defined | 0 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111
S2D2 | 14 | YearSplit | fraction | User defined | 0 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278
S2D3 | 14 | YearSplit | fraction | User defined | 0 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444
S3D1 | 14 | YearSplit | fraction | User defined | 0 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556
S3D2 | 14 | YearSplit | fraction | User defined | 0 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389 | 0.076389
S3D3 | 14 | YearSplit | fraction | User defined | 0 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722 | 0.034722
S4D1 | 14 | YearSplit | fraction | User defined | 0 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111 | 0.11111
S4D2 | 14 | YearSplit | fraction | User defined | 0 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278 | 0.15278
S4D3 | 14 | YearSplit | fraction | User defined | 0 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444 | 0.069444
NOTE: This uses the original template hour assignments. See Yearsplit_ReNinja for Renewables.ninja-derived assignments.
Note on G2: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G3: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G4: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G5: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G6: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G7: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G8: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G9: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G10: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G11: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G12: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.
Note on G13: Template original. See Yearsplit_ReNinja sheet for Renewables.ninja alternative.

## DaySplit
DAILYTIMEBRACKET | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | 12 | DaySplit | fraction | User defined | 0 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913 | 0.000913
2 | 12 | DaySplit | fraction | User defined | 0 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256 | 0.001256
3 | 12 | DaySplit | fraction | User defined | 0 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571 | 0.000571

## Interconnectors
NO | Project | From_Node | To_Node | Circuits | COD_Date | Affiliated_Power | Capacity_MW | Voltage_kV | DC_AC | Directionality | Status | Export_Resource_Type | Source
1 | Chukha → Birpara 220 kV D/C | BT | IN_E | 2 | Existing | Chukha Hydro | 332 | 220 kV | AC | Uni‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
2 | Chukha → Birpara via Singhigaon 220 kV S/C | BT | IN_E | 1 | Existing | Chukha Hydro |  | 220 kV | AC | Uni‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
3 | Kurichhu → Gelephu → Salakati 132 kV S/C | BT | IN_NE | 1 | Existing | Kurichhu | 60 | 132 kV | AC | Uni‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
4 | Tala → Siliguri 400 kV 2×D/C | BT | IN_E | 2 | Existing | Tala | 1020 | 400 kV | AC | Uni‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
5 | Jigmeling → Alipurduar 400 kV D/C (Quad) | BT | IN_E | 1 | Existing | Punatsangchhu‑I &2,Mangdechhu | 3000 | 400 kV | AC | Bi‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
6 | Bheramara back‑to‑back HVDC (India → Bangladesh) | IN_E | BD |  | Oct 2013 | Grid-to-Grid | 1000 | ±400 kV | DC | Bi‑directional | Operational | Fossil / mixed | Zixuan v3 (Sheet 1)
7 | Surajmaninagar- Comilla | IN_NE | BD |  | nan | Grid-to-Grid | 160 | Operate at 132 (designed with 400kV) | nan | nan | nan | nan | Zixuan v3 (Sheet 1)
8 | Bornagar-Parbotipur | IN_NE | BD |  | planned | Grid-to-Grid | TBD | 765kV | Should be DC | Bi‑directional | nan | nan | Zixuan v3 (Sheet 1)
9 | Muzaffarpur → Dhalkebar 400 kV D/C | IN_E | NP | 2 | 2016 (upgrade) | nan | 1100 | 400 kV | AC | Bi‑directional | Operational | Hydro | Zixuan v3 (Sheet 1)
10 | Raxaul (India) – Parwanipur (Nepal) | IN_N | NP | 2 | nan | nan | 150 | 132kV | nan | Bi‑directional | nan | nan | Zixuan v3 (Sheet 1)
11 | Kataiya (India) – Kusaha (Nepal) | IN_E | NP | 2 | nan | nan | 150 | 132kV | nan | Bi‑directional | nan | nan | Zixuan v3 (Sheet 1)
12 | Kushinagar (India) – Bhairahawa (Nepal) | IN_N | NP | 1 | nan | nan | 100 | 132kV | nan | Bi‑directional | nan | nan | Zixuan v3 (Sheet 1)
13 | Tanakpur (India) – Mahendranagar (Nepal) | IN_N | NP | 1 | nan | nan | 80 | 132kV | nan | Bi‑directional | nan | nan | Zixuan v3 (Sheet 1)
14 | Jogbani (India) – Biratnagar (Nepal) | IN_E | NP | 1 | nan | nan | 50 | 132kV | nan | Bi‑directional | nan | nan | Zixuan v3 (Sheet 1)
15 | Mainahiya (India) – Sampatiya (Nepal) | IN_N | NP | 1 | nan | nan | 50 | 132kV | nan | Bi‑directional | nan | nan | Zixuan v3 (Sheet 1)
16 | New Butwal (Nepal) – Gorakhpur (India) | NP | IN_N | 2 | 2025/26 (target) | nan | 2500?(Estimated) | 400 kV | AC | Bi‑directional | Under Construction | Hydro | Zixuan v3 (Sheet 1)
17 | Inaruwa (Duhabi) → Purnia 400 kV | NP | IN_E |  | 2027/28 (target) | nan | 2500?(Estimated) | 400 kV | AC | Bi‑directional | Planned | Hydro | Zixuan v3 (Sheet 1)
18 | Dodhara (Lamki) → Bareli 400 kV | NP | IN_N |  | 2028/29 (target) | nan | 2500?(Estimated) | 400 kV | AC | Bi‑directional | Planned | Hydro | Zixuan v3 (Sheet 1)
19 | India → Sri Lanka HVDC interconnector (Madurai ↔ Mannar / Anuradhapura) | IN_S | LK |  | 2030 (proposed) | nan | 500（Tentatively) | ±500 kV | DC | Bi‑directional | Proposed / Planning | Mixed (hydro / renewables / fossil) | Zixuan v3 (Sheet 1)
20 | Anarmani (Nepal) – Kishanganj (India) | NP | IN_E |  |  |  |  | 400 |  |  | Proposed |  | https://kathmandupost.com/national/2024/01/08/nepal-and-india-to-explore-potential-of-more-high-capacity-electricity-transmission-lines?utm_source=chatgpt.com
21 | Lamahi (Dang)-Lucknow (Uttar Pradesh) | NP | IN_N |  |  |  |  | 400 |  |  | Proposed |  | nan
22 | Nijgadh (Bara)-Motihari (Bihar) | NP | IN_E |  |  |  |  | 400 |  |  | Proposed |  | nan
23 | Katihar- Parbatipur | IN_E | BD |  |  |  |  | 765 |  |  | Proposed |  | https://cpd-power-energy-study.com/bangladesh-india-review-progress-of-katihar-parbatipur-baranagar-765kv-transmission-line/?utm_source=chatgpt.com
24 | Parbatipur-Boronagar | BD | IN_E |  |  |  |  | 765 |  |  | Proposed |  | nan
25 | Adani Company explore 5GW to India | BT | IN_E |  |  |  |  | not specified |  |  | Proposed |  | nan
CROSS-VALIDATION AGAINST INFRASTRUCTURE FILES
Total interconnection entries in Infrastructure files: 85
Bheramara HVDC Back-to-Back | 500 | Existing Interconnections | Bangladesh_Power_Sector.xlsx
Comilla-Tripura Interconnection | 160 | Existing Interconnections | Bangladesh_Power_Sector.xlsx
Adani Power Jharkhanda (Godda) Import | 1496 | Existing Interconnections | Bangladesh_Power_Sector.xlsx
Nepal Hydro Import (Trial) | 40 | Existing Interconnections | Bangladesh_Power_Sector.xlsx
TOTAL IMPORT CAPACITY | 2196 | Existing Interconnections | Bangladesh_Power_Sector.xlsx
Barapukuria HVDC B2B Station | 400 kV | Planned Interconnections | Bangladesh_Power_Sector.xlsx
Cumilla HVDC B2B Station | 400 kV | Planned Interconnections | Bangladesh_Power_Sector.xlsx
Jamalpur HVDC B2B Station | 400 kV | Planned Interconnections | Bangladesh_Power_Sector.xlsx
Sylhet HVDC B2B Station | 400 kV | Planned Interconnections | Bangladesh_Power_Sector.xlsx
Nepal Hydro Import - Dedicated Line | 400 kV / 765 kV | Planned Interconnections | Bangladesh_Power_Sector.xlsx
Bhutan Hydro Import - Dedicated Line | 400 kV | Planned Interconnections | Bangladesh_Power_Sector.xlsx
Second Bheramara HVDC Expansion | 400 kV | Planned Interconnections | Bangladesh_Power_Sector.xlsx
Myanmar Cross-Border Link | TBD | Planned Interconnections | Bangladesh_Power_Sector.xlsx
400kV Tala–Siliguri Line 1&2 | ~1,020 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
400kV Tala–Malbase–Siliguri Line 3&4 | ~1,020 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
400kV Puna-I–Alipurduar Line 1&2 | ~1,200 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
400kV Puna-I–Puna-II Line 1&2 | Internal | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
400kV Puna-II–Alipurduar Line 1&2 | ~1,200 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
400kV Puna-II–Jigmeling Line 1&2 | Internal | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
400kV Mangdechhu–Jigmeling Line 1-4 | Internal | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
400kV Jigmeling–Alipurduar Line 1&2 | ~720 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
220kV Chhukha–Birpara (India Border) | ~336 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
220kV Chhukha–Malbase–Siliguri | ~336 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
220kV Malbase–India Border (Birpara) | ~100 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx
220kV Samtse–Singhigaon (India Border) | ~100 | Existing Interconnections | Bhutan_Power_Infrastructure.xlsx

## Interconnector_Params
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 1 | CapitalCost | USD/kW | User defined | 0 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
1 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 2 | FixedCost | USD/kW/yr | User defined | 0 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
1 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
1 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
1 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
1 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
1 | TRNCBD_BD_IN_E | Cross-border interconnector: Bangladesh ↔ India East | 2 | OperationalLife | years | User defined | 0 | bar: 2023
2 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 1 | CapitalCost | USD/kW | User defined | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
2 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
2 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
2 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
2 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
2 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
2 | TRNCBD_BD_IN_NE | Cross-border interconnector: Bangladesh ↔ India Northeast | 2 | OperationalLife | years | User defined | 0 | bar: 2023
3 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 1 | CapitalCost | USD/kW | User defined | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
3 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 2 | FixedCost | USD/kW/yr | User defined | 0 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
3 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
3 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
3 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
3 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
3 | TRNCBD_BT_IN_E | Cross-border interconnector: Bhutan ↔ India East | 2 | OperationalLife | years | User defined | 0 | bar: 2023
4 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 1 | CapitalCost | USD/kW | User defined | 0 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
4 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 2 | FixedCost | USD/kW/yr | User defined | 0 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
4 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
4 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
4 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
4 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
4 | TRNCBD_BT_IN_NE | Cross-border interconnector: Bhutan ↔ India Northeast | 2 | OperationalLife | years | User defined | 0 | bar: 2023
5 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 1 | CapitalCost | USD/kW | User defined | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
5 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 2 | FixedCost | USD/kW/yr | User defined | 0 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
5 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
5 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
5 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
5 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
5 | TRNCBD_NP_IN_N | Cross-border interconnector: Nepal ↔ India North | 2 | OperationalLife | years | User defined | 0 | bar: 2023
6 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 1 | CapitalCost | USD/kW | User defined | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
6 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 2 | FixedCost | USD/kW/yr | User defined | 0 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
6 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
6 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
6 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
6 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
6 | TRNCBD_NP_IN_E | Cross-border interconnector: Nepal ↔ India East | 2 | OperationalLife | years | User defined | 0 | bar: 2023
7 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 1 | CapitalCost | USD/kW | User defined | 0 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031 | 1031
7 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 2 | FixedCost | USD/kW/yr | User defined | 0 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
7 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
7 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
7 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
7 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
7 | TRNCBD_LK_IN_S | Cross-border interconnector: Sri Lanka ↔ India South | 2 | OperationalLife | years | User defined | 0 | bar: 2023
8 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
8 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
8 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
8 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
8 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
8 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
8 | TRNCBD_IN_N_IN_E | Cross-border interconnector: India North ↔ India East (internal) | 2 | OperationalLife | years | User defined | 0 | bar: 2023
9 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
9 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
9 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
9 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
9 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
9 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
9 | TRNCBD_IN_N_IN_W | Cross-border interconnector: India North ↔ India West (internal) | 2 | OperationalLife | years | User defined | 0 | bar: 2023
10 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
10 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
10 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
10 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
10 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
10 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
10 | TRNCBD_IN_E_IN_NE | Cross-border interconnector: India East ↔ India Northeast (internal) | 2 | OperationalLife | years | User defined | 0 | bar: 2023
11 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550
11 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
11 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
11 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
11 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
11 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
11 | TRNCBD_IN_E_IN_S | Cross-border interconnector: India East ↔ India South (internal) | 2 | OperationalLife | years | User defined | 0 | bar: 2023
12 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 1 | CapitalCost | USD/kW | User defined | 0 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
12 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
12 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
12 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
12 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
12 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
12 | TRNCBD_IN_W_IN_S | Cross-border interconnector: India West ↔ India South (internal) | 2 | OperationalLife | years | User defined | 0 | bar: 2023
13 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 1 | CapitalCost | USD/kW | User defined | 0 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600
13 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 2 | FixedCost | USD/kW/yr | User defined | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
13 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 3 | ResidualCapacity | GW | User defined | 0 | bar: 2023
13 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 4 | TotalAnnualMaxCapacity | GW | User defined | 0 | bar: 2023
13 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 13 | CapacityFactor | fraction | User defined | 0 | bar: 2023
13 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 14 | TransmissionLossFactor | fraction | User defined | 0 | bar: 2023
13 | TRNCBD_MV_IN_S | Cross-border interconnector: Maldives ↔ India South (submarine cable) | 2 | OperationalLife | years | User defined | 0 | bar: 2023
Note on I2: Source: ADB Bheramara B2B ~$193m/500MW + expansion Corridor: BD↔IN_E Type: ±400kV HVDC B2B + 765kV AC Confidence: High
Note on I3: Source: ADB Bheramara B2B ~$193m/500MW + expansion Corridor: BD↔IN_E Type: ±400kV HVDC B2B + 765kV AC Confidence: High
Note on I9: Source: Tripura-Comilla ~$26m/100MW (public reporting) Corridor: BD↔IN_NE Type: 132/400 kV AC Confidence: Medium
Note on I10: Source: Tripura-Comilla ~$26m/100MW (public reporting) Corridor: BD↔IN_NE Type: 132/400 kV AC Confidence: Medium
Note on I16: Source: Indian 220/400 kV overhead unit costs Corridor: BT↔IN_E Type: 220/400 kV AC Confidence: Medium
Note on I17: Source: Indian 220/400 kV overhead unit costs Corridor: BT↔IN_E Type: 220/400 kV AC Confidence: Medium
Note on I23: Source: Indian 132 kV cost matrix Corridor: BT↔IN_NE Type: 132 kV AC Confidence: Low
Note on I24: Source: Indian 132 kV cost matrix Corridor: BT↔IN_NE Type: 132 kV AC Confidence: Low
Note on I30: Source: WB Nepal-India ETTP line components Corridor: NP↔IN_N Type: 132/400 kV AC Confidence: Medium
Note on I31: Source: WB Nepal-India ETTP line components Corridor: NP↔IN_N Type: 132/400 kV AC Confidence: Medium
Note on I37: Source: Muzaffarpur-Dhalkebar / Inaruwa-Purnia Corridor: NP↔IN_E Type: 400 kV AC Confidence: Medium
Note on I38: Source: Muzaffarpur-Dhalkebar / Inaruwa-Purnia Corridor: NP↔IN_E Type: 400 kV AC Confidence: Medium
Note on I44: Source: USAID/USTDA feasibility ~$1,031m/1000MW (2012$) Corridor: LK↔IN_S Type: ±500kV HVDC submarine Confidence: Medium
Note on I45: Source: USAID/USTDA feasibility ~$1,031m/1000MW (2012$) Corridor: LK↔IN_S Type: ±500kV HVDC submarine Confidence: Medium
Note on I51: Source: POWERGRID; Indian 400/765 kV unit-cost matrix Corridor: IN_N↔IN_E Type: 400/765 kV AC Confidence: Medium
Note on I52: Source: POWERGRID; Indian 400/765 kV unit-cost matrix Corridor: IN_N↔IN_E Type: 400/765 kV AC Confidence: Medium
Note on I58: Source: 765 kV AC/HVDC building blocks Corridor: IN_N↔IN_W Type: 400/765 kV AC/HVDC Confidence: Medium
Note on I59: Source: 765 kV AC/HVDC building blocks Corridor: IN_N↔IN_W Type: 400/765 kV AC/HVDC Confidence: Medium
Note on I65: Source: 400 kV AC constrained NE corridor Corridor: IN_E↔IN_NE Type: 400 kV AC Confidence: Medium
Note on I66: Source: 400 kV AC constrained NE corridor Corridor: IN_E↔IN_NE Type: 400 kV AC Confidence: Medium
Note on I72: Source: 765 kV/HVDC + Pugalur-N.Trichur VSC calibration Corridor: IN_E↔IN_S Type: 765 kV AC / HVDC Confidence: Medium
Note on I73: Source: 765 kV/HVDC + Pugalur-N.Trichur VSC calibration Corridor: IN_E↔IN_S Type: 765 kV AC / HVDC Confidence: Medium
Note on I79: Source: 400/765 kV AC medium-long corridor Corridor: IN_W↔IN_S Type: 400/765 kV AC Confidence: Medium
Note on I80: Source: 400/765 kV AC medium-long corridor Corridor: IN_W↔IN_S Type: 400/765 kV AC Confidence: Medium
Note on I86: Source: PFCCL 2025 concept (400 MW, 750 km) Corridor: MV↔IN_S Type: Submarine HVDC Confidence: Low
Note on I87: Source: PFCCL 2025 concept (400 MW, 750 km) Corridor: MV↔IN_S Type: Submarine HVDC Confidence: Low

## Existing_Generation
Country | Node | Plant_Name | Technology_Code | Technology_Name | Fuel | Capacity_MW | Commissioning_Year | Expected_Retirement_Year | Capacity_Factor_Annual | Status | Source
Bangladesh | BD | Ghorasal Repowered CCPP Unit-3 (GT) |  |  | Gas | 260 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ghorasal Repowered CCPP Unit-4 |  |  | Gas | 210 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ghorasal TPP Unit-5 |  |  | Gas | 210 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ghorasal 365 MW CCPP Unit-7 |  |  | Gas | 365 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ghorashal 108MW PP (Regent) |  |  | Gas | 108 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Tongi 80 MW GTPP |  |  | Gas | 105 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat 450 MW CCPP (MPL) |  |  | Gas | 450 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | 210 MW Siddhirgonj TPP |  |  | Gas | 210 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Haripur 412 MW CCPP |  |  | Gas | 412 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Siddhirgonj 2x120 MW GTPP |  |  | Gas | 210 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Siddhirganj 335 MW CCPP |  |  | Gas | 335 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat 335MW CCPP (Summit) |  |  | Gas | 335 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Madanganj-55 MW PP (Summit) |  |  | HFO | 55 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Gagnagar 102 MW PP (Digital Power) |  |  | HFO | 102 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Summit Power Ashulia |  |  | Gas | 45 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Summit Power Madhabdi |  |  | Gas | 35 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Gazipur 52 MW PP |  |  | HFO | 52 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Gazipur 100 MW PP |  |  | HFO | 105 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kodda 150MW PP (BR-Power gen) |  |  | HFO | 149 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kamalaghat 54 MW PP (Banco Energy) |  |  | HFO | 54 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kodda 300 MW PP Unit-2 (Summit) |  |  | HFO | 300 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kodda 149 MW PP Unit-1 (Summit) |  |  | HFO | 149 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Nababganj 55 MW PP (Southern Power) |  |  | HFO | 55 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Manikganj 55 MW PP (Northern) |  |  | HFO | 55 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat 104 MW PP (OPSL) |  |  | HFO | 104 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Manikgonj 162MW PP (MPGL) |  |  | HFO | 162 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Manikgonj 35MW Solar PP (Inspectra Solar) |  |  | Solar | 35 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kanchan Purbachal Power Generation |  |  | HFO | 55 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Unique Meghnaghat 584MW CCPP |  |  | Gas | 584 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat 583 MW CCPP (Summit) |  |  | Gas | 583 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Meghnaghat (Jera) 718MW CCPP |  |  | Gas | 718 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sripur 150 MW (BR-Power gen) |  |  | HFO | 150 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Karnaphuli Hydro PP Unit-1,2,3,4,5 |  |  | Hydro | 230 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chattogram TPP |  |  | Gas | 420 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kaptai 7 MW Solar PP |  |  | Solar | 6 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Raozan 25 MW PP |  |  | HFO | 25 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Teknaf 20MW PP (Solartech) |  |  | Solar | 20 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Patenga 50MW PP (Baraka) |  |  | HFO | 50 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  |  | HFO | 105 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shikalbaha Peaking GT |  |  | Gas | 150 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sikalbaha 225 MW CCPP |  |  | Gas | 225 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Anwara 300 MW PP (United) |  |  | HFO | 300 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Juldah 100 MW PP Unit-3 (Acorn) |  |  | HFO | 100 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Dohazari-Kalaish 100 MW Peaking |  |  | HFO | 102 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Hathazari 100 MW Peaking PP |  |  | HFO | 98 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chattogram 108 MW PP (ECPV) |  |  | HFO | 108 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sikalbaha 54 MW PP (Jodiac Power) |  |  | HFO | 54 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Karnaphuli Power Ltd. |  |  | HFO | 110 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Juldah Unit-2 (Acorn) |  |  | HFO | 100 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chattogram 116 MW PP (Anlima Energy) |  |  | HFO | 116 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Mirsharai 150 MW (BR-Power gen) |  |  | HFO | 163 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | SS Power 2x612MW Coal PP |  |  | Coal | 1224 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Matarbari 2x600 MW (CPGCL) |  |  | Coal | 1150 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Cox's Bazar Wind PP |  |  | Wind | 60 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 50 MW PP |  |  | Gas | 53 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 225 MW CCPP |  |  | Gas | 221 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 450 MW CCPP (South) |  |  | Gas | 360 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 450 MW CCPP (North) |  |  | Gas | 360 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 420 MW CCPP (East) |  |  | Gas | 400 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 195MW PP (APSCL-United) |  |  | Gas | 195 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 51 MW PP (Midland) |  |  | Gas | 51 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 150MW PP (Midland) |  |  | HFO | 150 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Titas 50 MW Peaking PP |  |  | HFO | 52 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chandpur 150 MW CCPP |  |  | Gas | 163 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chandpur 200MW (Desh Energy) |  |  | HFO | 200 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Jangalia 52 MW PP (Lakdanavi) |  |  | HFO | 52 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Cumilla 25 MW PP (Summit) |  |  | Gas | 25 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Feni 114 MW (Lakdanavi) |  |  | HFO | 114 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chowmuhani 113 MW |  |  | HFO | 113 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chandpur 115MW PP (Doreen) |  |  | HFO | 115 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ashuganj 55 MW PP (Precision) |  |  | Gas | 55 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sonagazi 75 MW Solar Plant (EGCB) |  |  | Solar | 75 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | RPCL 210MW CCPP |  |  | Gas | 210 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Jamalpur 115 MW PP (United) |  |  | HFO | 115 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Mymensingh 200 MW PP (United) |  |  | HFO | 200 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sarishabari 3 MW Solar Plant |  |  | Solar | 3 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sutiakhali 50 MW Solar PP |  |  | Solar | 50 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bhairob 54 MW PP |  |  | HFO | 54 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Tangail 22 MW PP (PPGL) |  |  | HFO | 22 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Fenchugonj CCPP Phase-1 |  |  | Gas | 97 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Fenchugonj CCPP Phase-2 |  |  | Gas | 104 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Kushiara 163 MW CCPP (KP) |  |  | Gas | 163 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shahjibazar GTPP Unit-8 & 9 |  |  | Gas | 70 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shajibazar 330 MW CCPP |  |  | Gas | 330 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sylhet 225 MW CCPP |  |  | Gas | 231 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sylhet 20 MW GTPP |  |  | Gas | 20 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shahjahanulla 25 MW PP |  |  | Gas | 25 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bibiana-II 341 MW CCPP (Summit) |  |  | Gas | 341 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bibiyana-III 400 MW CCPP |  |  | Gas | 400 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bibiyana South 383 MW CCPP |  |  | Gas | 383 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shahjibazar 100 MW GTPP |  |  | Gas | 100 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Shahjibazar 86MW PP (Shahjibazar) |  |  | Gas | 86 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bheramara 410 MW CCPP |  |  | Gas | 410 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Faridpur 50 MW Peaking PP |  |  | HFO | 54 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Gopalganj 100 MW Peaking PP |  |  | HFO | 109 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Khulna 225 MW CCPP |  |  | HSD/Gas | 230 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rupsha 105 MW PP (Orion rupsha) |  |  | HFO | 105 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Madhumati 100 MW PP |  |  | HFO | 105 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Mongla Orion 100 MW Solar PP |  |  | Solar | 100 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Maitree Super Thermal 1320 MW PP (BIFPCL) |  |  | Coal | 1234 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Khulna 330 MW CCPP |  |  | Gas/HSD | 336 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barisal 110 MW PP (Summit) |  |  | HFO | 110 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bhola 225 MW CCPP |  |  | Gas | 194 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Payra 1320 MW TPP (BCPCL) |  |  | Coal | 1244 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Potuakhali 150MW PP (UPPL) |  |  | HFO | 150 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barisal Electric 307 MW Coal |  |  | Coal | 307 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barisal 1 MW Solar PP |  |  | Solar | 1 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bhola 220MW CCPP (Nutan Bidyut BD) |  |  | Gas/HSD | 220 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Baghabari 71 MW GTPP |  |  | Gas | 71 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Baghabari 100 MW GTPP |  |  | Gas | 100 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Baghabari 50 MW Peaking PP |  |  | HFO | 52 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bera 70 MW Peaking PP |  |  | HFO | 71 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Chapainawabganj 100 MW Peaking PP |  |  | HFO | 104 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Katakhali 50 MW Peaking PP |  |  | HFO | 50 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Santahar 50 MW Peaking PP |  |  | HFO | 50 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 225MW CCPP Unit-1 |  |  | Gas | 210 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 225MW CCPP Unit-2 |  |  | Gas | 220 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 225MW CCPP Unit-3 |  |  | Gas | 220 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 400 MW CCPP Unit-4 |  |  | Gas | 414 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Natore 52 MW PP (Rajlanka) |  |  | HFO | 52 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bagura 113 MW PP (Confidence) U-1 |  |  | HFO | 113 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Bagura 113 MW PP (Confidence) U-2 |  |  | HFO | 113 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 6.55 MW Solar |  |  | Solar | 6 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajganj 68 MW Solar Park |  |  | Solar | 68 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Pabna Solar 100 MW |  |  | Solar | 100 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sirajgonj 2 MW Wind Power Plant |  |  | Wind | 2 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Pabna 64 MW Solar Plant |  |  | Solar | 65 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barapukuria TPP Unit-1 & 2 |  |  | Coal | 250 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Barapukuria 275 MW TPP Unit-3 |  |  | Coal | 274 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rangpur 20 MW GTPP |  |  | HSD | 20 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rangpur 113 MW PP (Confidence) |  |  | HFO | 113 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Saidpur 20 MW GTPP |  |  | HSD | 20 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Majipara Tatulia 8 MW Solar PP |  |  | Solar | 8 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Thakurgaon 115MW PP (Energypac) |  |  | HFO | 115 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Lalmonirhat 30 MW Solar (Intraco) |  |  | Solar | 30 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Teesta Solar Limited 200 MW |  |  | Solar | 200 |  |  | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Saidpur 150 MW Simple Cycle PP |  |  | HSD | 162 |  |  | Bangladesh_Power_Sector.xlsx
Bhutan | BT | Tala Hydropower Plant |  |  | Hydro | 1020 |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Mangdechhu Hydropower Plant |  |  | Hydro | 720 |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Chhukha Hydropower Plant |  |  | Hydro | 336 |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Dagachhu Hydropower Plant |  |  | Hydro | 252 |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Nikachhu Hydropower Plant |  |  | Hydro | 118 |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Kurichhu Hydropower Plant |  |  | Hydro | 60 |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Basochhu Hydropower Plant |  |  | Hydro | 64 |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Punatsangchhu-II Hydropower Plant (PHP-II) |  |  | Hydro | 1020 |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Mini/Micro Hydel Plants (various) |  |  | Hydro | - |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | DSP Solar Plant |  |  | Solar | - |  |  | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Diesel Generator Sets (various) |  |  | Diesel | - |  |  | Bhutan_Power_Infrastructure.xlsx
Nepal | NP | Kaligandaki 'A' (KGA) |  |  | Hydro | 144 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Middle Marsyangdi (MMHPS) |  |  | Hydro | 70 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Marsyangdi (MHPS) |  |  | Hydro | 69 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Kulekhani I |  |  | Hydro | 60 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Trishuli 3A HEP |  |  | Hydro | 60 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Kulekhani II |  |  | Hydro | 32 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Chameliya |  |  | Hydro | 30 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Trishuli |  |  | Hydro | 24 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Gandak |  |  | Hydro | 15 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Devighat |  |  | Hydro | 14.1 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Modikhola |  |  | Hydro | 14.8 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Kulekhani III HEP |  |  | Hydro | 14 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Sunkoshi |  |  | Hydro | 10.05 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Puwa Khola (Ilam) |  |  | Hydro | 6.2 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Chatara |  |  | Hydro | 3.2 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Panauti |  |  | Hydro | 2.4 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tatopani |  |  | Hydro | 2 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Seti (Pokhara) |  |  | Hydro | 1.5 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tinau |  |  | Hydro | 1.024 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Fewa |  |  | Hydro | 1 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Sundarijal |  |  | Hydro | 0.97 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Pharping |  |  | Hydro | 0.5 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Gamgad |  |  | Hydro | 0.4 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khandbari |  |  | Hydro | 0.25 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Jomsom |  |  | Hydro | 0.24 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Phidim |  |  | Hydro | 0.24 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Baglung |  |  | Hydro | 0.2 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Surnaiyagad |  |  | Hydro | 0.2 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Doti |  |  | Hydro | 0.2 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Ramechhap |  |  | Hydro | 0.15 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Terhathum |  |  | Hydro | 0.1 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Multifuel Power Plant (Duhabi) |  |  | Thermal (Multi-fuel) | 39 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Hetauda Diesel Power Plant |  |  | Thermal (Diesel) | 14.41 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Chilime HEP |  |  | Hydro | 22.1 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Tamakoshi HEP |  |  | Hydro | 456 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Sanjen HEP |  |  | Hydro | 14.8 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Sanjen HEP |  |  | Hydro | 42.5 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rasuwagadhi HEP |  |  | Hydro | 111 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khimti Khola HEP |  |  | Hydro | 60 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Bhotekoshi HEP |  |  | Hydro | 45 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Indrawati III HEP |  |  | Hydro | 7.5 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Jhimruk Khola HEP |  |  | Hydro | 12 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Andhi Khola HEP |  |  | Hydro | 9.4 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Mardi Khola HEP |  |  | Hydro | 4.8 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Lower Modi 1 HEP |  |  | Hydro | 10 |  |  | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Sipring Khola HEP |  |  | Hydro | 9.658 |  |  | Nepal_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Victoria |  |  | Major Hydro | 210 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kotmale |  |  | Major Hydro | 201 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Upper Kotmale |  |  | Major Hydro | 150 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Randenigala |  |  | Major Hydro | 122.6 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Rantembe |  |  | Major Hydro | 50 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Ukuwela |  |  | Major Hydro | 40 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Bowatenna |  |  | Major Hydro | 40 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Nillambe |  |  | Major Hydro | 3.2 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Uma Oya |  |  | Major Hydro | 122 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Samanalawewa |  |  | Major Hydro | 120 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kukuleganga |  |  | Major Hydro | 75 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Inginiyagala |  |  | Major Hydro | 8.8 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Udawalawa |  |  | Major Hydro | 4 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Laxapana |  |  | Major Hydro | 153.8 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Polpitiya |  |  | Major Hydro | 90 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Canyon |  |  | Major Hydro | 60 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wimalasurendra |  |  | Major Hydro | 50 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Broadlands |  |  | Major Hydro | 35 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Lakvijaya Unit 1 |  |  | Coal | 300 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Lakvijaya Unit 2 |  |  | Coal | 300 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Lakvijaya Unit 3 |  |  | Coal | 300 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa GT-07 |  |  | Oil | 115 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa CCY-1 GT (KCCP1) |  |  | Oil | 101 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa CCY-1 ST (KCCP1) |  |  | Oil | 54 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa CCY-2 GT (KCCP2) |  |  | Oil | 101 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa CCY-2 ST (KCCP2) |  |  | Oil | 54 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa Frame V GTs |  |  | Oil | 80 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda A |  |  | Oil | 80 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda B |  |  | Oil | 80 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Barge Mounted Plant |  |  | Oil | 60 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Uthuru Janani |  |  | Oil | 24 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Old Kelanitissa Diesel |  |  | Oil | 40 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Thambapavani (Mannar) Wind Farm |  |  | Wind | 103.5 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | IPP Wind (various) |  |  | Wind | 163 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | IPP Ground-Mounted Solar |  |  | Solar | 138 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Rooftop Solar (CEB network) |  |  | Solar | 657 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Rooftop Solar (LECO network) |  |  | Solar | 158 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | IPP Mini Hydro (aggregate) |  |  | Mini Hydro | 419 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | IPP Biomass / Waste Heat (aggregate) |  |  | Biomass/Waste Heat | 54 |  |  | SriLanka_Electricity_Infrastructure.xlsx
Maldives | MV | Greater Male' Diesel Power Plants |  |  | Diesel | 140 |  |  | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Greater Male' Solar PV (rooftop + ground) |  |  | Solar PV | 10 |  |  | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Outer Inhabited Islands — Diesel Gensets |  |  | Diesel | 181 |  |  | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Outer Inhabited Islands — Solar PV |  |  | Solar PV | 27 |  |  | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Resort Islands — Diesel Gensets |  |  | Diesel | 211 |  |  | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Resort Islands — Solar PV |  |  | Solar PV | 31 |  |  | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Battery Energy Storage Systems (BESS) — Nationwide |  |  | Storage | ≥8 MWh |  |  | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ADh. Maamigili Island Power System |  |  | Diesel |  |  |  | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | R. Dhuvaafaru Island Power System |  |  | Diesel |  |  |  | Maldives_Energy_Infrastructure.xlsx
India | IN_E | Amrit Bio Energy & Industries Ltd West Bengal Bankura 10 |  |  | Bio Power | 10 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Harinagar Sugar Mills Ltd Bihar Pashchim Champaran 14.5 |  |  | Bio Power | 14.5 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Ispat Alloys Ltd West Bengal Bardhaman 10 |  |  | Bio Power | 10 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Kamarhatty Power Ltd West Bengal Bardhaman 6 |  |  | Bio Power | 6 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | New Swadeshi Sugar Mill Ltd Bihar Pashchim Champaran 10 |  |  | Bio Power | 10 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] Bihar N.A. 88 |  |  | Bio Power | 88 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] Odisha N.A. 30 |  |  | Bio Power | 30.4 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Biomass & bagasse based cogen.] West Bengal N. |  |  | Bio Power | 274 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Bihar N.A. 26.4 |  |  | Bio Power | 26.4 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Jharkhand N.A. 20.14 |  |  | Bio Power | 20.14 | Pre-2000 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] Odisha N.A. 8.82 |  |  | Bio Power | 8.82 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Non-Bagasse based cogen.] West Bengal N.A. 43. |  |  | Bio Power | 43.52 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] Bihar N.A. 1.32 |  |  | Bio Power | 1.32 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] Odisha N.A. 5 |  |  | Bio Power | 5 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Others (districts not specified) [Waste to Energy (Off-grid)] West Bengal N.A. 8 |  |  | Bio Power | 8.34 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Shalivahana Green Energy Ltd Odisha Dhenkanal 20 |  |  | Bio Power | 20 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Bakreshwar TPS |  | Subcritical | Coal | 1050 | 1999-07-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Bandel TPS |  | Subcritical | Coal | 270 | 1965-05-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Barauni TPS |  | Subcritical | Coal | 500 | 2018-01-01 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Barh STPP |  | Supercritical | Coal | 3300 | 2013-11-30 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Bokaro A Extension TPS |  | Subcritical | Coal | 500 | 2016-03-22 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Budge Budge TPS |  | Subcritical | Coal | 750 | 1997-09-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Chandrapura (DVC) TPS |  | Subcritical | Coal | 500 | 2009-11-01 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Darlipali STPP |  | Supercritical | Coal | 1600 | 2019-12-01 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Derang TPP |  | Subcritical | Coal | 1200 | 2014-05-01 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Durgapur Projects (D.P.L.) TPS |  | Subcritical | Coal | 550 | 2007-11-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Durgapur Steel TPS |  | Subcritical | Coal | 1000 | 2011-07-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Farakka STPS |  | Subcritical | Coal | 2100 | 1986-01-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Haldia TPP |  | Subcritical | Coal | 600 | 2014-01-14 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Hiranmaye TPP |  | Subcritical | Coal | 300 | 2017-08-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | IB Valley TPS |  | Subcritical | Coal | 1740 | 1994-05-01 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Ind Barath (Utkal)/JSW Energy (Utkal) Ltd. |  | Subcritical | Coal | 700 | 2016-02-25 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Jojobera TPS |  | Subcritical | Coal | 240 | 2001-10-01 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Kahalgaon STPS |  | Subcritical | Coal | 2340 | 1992-03-01 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Kamalanga TPS |  | Subcritical | Coal | 1050 | 2013-03-29 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Kodarma TPP |  | Subcritical | Coal | 1000 | 2011-07-20 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Kolaghat TPS |  | Subcritical | Coal | 840 | 1984-10-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Maadurga Thermal Power (MTPCL) |  | Subcritical | Coal | 60 | 2024-09-23 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Mahadev Prasad or Jamshedpur Kandra STPP |  | Subcritical | Coal | 540 | 2012-11-01 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Maithon TPP |  | Subcritical | Coal | 1050 | 2011-09-01 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Mejia TPS |  | Subcritical | Coal | 2340 | 1995-12-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Muzaffarpur TPS |  | Subcritical | Coal | 390 | 2015-03-31 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Nabi Nagar TPP |  | Subcritical | Coal | 1000 | 2016-03-20 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | New NabiNagar TPP (Majhiyan) |  | Supercritical | Coal | 1980 | 2019-07-01 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | North Karanpura TPP |  | Supercritical | Coal | 1980 | 2023-01-18 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Patratu TPS |  | Ultra-Supercritical | Coal | 800 | 2025-10-16 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Raghunathpur TPS |  | Subcritical | Coal | 1200 | 2014-08-24 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Sagardighi TPS |  | Subcritical | Coal | 1600 | 2007-09-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Santaldih TPS |  | Subcritical | Coal | 500 | 2007-11-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Southern Generating Power Station (Southern Repl. TPS) |  | Subcritical | Coal | 135 | 1990-04-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Sterlite (Jharsuguda)/ Vedanta Thermal Power Plant |  | Subcritical | Coal | 600 | 2010-10-01 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Super Critical Buxar Thermal Power Plant |  | Supercritical | Coal | 660 | 2025-11-05 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Talcher or Kaniha Talcher STPS |  | Subcritical | Coal | 3000 | 1995-02-01 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Tenughat TPS |  | Subcritical | Coal | 420 | 1994-04-01 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Balimela Hydroelectric Power Project |  |  | Hydro | 510 | 1973-08-14 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Chuzachen Hydroelectric Power Project |  |  | Hydro | 110 | 2013-04-20 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Dikchu Hydroelectric Power Project |  |  | Hydro | 96 | 2017-04-11 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Hirakud (Burla & Chiplima) Hydroelectric Power Project |  |  | Hydro | 359.8 | 1956-12-18 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Jaldhaka I Hydroelectric Power Project |  |  | Hydro | 36 | 1967-08-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Jorethang Loop Hydroelectric Power Project |  |  | Hydro | 96 | 2015-09-22 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Machkund Hydroelectric Power Project |  |  | Hydro | 114.75 | 1955-08-19 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Maithon Hydroelectric Power Project |  |  | Hydro | 63.2 | 1957-10-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Panchet Hydroelectric Power Project |  |  | Hydro | 80 | 1959-06-12 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Purulia Hydroelectric Power Project |  |  | Hydro | 900 | 2007-12-17 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Rammam II Hydroelectric Power Project |  |  | Hydro | 50 | 1995-08-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Rangit Hydroelectric Power Project |  |  | Hydro | 60 | 2000-02-03 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Rengali Hydroelectric Power Project |  |  | Hydro | 250 | 1985-08-27 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Rongnichu Hydro Power Project |  |  | Hydro | 113 | 2021-06-01 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Subernarekha I & II Hydroelectric Power Project |  |  | Hydro | 130 | 1977-05-30 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Tashiding Hydroelectric Power Project |  |  | Hydro | 97 | 2018-11-06 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta III Hydroelectric Power Project |  |  | Hydro | 1200 | 2017-01-14 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Low Dam III Hydroelectric Power Project |  |  | Hydro | 132 | 2013-01-20 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Low Dam IV Hydroelectric Power Project |  |  | Hydro | 160 | 2016-02-14 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta V Hydroelectric Power Project |  |  | Hydro | 510 | 2008-02-06 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Upper Indravati Hydroelectric Power Project |  |  | Hydro | 600 | 1999-09-19 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Upper Kolab Hydroelectric Power Project |  |  | Hydro | 320 | 1988-03-15 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Amethi Small Hydro Project |  |  | Small Hydro | 0.5 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Angoor Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Arwal Small Hydro Project |  |  | Small Hydro | 0.5 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | BSHPC Small Hydro Project 1 |  |  | Small Hydro | 2 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | BSHPC Small Hydro Project 2 |  |  | Small Hydro | 3.3 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Baitarini Power Hydel Project |  |  | Small Hydro | 24 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Barun Small Hydel Power Station |  |  | Small Hydro | 3.3 | 1996-12-01 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Belsar Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Dehri Small Hydel Power Station |  |  | Small Hydro | 6.6 | 1995-12-01 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Dhelabagh Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Fazi Hydel Project |  |  | Small Hydro | 1.2 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Goutamghagh Mini Hydel Scheme |  |  | Small Hydro | 0.01 | 1999-01-07 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Jaldhaka Small Hydro Project II |  |  | Small Hydro | 8 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Jalimghagh Mini Hydel Scheme |  |  | Small Hydro | 0.02 | 1997-03-14 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Kakatiya Hydroelectric Project |  |  | Small Hydro | 9 | 2022-04-30 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Kataiya Small Hydro Project |  |  | Small Hydro | 3 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Kosi Small Hydro Project |  |  | Small Hydro | 20 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Little Rangit Small Hydro Project |  |  | Small Hydro | 2 | 1970-01-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Lower Kolab Small Hydro Electric Project |  |  | Small Hydro | 12 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Massanjore Hydel Project |  |  | Small Hydro | 4 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Middle Kolab Small Hydro Electric Project |  |  | Small Hydro | 25 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Mungopoo-Kalikhola Small Hydro Project |  |  | Small Hydro | 3 | 2003-12-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Nasriganj Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Neora Hydro Limited Small Hydro Project |  |  | Small Hydro | 3 | 2006-04-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Nindighagh Mini Hydel Scheme |  |  | Small Hydro | 0.02 | 1997-03-14 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Nippon Power Limited Small Hydro Project |  |  | Small Hydro | 3 | 2007-03-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Paharma Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Potteru Hydro Electric Project Phase I |  |  | Small Hydro | 6 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Rajpur Small Hydro Project |  |  | Small Hydro | 0.7 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Rampur Small Hydro Project |  |  | Small Hydro | 0.25 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Richington Small Hydro Project |  |  | Small Hydro | 2 | 1979-12-01 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 1 |  |  | Small Hydro | 3 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 10 |  |  | Small Hydro | 8 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 2 |  |  | Small Hydro | 3 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 3 |  |  | Small Hydro | 3 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 4 |  |  | Small Hydro | 2 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 5 |  |  | Small Hydro | 3 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 6 |  |  | Small Hydro | 2 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 7 |  |  | Small Hydro | 12 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 8 |  |  | Small Hydro | 4 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | SPDCL Small Hydro Project 9 |  |  | Small Hydro | 2.5 | Pre-2000 | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Samal Hydro Electric Project |  |  | Small Hydro | 20 | 2009-10-11 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Sapthadharo Small Hydroelectric Project |  |  | Small Hydro | 18 | Pre-2000 | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Sebari Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Shrikhinda Small Hydro Project |  |  | Small Hydro | 0.7 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Sidrapong Small Hydro Project |  |  | Small Hydro | 0.6 | 1897-10-11 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Falls Small Hydro Project Phase 1 |  |  | Small Hydro | 22.5 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Falls Small Hydro Project Phase 2 |  |  | Small Hydro | 22.5 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta Falls Small Hydro Project Phase 3 |  |  | Small Hydro | 22.5 | Pre-2000 | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Tejpura Small Hydro Project |  |  | Small Hydro | 1.5 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Titaiya Small Hydro Project |  |  | Small Hydro | 4 | 1953-02-01 | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Triveni Link Canal Small Hydro Project |  |  | Small Hydro | 3 | Pre-2000 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Valmikinagar Hydroelectric Power Station |  |  | Small Hydro | 15 | 1993-12-01 | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_S | Kalpong Hydro Electric Project |  |  | Small Hydro | 5.25 | 2001-09-01 | Andaman and Nicobar Islan | India_Electricity_Infrastructure.xlsx
India | IN_NE | Others (districts not specified) [Non-Bagasse based cogen.] Assam N.A. 2 |  |  | Bio Power | 2 | Pre-2000 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Others (districts not specified) [Non-Bagasse based cogen.] Meghalaya N.A. 13.8 |  |  | Bio Power | 13.8 | Pre-2000 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Bongaigaon TPP |  | Subcritical | Coal | 750 | 2015-06-02 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Doyang Hydroelectric Power Project |  |  | Hydro | 75 | 2000-06-29 | Nagaland | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kameng Hydro Power Project |  |  | Hydro | 600 | 2020-02-01 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Karbi Langpai Hydroelectric Power Project |  |  | Hydro | 100 | 2007-06-29 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Khandong Hydroelectric Power Project |  |  | Hydro | 46 | 1984-03-08 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kopili Hydroelectric Power Project |  |  | Hydro | 200 | 1988-07-04 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kyrdemkulai (Umium III) Hydroelectric Power Project |  |  | Hydro | 60 | 1979-06-01 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Loktak Hydroelectric Power Project |  |  | Hydro | 105 | 1983-06-01 | Manipur | India_Electricity_Infrastructure.xlsx
India | IN_NE | Myntdu I Hydroelectric Power Project |  |  | Hydro | 126 | 2011-11-23 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | New Umtru Hydroelectric Power Project |  |  | Hydro | 40 | 2017-04-22 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Pare Hydroelectric Power Project |  |  | Hydro | 110 | 2018-05-21 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Ranganadi Hydroelectric Power Project |  |  | Hydro | 405 | 2002-01-26 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Subansiri Lower Hydro Power Project |  |  | Hydro | 250 | 2025-12-18 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tuirial Hydroelectric Power Project |  |  | Hydro | 60 | 2017-08-25 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Umium I Hydroelectric Power Project |  |  | Hydro | 36 | 1965-02-21 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Umium IV Hydroelectric Power Project |  |  | Hydro | 60 | 1992-08-11 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Agartala Gas Turbine Power Station |  |  | Oil & Gas | 135 | 1998-02-06 | Tripura | India_Electricity_Infrastructure.xlsx
India | IN_NE | Baramura Gas Thermal Project |  |  | Oil & Gas | 42 | 2002-11-27 | Tripura | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kathalguri (Assam) Gas Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 291 | 1995-03-16 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lakwa GT Replacement Power Project (LRPP ) |  |  | Oil & Gas | 69.75 | 2018-10-01 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lakwa Gas Turbine Power Station |  |  | Oil & Gas | 97.2 | 1994-01-03 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Namrup Thermal Power Station (NTPS) |  |  | Oil & Gas | 139.4 | 1965-04-01 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Rokhia Gas Thermal Project |  |  | Oil & Gas | 63 | 2002-08-02 | Tripura | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tripura (Monarchak) Gas based Combined Cycle Power Plant |  |  | Oil & Gas | 101 | 2015-03-30 | Tripura | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tripura (Palatana) Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 726.6 | 2013-01-02 | Tripura | India_Electricity_Infrastructure.xlsx
India | IN_NE | Atenglok Multipurpose Pico Hydel Power Project |  |  | Small Hydro | 0.01 | 2008-11-14 | Manipur | India_Electricity_Infrastructure.xlsx
India | IN_NE | Chadong Kong Micro Hydel Power Project |  |  | Small Hydro | 0.03 | 2011-06-27 | Manipur | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 1 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 10 |  |  | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 11 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 12 |  |  | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 13 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 14 |  |  | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 15 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 16 |  |  | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 17 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 18 |  |  | Small Hydro | 4.5 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 2 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 3 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 4 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 5 |  |  | Small Hydro | 4 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 6 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 7 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 8 |  |  | Small Hydro | 2 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | DHPD Small Hydro Project 9 |  |  | Small Hydro | 4.5 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Dhansiri Small Hydro Power Project |  |  | Small Hydro | 20 | Pre-2000 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Flovel Small Hydro Project |  |  | Small Hydro | 16 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Ganol Hydro Power Project |  |  | Small Hydro | 22.5 | 2023-07-31 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Gelnel Mini Hydel Power Project |  |  | Small Hydro | 0.4 | 2010-09-04 | Manipur | India_Electricity_Infrastructure.xlsx
India | IN_NE | Gumti Hydel Project |  |  | Small Hydro | 15 | 1976-12-01 | Tripura | India_Electricity_Infrastructure.xlsx
India | IN_NE | Iru Lok Hydel Power Project |  |  | Small Hydro | 0.01 | 2012-01-21 | Manipur | India_Electricity_Infrastructure.xlsx
India | IN_NE | Kau Tlabung Small Hydro Project |  |  | Small Hydro | 3 | 2005-05-05 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Khawiva Small Hydro Project |  |  | Small Hydro | 1.05 | 1988-12-08 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lakhroh Mini Hydel Project |  |  | Small Hydro | 1.5 | 2019-03-01 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lamsial Mini Hydel Project |  |  | Small Hydro | 0.5 | 2008-08-26 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lang Hydro Electric Project |  |  | Small Hydro | 1 | Pre-2000 | Nagaland | India_Electricity_Infrastructure.xlsx
India | IN_NE | Likimro Small Hydro Project |  |  | Small Hydro | 24 | Pre-2000 | Nagaland | India_Electricity_Infrastructure.xlsx
India | IN_NE | Machima I Small Hydro Project |  |  | Small Hydro | 2 | 1996-01-05 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Machima II Small Hydro Project |  |  | Small Hydro | 3 | 2009-11-11 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Mizoram Small Hydro Project Bunched |  |  | Small Hydro | 10.62 | Pre-2000 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Mizoram State Hydro Project 1 |  |  | Small Hydro | 3 | Pre-2000 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Mizoram State Hydro Project 2 |  |  | Small Hydro | 2.5 | Pre-2000 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Multipurpose Pico Hydel Project |  |  | Small Hydro | 0.01 | 2009-12-30 | Manipur | India_Electricity_Infrastructure.xlsx
India | IN_NE | Myntriang Small Hydroelectric Project (MSHEP) |  |  | Small Hydro | 13.5 | Pre-2000 | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Nametrang Small Hydro Project |  |  | Small Hydro | 3 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Nuranang Small Hydro Project |  |  | Small Hydro | 6 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Serlui A Small Hydro Project |  |  | Small Hydro | 1 | 1984-04-24 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Serlui B Small Hydro Project |  |  | Small Hydro | 12 | 2010-04-30 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Siru Small Hydro Electric Project |  |  | Small Hydro | 6 | Pre-2000 | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Sonapani Mini Hydel Electric Project |  |  | Small Hydro | 1.5 | 2009-10-27 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tehok Hydro Electric Project |  |  | Small Hydro | 1 | Pre-2000 | Nagaland | India_Electricity_Infrastructure.xlsx
India | IN_NE | Terei Small Hydro Project |  |  | Small Hydro | 3 | 1999-10-12 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tsütsüng hydro electric project |  |  | Small Hydro | 1 | 2022-05-03 | Nagaland | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tuipanglui Small hydro Project |  |  | Small Hydro | 3 | 2004-12-17 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tuipui Mini Hydel Project |  |  | Small Hydro | 0.5 | 1991-12-15 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tuirivang Small Hydro Project |  |  | Small Hydro | 0.3 | 1989-08-14 | Mizoram | India_Electricity_Infrastructure.xlsx
India | IN_NE | Umium Stage II Small Hydro Project |  |  | Small Hydro | 18 | 1970-07-22 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_NE | Umtru Small Hydro Project |  |  | Small Hydro | 11.2 | 1957-05-01 | Meghalaya | India_Electricity_Infrastructure.xlsx
India | IN_N | A2Z Gurgaon Uttar Pradesh Kanpur Nagar 15 |  |  | Bio Power | 15 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | AB Grains Spirits Pvt. Ltd. Haryana Ambala 8.9 2014-15 |  |  | Bio Power | 8.9 | 2014-01-15 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | ADS Spirits Pvt.Ltd. Haryana Jhajjar 2.3 2013-14 |  |  | Bio Power | 2.3 | 2013-01-14 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Aguata Sugar and Chemicals Uttar Pradesh Bulandshahar 2.5 |  |  | Bio Power | 2.5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Akbarchinimill Uttar Pradesh Ayodhya 11 |  |  | Bio Power | 11 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Amrit Envi. Tech. (P) Ltd. Rajasthan Jaipur 8 2006-10-01 |  |  | Bio Power | 8 | 2006-10-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Anand Triplex board Uttar Pradesh Meerut 10 2008-09 |  |  | Bio Power | 10 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Arohal Food Pvt.Ltd, Uttar Pradesh Bahraich 0.4 2008-09 |  |  | Bio Power | 0.4 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ashoka Distillers& Chemicals Ltd. Haryana Palwal 3 2015-16 |  |  | Bio Power | 3 | 2015-01-16 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Avani Tripura Dev Uttarakhand Pithoragarh 0.12 |  |  | Bio Power | 0.12 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Awadh sugarmill Uttar Pradesh Sitapur 10 |  |  | Bio Power | 10 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | BAHL Paper Mill Uttarakhand Udham Singh Nagar 4 |  |  | Bio Power | 4 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj Chinimill Uttar Pradesh Kheri 12 |  |  | Bio Power | 12 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj Hindustan sugarmill Uttar Pradesh Kheri 12 |  |  | Bio Power | 12 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj Hindustan sugarmill Uttar Pradesh Shahjahanpur 12 |  |  | Bio Power | 12 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj Kagaj Pvt Ltd Uttar Pradesh Unnao 1 2009-10 |  |  | Bio Power | 1 | 2009-10-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaj sugarmill Uttar Pradesh Gonda 12 |  |  | Bio Power | 12 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz Hindustan Kinaunee Uttar Pradesh Meerut 10 |  |  | Bio Power | 10 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz Hindustan Ltd Uttar Pradesh Bijnor 10 |  |  | Bio Power | 10 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz Hindustan Ltd Uttar Pradesh Shamli 10 |  |  | Bio Power | 10 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz sugar Limited Uttar Pradesh Pilibhit 7 |  |  | Bio Power | 7 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz sugarmill Uttar Pradesh Muzaffarnagar 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz sugarmill Uttar Pradesh Pilibhit 12 |  |  | Bio Power | 12 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajaz sugarmill Uttar Pradesh Saharanpur 10 |  |  | Bio Power | 10 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balrampur Chinimill Uttar Pradesh Balrampur 22.25 |  |  | Bio Power | 22.25 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balrampur Chinimill Uttar Pradesh Gonda 5 |  |  | Bio Power | 5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balrampur Chinimill Uttar Pradesh Kheri 11 |  |  | Bio Power | 11 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balrampur Chinimill Uttar Pradesh Kheri 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Best Food International (P) Ltd Haryana Karnal 4 2010-11 |  |  | Bio Power | 4 | 2010-11-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Best Food International (P) Ltd Haryana Karnal 6 2012-13 |  |  | Bio Power | 6 | 2012-01-13 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhaghauli sugarmill and Distilery Uttar Pradesh Hardoi 12 |  |  | Bio Power | 12 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bharat Sugar Mills Uttar Pradesh Prayagraj 15 |  |  | Bio Power | 15 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhavani papermill Uttar Pradesh Rae Bareli 6 2007-08 |  |  | Bio Power | 6 | 2007-08-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bindal papermill Uttar Pradesh Muzaffarnagar 15 2008-09 |  |  | Bio Power | 15 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Centuri lamination Uttar Pradesh Ghaziabad 4.2 2008-09 |  |  | Bio Power | 4.2 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ch.DeviLal Co-operative Sugar Mill Ltd. Haryana Sonipat 6 2003-04 |  |  | Bio Power | 6 | 2003-04-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Chaddha sugarmill Uttar Pradesh Amroha 23 |  |  | Bio Power | 23 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | DSCL Uttar Pradesh Kheri 12 |  |  | Bio Power | 12 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | DSCL sugarmill Uttar Pradesh Hardoi 15 |  |  | Bio Power | 30 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dalmiya chinimill Uttar Pradesh Shahjahanpur 25 |  |  | Bio Power | 25 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dalmiya chinimill Uttar Pradesh Sitapur 25 |  |  | Bio Power | 50 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Daurala Sugar Mills Uttar Pradesh Meerut 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dawarala sugarmill Uttar Pradesh Meerut 10 |  |  | Bio Power | 10 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dee Development Engineers Pvt. Ltd Punjab Ferozepur 8 2009-02-01 |  |  | Bio Power | 8 | 2009-02-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Deopriya papermill Uttar Pradesh Meerut 6 2006-07 |  |  | Bio Power | 6 | 2006-07-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhampur Sugars Ltd (DSM) Uttar Pradesh Bijnor 30 |  |  | Bio Power | 30 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhampur Sugars Ltd (DSM) Uttar Pradesh Kanpur Dehat 40 |  |  | Bio Power | 40 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhampur Sugars Ltd (DSM) Uttar Pradesh Moradabad 40 |  |  | Bio Power | 40 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhampur Sugars Ltd (DSM) Uttar Pradesh Muzaffarnagar 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dwarkesh chinimill Uttar Pradesh Bijnor 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dwarkesh sugarmill Uttar Pradesh Bareilly 24 |  |  | Bio Power | 24 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dwarkesh sugarmill Uttar Pradesh Bijnor 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | EICL Ltd. (Bharat Starch Industries) Haryana Yamuna Nagar 2 2008-09 |  |  | Bio Power | 2 | 2008-09-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | East Delhi Waste Processing Company Limited (EDWRCL) Delhi East Delhi 12 21.10.2 |  |  | Bio Power | 12 | 2012-10-21 | Delhi | India_Electricity_Infrastructure.xlsx
India | IN_N | GEMCO Energy Limited Haryana Bhiwani 8 2013-14 |  |  | Bio Power | 8 | 2013-01-14 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Ganga papermill Uttar Pradesh Varanasi 1.5 2008-09 |  |  | Bio Power | 1.5 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ginus papermill Uttar Pradesh Moradabad 6 2007-08 |  |  | Bio Power | 6 | 2007-08-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Goel International Pvt. Ltd. Haryana Karnal 3 2011-12 |  |  | Bio Power | 3 | 2011-12-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Govindnagar Sugar Uttar Pradesh Basti 6 |  |  | Bio Power | 6 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Green Planet Energy Pvt. Ltd. Punjab Hoshiarpur 6 2012-03-01 |  |  | Bio Power | 6 | 2012-03-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Green Planet Energy Pvt. Ltd. Punjab Jalandhar 6 2013-02-01 |  |  | Bio Power | 6 | 2013-02-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Gulsan sugar and Chemical Uttar Pradesh Muzaffarnagar 4 2008-09 |  |  | Bio Power | 4 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Haidergarh chinimill Uttar Pradesh Bara Banki 20.95 |  |  | Bio Power | 20.95 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Haryana Liquors Haryana Karnal 2.5 2014-15 |  |  | Bio Power | 2.5 | 2014-01-15 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | J.H.V.Sugar Uttar Pradesh Maharajganj 17 |  |  | Bio Power | 17 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | J.K.Sugarmill Uttar Pradesh Bareilly 12.5 |  |  | Bio Power | 12.5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Jhunjunwala Vanaspati, Uttar Pradesh Jaunpur 3 2008-09 |  |  | Bio Power | 3 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | K. R. Pulp and Paper Ltd. Uttar Pradesh Shahjahanpur 2.5 2008-09 |  |  | Bio Power | 2.5 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | K.M.Sugarmill Uttar Pradesh Ayodhya 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | K.R. Pulp paper Uttar Pradesh Shahjahanpur 12 2009-10 |  |  | Bio Power | 12 | 2009-10-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | KalpaTaru Power Transmission Ltd. Rajasthan Ganganagar 7.8 2003-07-15 |  |  | Bio Power | 7.8 | 2003-07-15 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | KalpaTaru Power Transmission Ltd. Rajasthan Tonk 8 2006-11-10 |  |  | Bio Power | 8 | 2006-11-10 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Kamlapur Sugar and Industries Uttar Pradesh Sitapur 45 |  |  | Bio Power | 45 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kayem (PAN) Foods Industries (P ) Ltd. Haryana Panipat 0.5 2011-12 |  |  | Bio Power | 0.5 | 2011-12-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Kesar Industries Uttar Pradesh Bareilly 25 |  |  | Bio Power | 25 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | L.H.Sugar Factory Ltd Uttar Pradesh Pilibhit 28 |  |  | Bio Power | 28 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Laxmi Sugar Mill Uttarakhand Haridwar 20 |  |  | Bio Power | 20 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Laxmi cotton Uttar Pradesh Fatehpur 8 2009-10 |  |  | Bio Power | 8 | 2009-10-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Laxmi cottonmill Uttar Pradesh Fatehpur 17.5 2008-09 |  |  | Bio Power | 17.5 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | MSW Bawana Delhi N.A. 24 09.07.2016 |  |  | Bio Power | 24 | 2016-09-07 | Delhi | India_Electricity_Infrastructure.xlsx
India | IN_N | Mahavir spin Uttar Pradesh Unnao 0.4 2008-09 |  |  | Bio Power | 0.4 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Malwa Power Ltd. Punjab Sri Muktsar Sahib 6 2005-05-01 |  |  | Bio Power | 6 | 2005-05-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Mankapur chinimill Uttar Pradesh Gonda 25 |  |  | Bio Power | 25 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Maruti papermill Uttar Pradesh Muzaffarnagar 1.5 2008-09 |  |  | Bio Power | 1.5 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mawana sugars Ltd Uttar Pradesh Meerut 11 |  |  | Bio Power | 11 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mawana sugars Ltd Uttar Pradesh Meerut 9 |  |  | Bio Power | 9 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mawana sugars Ltd Uttar Pradesh Muzaffarnagar 17 |  |  | Bio Power | 17 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mohit Petro Chemi Uttar Pradesh Bijnor 1 2008-09 |  |  | Bio Power | 1 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mohit papermill Uttar Pradesh Bijnor 4.5 2008-09 |  |  | Bio Power | 4.5 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | NV Distilleries Limited Haryana Ambala 2.1 2012-13 |  |  | Bio Power | 2.1 | 2012-01-13 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | NV International Haryana Ambala 4 2014-15 |  |  | Bio Power | 4 | 2014-01-15 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | New India sugar Ltd. Uttar Pradesh Kushinagar 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Nova Uttar Pradesh Farrukhabad 1 2008-09 |  |  | Bio Power | 1 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Orient Green Power Co. Rajasthan Baran 8 2013-10-06 |  |  | Bio Power | 8 | 2013-10-06 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Oswal overseas Uttar Pradesh Bareilly 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) (Waste to Energy) Delhi N.A. 33.17 |  |  | Bio Power | 33.17 | Pre-2000 | Delhi | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) (Waste to Energy) Haryana N.A. 11.2 |  |  | Bio Power | 11.2 | Pre-2000 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) (Waste to Energy) Punjab N.A. 10.75 |  |  | Bio Power | 10.75 | Pre-2000 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) (Waste to Energy) Rajasthan N.A. 59.6 |  |  | Bio Power | 59.6 | Pre-2000 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Haryana N.A. 4 |  |  | Bio Power | 47.03 | Pre-2000 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Punjab N.A. 23 |  |  | Bio Power | 237 | Pre-2000 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Rajasthan N.A. |  |  | Bio Power | 29.9 | Pre-2000 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Uttar Pradesh |  |  | Bio Power | 834.69 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Uttarakhand N. |  |  | Bio Power | 4 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Haryana N.A. 65.88 |  |  | Bio Power | 65.88 | Pre-2000 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Himachal Pradesh N.A |  |  | Bio Power | 9.2 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Punjab N.A. 231.7900 |  |  | Bio Power | 231.79 | Pre-2000 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Rajasthan N.A. 2 |  |  | Bio Power | 2 | Pre-2000 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Uttar Pradesh N.A. 7 |  |  | Bio Power | 7.86 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Non-Bagasse based cogen.] Uttarakhand N.A. 60 |  |  | Bio Power | 60 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Haryana N.A. 38.61 |  |  | Bio Power | 38.61 | Pre-2000 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Himachal Pradesh N |  |  | Bio Power | 1 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Punjab N.A. 34.55 |  |  | Bio Power | 34.55 | Pre-2000 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Rajasthan N.A. 11. |  |  | Bio Power | 11.77 | Pre-2000 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Uttar Pradesh N.A. |  |  | Bio Power | 159.63 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Waste to Energy (Off-grid)] Uttarakhand N.A. 1 |  |  | Bio Power | 16.85 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Parle zee Ltd Uttar Pradesh Bahraich 10 |  |  | Bio Power | 10 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Punjab Biomass Power Pvt. Ltd. Punjab Patiala 12 2010-06-01 |  |  | Bio Power | 12 | 2010-06-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | R.P Basmati Rice Ltd Haryana Karnal 0.5 2010-11 |  |  | Bio Power | 0.5 | 2010-11-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | REI Agro Ltd, (Unit-I) Haryana Rewari 3 2011-12 |  |  | Bio Power | 3 | 2011-12-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | REI Agro Ltd, (Unit-II) Bawal Growth Centres Haryana Rewari 2.5 2010-11 |  |  | Bio Power | 2.5 | 2010-11-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Raghuraji Agro Ind. Uttar Pradesh Ambedkar Nagar 1.1 2008-09 |  |  | Bio Power | 1.1 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Rai Bahadur Narain Singh Sugar Mills Ltd Uttarakhand Haridwar 29.6 |  |  | Bio Power | 29.6 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Rama papers Ltd Uttar Pradesh Bijnor 6 2006-07 |  |  | Bio Power | 6 | 2006-07-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ramnagar Chini Mills Uttar Pradesh Shahjahanpur 16 |  |  | Bio Power | 16 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Rana Sugars Ltd. Uttar Pradesh Rampur 15 |  |  | Bio Power | 15 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ranya papermill Uttar Pradesh Basti 3 2007-08 |  |  | Bio Power | 3 | 2007-08-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Rozagaon chinimill Uttar Pradesh Bara Banki 16 |  |  | Bio Power | 16 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | S.M. Environmental Technologies Pvt. Ltd. Rajasthan Baran 8 2010-02-19 |  |  | Bio Power | 8 | 2010-02-19 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | SIAL SBEC Bioenergy Uttar Pradesh Baghpat 14 |  |  | Bio Power | 14 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | SSA International Ltd, Haryana Panipat 1.1 |  |  | Bio Power | 1.1 | Pre-2000 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Sainsons Paper Industries Haryana Kurukshetra 3 2009-10 |  |  | Bio Power | 3 | 2009-10-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Sakumbhari Stra Ltd. Uttar Pradesh Moradabad 12 2006-07 |  |  | Bio Power | 12 | 2006-07-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sambhav Energy Ltd. Rajasthan Sirohi 20 2010-02-19 |  |  | Bio Power | 20 | 2010-02-19 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Sangal Papermill Uttar Pradesh Meerut 3 2007-08 |  |  | Bio Power | 3 | 2007-08-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sanjog Sugar & Eco Power Pvt. Ltd. Rajasthan Hanumangarh 10 2011-10-07 |  |  | Bio Power | 10 | 2011-10-07 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Sant lal ricemill Uttar Pradesh Mainpuri 2.25 2009-10 |  |  | Bio Power | 2.25 | 2009-10-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sathyam Power Pvt Ltd Rajasthan Nagaur 10 2011-03-31 |  |  | Bio Power | 10 | 2011-03-31 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Satyam Industries Pvt. Ltd Haryana Panipat 3 2011-12 |  |  | Bio Power | 3 | 2011-12-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Saxsaria, Biswal Sugar Factory Uttar Pradesh Sitapur 45 |  |  | Bio Power | 45 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shaktibhog Foods Ltd Haryana Karnal 3.5 2014-15 |  |  | Bio Power | 3.5 | 2014-01-15 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Shakumbari Sugar and Allied Industries Ltd Uttar Pradesh Hardoi 16 |  |  | Bio Power | 16 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shri. Vishnu Overseas Pvt. Ltd Haryana Kaithal 1.5 2010-11 |  |  | Bio Power | 1.5 | 2010-11-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Simbholi sugar Ltd Uttar Pradesh Ghaziabad 5 |  |  | Bio Power | 5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Simbholi sugarmill Uttar Pradesh Bahraich 19 |  |  | Bio Power | 19 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sri Jyoti Renewable Energy Pvt. Ltd. Haryana Bhiwani 9.5 2014-15 |  |  | Bio Power | 9.5 | 2014-01-15 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Star Papermill Ltd. Uttar Pradesh Saharanpur 5 2008-09 |  |  | Bio Power | 5 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Starwire (India) Ltd Haryana Mahendragarh 9.9 2013-14 |  |  | Bio Power | 9.9 | 2013-01-14 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Sukhvir Agro Energy Ltd, Uttar Pradesh Ghazipur 13 |  |  | Bio Power | 13 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sumit Agro project, Uttar Pradesh Meerut 3 2007-08 |  |  | Bio Power | 3 | 2007-08-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunstar Overseas Ltd Haryana Sonipat 1.95 2010-11 |  |  | Bio Power | 1.95 | 2010-11-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Surya Chambal Power Ltd. Rajasthan Kota 7.5 2006-03-31 |  |  | Bio Power | 7.5 | 2006-03-31 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Syus papermill Uttar Pradesh Basti 3 2008-09 |  |  | Bio Power | 3 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | The HAFED Cooperative Sugar Mill Haryana Karnal 6 2010-11 |  |  | Bio Power | 6 | 2010-11-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | The Meham Cooperative Sugar Mill Haryana Rohtak 5 2007-08 |  |  | Bio Power | 5 | 2007-08-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | The Piccadily Agro Industries Haryana Karnal 17 2010-11 |  |  | Bio Power | 17 | 2010-11-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | The Rajasthan State Ganganagar Sugar Mills Ltd. Rajasthan Ganganagar 4.95 2016-0 |  |  | Bio Power | 4.95 | 2016-05-09 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | The Rohtak Cooperative Sugar Mill Haryana Rohtak 16 2009-10 |  |  | Bio Power | 16 | 2009-10-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | The Shahbad Cooperative Sugar Mill Haryana Kurukshetra 24 2009-10 |  |  | Bio Power | 24 | 2009-10-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | The Sonepat Cooperative Sugar Mill Ltd. Haryana Sonipat 3 2004- 05 |  |  | Bio Power | 3 | 2004-05-21 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Tikola sugarmill Ltd. Uttar Pradesh Muzaffarnagar 5 |  |  | Bio Power | 5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Timarpur Okhla Waste Management Co Pvt Ltd (TOWMCL) Delhi N.A. 16 27.01.2012 |  |  | Bio Power | 16 | 2012-01-27 | Delhi | India_Electricity_Infrastructure.xlsx
India | IN_N | Tirupati Basmati Exports Private Limited Haryana Karnal 1.2 2016-17 |  |  | Bio Power | 1.2 | 2016-01-17 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Transtech Green Power Ltd. Rajasthan Jalore 12 2010-07-28 |  |  | Bio Power | 12 | 2010-07-28 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Triveni sugarmill Uttar Pradesh Muzaffarnagar 20 |  |  | Bio Power | 20 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Triveni sugarmill Uttar Pradesh Saharanpur 19.16 |  |  | Bio Power | 19.16 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Universal Biomass Energy Pvt. Ltd. Punjab Sri Muktsar Sahib 14.5 2009-10-01 |  |  | Bio Power | 14.5 | 2009-10-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Gangej sugarmill Uttar Pradesh Bijnor 24 |  |  | Bio Power | 24 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ushar Agro Uttar Pradesh Mathura 1 2008-09 |  |  | Bio Power | 1 | 2008-09-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttam sugarmill Uttar Pradesh Bijnor 13.5 |  |  | Bio Power | 13.5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttar Sugar Mills Ltd Uttarakhand Haridwar 15 |  |  | Bio Power | 15 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttar sugarmill Uttar Pradesh Saharanpur 10 |  |  | Bio Power | 10 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttar sugarmill Uttar Pradesh Shahjahanpur 6.5 |  |  | Bio Power | 6.5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Viaton Energy Pvt. Ltd. Punjab Mansa 10 2013-07-01 |  |  | Bio Power | 10 | 2013-07-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Yado Sugar Uttar Pradesh Budaun 5 |  |  | Bio Power | 5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Yes papermill Uttar Pradesh Ayodhya 12.5 2006-07 |  |  | Bio Power | 12.5 | 2006-07-21 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Anpara C TPS or Lanco Anapara |  | Subcritical | Coal | 1200 | 2011-11-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Anpara TPS |  | Subcritical | Coal | 2630 | 1986-01-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Barkhera TPS |  | Subcritical | Coal | 90 | 2011-11-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Barsingar Lignite TPP |  | Subcritical | Coal | 250 | 2010-06-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Chhabra TPP |  | Subcritical | Coal | 2320 | 2009-10-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Dadri TPP (NCTPP) |  | Subcritical | Coal | 1820 | 1991-12-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghatampur TPP |  | Ultra-Supercritical | Coal | 1320 | 2024-12-03 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Giral Lignite TPS |  | Subcritical | Coal | 250 | 2007-02-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Goindwal Sahib TPP |  | Subcritical | Coal | 540 | 2016-02-14 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Guru Hargobind TPS |  | Subcritical | Coal | 920 | 1997-12-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Harduaganj TPS |  | Subcritical | Coal | 1265 | 1978-03-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Indira Gandhi STPP |  | Subcritical | Coal | 1500 | 2010-10-01 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Jalipa- Kapurdi TPP |  | Subcritical | Coal | 1080 | 2009-10-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Jawaharpur STPP |  | Ultra-Supercritical | Coal | 1320 | 2024-02-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kalisindh STPS |  | Supercritical | Coal | 1200 | 2014-05-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Kawai TPS |  | Supercritical | Coal | 1320 | 2013-05-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Khamberkhera TPS |  | Subcritical | Coal | 90 | 2011-10-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Khurja Power Project |  | Ultra-Supercritical | Coal | 1320 | 2025-01-23 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kota TPS |  | Subcritical | Coal | 1240 | 1983-01-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Kundarkhi TPS |  | Subcritical | Coal | 90 | 2012-01-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Lalitpur TPP |  | Supercritical | Coal | 1980 | 2016-01-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mahatma Gandhi TPS or Jhajjhar TPS |  | Supercritical | Coal | 1320 | 2012-01-01 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Maqsoodpur TPS |  | Subcritical | Coal | 90 | 2011-11-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Meja STPP |  | Supercritical | Coal | 1320 | 2018-03-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Obra TPS |  | Subcritical | Coal | 2320 | 1977-12-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Panipat TPS |  | Subcritical | Coal | 710 | 2001-03-01 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Panki TPS |  | Supercritical | Coal | 660 | 2025-02-25 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Parichha TPS |  | Subcritical | Coal | 920 | 2006-03-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Prayagraj (Bara) TPP |  | Supercritical | Coal | 1980 | 2015-12-25 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Rajiv Gandhi TPS |  | Subcritical | Coal | 1200 | 2010-03-01 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Rajpura TPP |  | Supercritical | Coal | 1400 | 2014-02-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Rihand STPS |  | Subcritical | Coal | 3000 | 1988-03-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ropar TPS or Guru Gobind Singh STPP |  | Subcritical | Coal | 840 | 1988-03-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Rosa TPP |  | Subcritical | Coal | 1200 | 2010-02-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shree Cement Ltd. TPS |  | Subcritical | Coal | 344 | 2023-08-31 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Singrauli STPS |  | Subcritical | Coal | 2000 | 1982-02-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Suratgarh STPS |  | Subcritical | Coal | 2820 | 1998-02-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Talwandi Sabo TPP |  | Supercritical | Coal | 1980 | 2014-06-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Tanda TPS |  | Subcritical | Coal | 1760 | 1988-01-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Unchahar or Feroz Gandhi TPS |  | Subcritical | Coal | 1550 | 1988-11-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Utraula TPS |  | Subcritical | Coal | 90 | 2012-02-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Yamuna Nagar or Deenbandhu Chotu Ram TPS |  | Subcritical | Coal | 600 | 2007-04-01 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Allain Duhangan Hydroelectric Power Project |  |  | Hydro | 192 | 2010-09-16 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Anandpur Sahib I & II Hydroelectric Power Project |  |  | Hydro | 134 | 1985-04-27 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Baglihar I Hydroelectric Power Project |  |  | Hydro | 450 | 2008-08-10 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Baglihar II Hydroelectric Power Project |  |  | Hydro | 450 | 2015-09-05 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Baira Siul Hydroelectric Power Project |  |  | Hydro | 180 | 1980-05-18 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bajoli Holi Hydro Power Project |  |  | Hydro | 180 | 2022-03-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Baspa II Hydroelectric Power Project |  |  | Hydro | 300 | 2003-05-24 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bassi Hydroelectric Power Project |  |  | Hydro | 66 | 1970-06-12 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhakra Nangal (Left & Right) Hydroelectric Power Project |  |  | Hydro | 1415 | 1960-11-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Budhil Hydroelectric Power Project |  |  | Hydro | 70 | 2012-05-26 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chamera I Hydroelectric Power Project |  |  | Hydro | 540 | 1994-05-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chamera II Hydroelectric Power Project |  |  | Hydro | 300 | 2003-11-02 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chamera III Hydroelectric Power Project |  |  | Hydro | 231 | 2012-06-07 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chanju I Hydroelectric Power Project |  |  | Hydro | 36 | 2017-02-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chibro (Yamuna St.II) Hydroelectric Power Project |  |  | Hydro | 240 | 1975-04-20 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Chilla Hydroelectric Power Project |  |  | Hydro | 144 | 1980-07-17 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Chutak Hydroelectric Power Project |  |  | Hydro | 44 | 2012-11-08 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dehar Power House |  |  | Hydro | 990 | 1977-11-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhakrani (Yamuna St.I) Hydroelectric Power Project |  |  | Hydro | 33.75 | 1965-11-15 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhalipur (Yamuna St.I) Hydroelectric Power Project |  |  | Hydro | 51 | 1965-12-10 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhauliganga Hydroelectric Power Project |  |  | Hydro | 280 | 2005-10-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Dulhasti Hydroelectric Power Project |  |  | Hydro | 390 | 2007-04-07 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Ganguwal Power House |  |  | Hydro | 77.65 | 1955-01-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Giri Bata Hydroelectric Power Project |  |  | Hydro | 60 | 1978-05-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Jawahar Sagar Hydroelectric Power Project |  |  | Hydro | 99 | 1972-05-09 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Karcham Wangtoo Hydroelectric Power Project |  |  | Hydro | 1045 | 2011-05-24 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kashang Integrated Hydroelectric Power Project |  |  | Hydro | 195 | 2016-08-28 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Khara Hydroelectric Power Project |  |  | Hydro | 72 | 1992-06-14 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Khatima Hydroelectric Power Project |  |  | Hydro | 41.4 | 1955-01-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Khodri (Yamuna St.II) Hydroelectric Power Project |  |  | Hydro | 120 | 1984-01-29 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kishenganga Hydroelectric Power Project |  |  | Hydro | 330 | 2018-03-13 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Koldam Hydroelectric Power Project |  |  | Hydro | 800 | 2015-03-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Koteshwar Hydroelectric Power Project |  |  | Hydro | 400 | 2011-03-28 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kotla Power House |  |  | Hydro | 77.65 | 1956-05-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Kulhal (Yamuna St.IV) Hydroelectric Power Project |  |  | Hydro | 30 | 1975-03-12 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kutehr Hydro Power Project |  |  | Hydro | 240 | 2025-08-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Larji Hydroelectric Power Project |  |  | Hydro | 126 | 2006-06-28 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Lower Jhelum Hydroelectric Power Project |  |  | Hydro | 105 | 1978-02-01 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Mahi Bajaj Sagar I & II Hydroelectric Power Project |  |  | Hydro | 140 | 1986-01-22 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Malana Hydroelectric Power Project |  |  | Hydro | 86 | 2001-07-05 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Malana II Hydroelectric Power Project |  |  | Hydro | 100 | 2011-08-06 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Maneri Bhali I Hydroelectric Power Project |  |  | Hydro | 90 | 1984-06-06 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Maneri Bhali II Hydroelectric Power Project |  |  | Hydro | 304 | 2008-06-30 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Matatilla Hydroelectric Power Project |  |  | Hydro | 30.6 | 1965-05-18 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mukerian I to IV Hydroelectric Power Project |  |  | Hydro | 207 | 1983-10-02 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Naitwar Mori Hydro Power Project |  |  | Hydro | 60 | 2023-11-24 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Naptha Jhakri Hydroelectric Power Project |  |  | Hydro | 1500 | 2003-05-06 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Nimoo Bazgo Hydroelectric Power Project |  |  | Hydro | 45 | 2013-10-30 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Obra Hydroelectric Power Project |  |  | Hydro | 99 | 1970-08-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Parbati III Hydroelectric Power Project |  |  | Hydro | 520 | 2014-02-18 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Parbati St. II Hydro Power Project |  |  | Hydro | 800 | 2025-03-24 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Pong Power House |  |  | Hydro | 396 | 1978-01-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ram Ganga Hydroelectric Power Project |  |  | Hydro | 198 | 1975-12-31 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Rampur Hydroelectric Power Project |  |  | Hydro | 412.02 | 2014-03-21 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Rana Pratap Sagar Hydroelectric Power Project |  |  | Hydro | 172 | 1968-08-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Ranjit Sagar Hydroelectric Power Project |  |  | Hydro | 600 | 2000-08-12 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Rihand Hydroelectric Power Project |  |  | Hydro | 300 | 1962-08-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sainj Hydroelectric Power Project |  |  | Hydro | 100 | 2017-09-04 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Salal I & II Hydroelectric Power Project |  |  | Hydro | 690 | 1987-11-20 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Sanjay Hydroelectric Power Project |  |  | Hydro | 120 | 1989-06-11 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sawra Kuddu Hydro Power Project |  |  | Hydro | 111 | 2021-01-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sewa II Hydroelectric Power Project |  |  | Hydro | 120 | 2010-06-22 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Shanan Power House |  |  | Hydro | 110 | 1932-08-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shrinagar Hydroelectric Power Project |  |  | Hydro | 330 | 2015-04-10 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Singoli Bhatwari Hydro Power Project |  |  | Hydro | 99 | 2020-12-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Sorang Hydro Power Project |  |  | Hydro | 100 | 2021-09-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Tanakpur Hydroelectric Power Project |  |  | Hydro | 94.2 | 1993-04-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Tehri I Hydroelectric Power Project |  |  | Hydro | 1000 | 2006-09-22 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Tehri Pumped Storage Hydro Power Project |  |  | Hydro | 750 | 2025-06-05 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Uhl-III Hydro Power Project |  |  | Hydro | 99.99 | 2025-03-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Sindh II Hydroelectric Power Project |  |  | Hydro | 105 | 2000-06-01 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Uri I Hydroelectric Power Project |  |  | Hydro | 480 | 1997-06-01 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Uri II Hydroelectric Power Project |  |  | Hydro | 240 | 2013-09-25 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Vishnuprayag Hydroelectric Power Project |  |  | Hydro | 400 | 2006-06-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Vyasi Hydro Power Project |  |  | Hydro | 120 | 2022-06-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Narora Atomic Power Station |  |  | Nuclear | 440 | 1991-01-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Rajasthan Atomic Power Station |  |  | Nuclear | 1780 | 1981-04-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Anta Gas Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 419.33 | 1989-01-20 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Auraiya Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 663.36 | 1989-03-29 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dadri Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 829.78 | 1992-05-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dholpur Combined Cycle Power Station |  |  | Oil & Gas | 330 | 2007-03-29 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Faridabad NTPC Gas Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 431.59 | 1999-06-18 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Gama Combined Cycle Power Plant |  |  | Oil & Gas | 225 | 2016-04-25 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | I.P. Gas Turbine Power Station |  |  | Oil & Gas | 270 | 1986-05-14 | Delhi | India_Electricity_Infrastructure.xlsx
India | IN_N | Kashipur Combined Cycle Power Plant Phase I |  |  | Oil & Gas | 225 | 2016-11-20 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kashipur Combined Cycle Power Plant Phase II |  |  | Oil & Gas | 214 | 2023-06-13 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Pragati-I Combined Cycle Gas Power Station |  |  | Oil & Gas | 330.4 | 2002-03-15 | Delhi | India_Electricity_Infrastructure.xlsx
India | IN_N | Pragati-III Combined Cycle Gas Power Project |  |  | Oil & Gas | 1500 | 2010-10-24 | Delhi | India_Electricity_Infrastructure.xlsx
India | IN_N | Ramgarh Gas Thermal Power Station |  |  | Oil & Gas | 273.5 | 1994-11-15 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Ajog Small Hydro Power Plant |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Akhara Small Hydro Project |  |  | Small Hydro | 1.1 | 2010-03-25 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Aleo II Small Hydro Power Plant |  |  | Small Hydro | 4.8 | 2010-08-05 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Aleo Small Hydro Power Plant |  |  | Small Hydro | 3 | 2005-08-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Alwas Small Hydro Power Plant |  |  | Small Hydro | 2.25 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Andhra II Small Hydro Power Project |  |  | Small Hydro | 5 | 2004-07-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Andhra Small Hydro Power Plant |  |  | Small Hydro | 16.95 | 1987-06-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ani Small Hydro Power Project |  |  | Small Hydro | 5 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Anoopgarh Phase I Mini Hydel Station |  |  | Small Hydro | 4.5 | 1987-09-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Anoopgarh Phase II Mini Hydel Station |  |  | Small Hydro | 4.5 | 1987-12-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Awa Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2000-05-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Babail Small Hydro Power Station |  |  | Small Hydro | 3 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Babbanpur Small Hydro Project |  |  | Small Hydro | 1.25 | 2004-07-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Bachham Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Badiyakot Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Bagar Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Bagipul Small Hydro Power Plant |  |  | Small Hydro | 1 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bagrood Small Hydro Power Project |  |  | Small Hydro | 0.24 | 2013-07-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balh Padhar Small Hydro Power Project |  |  | Small Hydro | 4 | 2008-03-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balij Ka Nallah-II Small Hydro Power Project |  |  | Small Hydro | 3.5 | 2002-10-24 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balij Ka Nallah-III Small Hydro Power Project |  |  | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balij ka Nala Small Hydro Power Project |  |  | Small Hydro | 3.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Baloot Fozal Small Hydro Power Plant |  |  | Small Hydro | 4.6 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Balsio Small Hydro Power Project |  |  | Small Hydro | 5 | 2011-02-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Baltikulan Small Hydro Project |  |  | Small Hydro | 5 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Baner II Small Hydro Power Plant |  |  | Small Hydro | 6 | 2001-10-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Baner III Small Hydro Power Plant |  |  | Small Hydro | 5 | 2005-11-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Baner Sangam Small Hydro Power Project |  |  | Small Hydro | 5 | 2016-06-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Baner Small Hydro Power Plant |  |  | Small Hydro | 12 | 1996-06-18 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bank Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Baragaon Small Hydro Power Project |  |  | Small Hydro | 24 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Baragran Small Hydro Power Project |  |  | Small Hydro | 4.9 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Barewal & Jhammal Combined Hydro Project |  |  | Small Hydro | 0.9 | 2010-06-12 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Barseu Small Hydro Power Plant |  |  | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Barthi Small Hydro Power Plant |  |  | Small Hydro | 1 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bazgo Small Hydro Project |  |  | Small Hydro | 0.3 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Beas Small Hydro Power Project |  |  | Small Hydro | 2.25 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Behna-I Small Hydro Power Project |  |  | Small Hydro | 5 | 2006-07-25 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Belij Small Hydro Power Project |  |  | Small Hydro | 5 | 2007-06-14 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Belka Small Hydro Power Station |  |  | Small Hydro | 3 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhaba Augmentation Hydro Electric Project |  |  | Small Hydro | 4.5 | 2011-07-09 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhaderwah Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhanubhura Small Hydro Project |  |  | Small Hydro | 1.3 | 2003-04-26 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhilganga Hydro Power Project |  |  | Small Hydro | 24 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhola Small Hydro Power Station |  |  | Small Hydro | 2.7 | 1928-12-01 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bhujal Small Hydro Power Plant |  |  | Small Hydro | 1 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Bibiwala Small Hydro Project |  |  | Small Hydro | 0.4 | 2016-04-11 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Binwa Parai Small Hydro Power Plant |  |  | Small Hydro | 5 | 2007-06-07 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Binwa Small Hydro Power Plant |  |  | Small Hydro | 6 | 1984-06-06 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Binwa Small Hydro Power Project |  |  | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Binwa-IV Small Hydro Power Project |  |  | Small Hydro | 4 | 2011-12-13 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Birahi Ganga Hydro Power Project |  |  | Small Hydro | 7.2 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Birsalpur Mini Hydel Station |  |  | Small Hydro | 0.54 | 1998-10-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Borbalda Micro Hydel Project |  |  | Small Hydro | 0.03 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Bowani Small Hydro Project |  |  | Small Hydro | 1 | 2002-08-22 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Bowani Small Hydro Project 2 |  |  | Small Hydro | 1.2 | 2012-03-20 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Brahal Small Hydro Power Project |  |  | Small Hydro | 4 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Braham Ganga Small Hydro Power Project |  |  | Small Hydro | 5 | 2002-08-02 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Brahl Top Small Hydro Power Plant |  |  | Small Hydro | 5 | 2012-04-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Brua Hydroelectric Project |  |  | Small Hydro | 9 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | CLC India (Spentex Industries Ltd.) Small Hydro Project |  |  | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chaba Small Hydro Power Project |  |  | Small Hydro | 1.75 | 1919-06-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chachyot Small Hydro Power Project |  |  | Small Hydro | 3.5 | 2008-02-25 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chaini Tepa Small Hydro Power Plant |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chaksi Small Hydro Power Plant |  |  | Small Hydro | 2.4 | 2012-06-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chamoli Hydro Power Project |  |  | Small Hydro | 5 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Chandigarh Distillers and Bottlers Ltd. (CDB Group) Plant 1 |  |  | Small Hydro | 9 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chandigarh Distillers and Bottlers Ltd. (CDB Group) Plant 2 |  |  | Small Hydro | 4 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chandni Small Hydro Power Project |  |  | Small Hydro | 3 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Channuwal Small Hydro Project |  |  | Small Hydro | 0.9 | 2009-09-30 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Charanwala Mini Hydel Station |  |  | Small Hydro | 1.2 | 1994-03-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Chenani -III Small Hydro Project |  |  | Small Hydro | 7.5 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Chenani-I Small Hydro Project |  |  | Small Hydro | 23.3 | 1971-12-01 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Chenani-II Small Hydro Project |  |  | Small Hydro | 2 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Chho Tundah Small Hydro Power Plant |  |  | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chhoned-I Small Hydro Power Plant |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chiludgad Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Ching Small Hydro Power Project |  |  | Small Hydro | 1 | 2000-05-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chirchind Small Hydro Power Project |  |  | Small Hydro | 5 | 2001-05-16 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Chitraura Small Hydro Power Station |  |  | Small Hydro | 3 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Choting Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Choudhary Power Projects |  |  | Small Hydro | 15 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Chupki Small Hydro Project |  |  | Small Hydro | 1.5 | 1999-11-12 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Dadahur & Chakbhai Combined Hydro Project |  |  | Small Hydro | 2 | 2004-11-18 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Dadupur Mini Hydel Scheme |  |  | Small Hydro | 6 | 2010-12-01 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Dah Small Hydro Project |  |  | Small Hydro | 6 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dalla Small Hydro Project |  |  | Small Hydro | 1 | 1999-05-24 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Daredi Small Hydro Power Plant |  |  | Small Hydro | 4 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Daudhar Small Hydro Project |  |  | Small Hydro | 1.5 | Pre-2000 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Daudhar Small Hydro Project |  |  | Small Hydro | 1.5 | 1987-07-16 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Dawaitwal, Issewal & Kailpur Combined Small Hydro Project |  |  | Small Hydro | 0.9 | 2011-07-15 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Dehar II Small Hydro Power Project |  |  | Small Hydro | 1.5 | 2005-12-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dehar Small Hydro Power Project |  |  | Small Hydro | 5 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhugli Small Hydro Power Plant |  |  | Small Hydro | 3.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dikleri Small Hydo Power Project |  |  | Small Hydro | 2 | 2009-01-12 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dogtigaun Micro Hydel Project |  |  | Small Hydro | 0.02 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Dolowal Small Hydro Project |  |  | Small Hydro | 1.4 | 2003-04-26 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Drinidhar Small Hydro Power Plant |  |  | Small Hydro | 5 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dug Small Hydro Power Plant |  |  | Small Hydro | 1.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dukrund Small Hydro Power Plant |  |  | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dukrund-I Small Hydro Power Plant |  |  | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dunali Small Hydro Power Project |  |  | Small Hydro | 5 | 2002-11-18 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dunao Small Hydel Project |  |  | Small Hydro | 1.5 | 2017-07-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Durghed Small Hydro Power Plant |  |  | Small Hydro | 1.1 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | GTV Engineering Ltd. Small Hydro Project |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gaj II Small Hydro Power Plant |  |  | Small Hydro | 1.5 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gaj Small Hydro Power Plant |  |  | Small Hydro | 10.5 | 1996-06-18 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gaj Top Small Hydro Power Plant |  |  | Small Hydro | 3.8 | 2011-06-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gaj-III Small Hydro Power Project |  |  | Small Hydro | 3.6 | 2011-04-07 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Galogi Hydel Power Station |  |  | Small Hydro | 3 | 1912-11-19 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Gamshali Bampa Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Ganderbal Small Hydro Project |  |  | Small Hydro | 15 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Gangotri Kedarganga Micro Hydel Project |  |  | Small Hydro | 0.15 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Gangotri Rudragara Micro Hydel Project |  |  | Small Hydro | 0.15 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Gehra Small Hydro Power Plant |  |  | Small Hydro | 2 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghanvi II Small Hydro Power Plant |  |  | Small Hydro | 10 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghanvi Small Hydro Power Plant |  |  | Small Hydro | 22.5 | 2000-12-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gharwan Small Hydro Power Plant |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghator Top Small Hydro Power Plant |  |  | Small Hydro | 4.98 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghator-I Small Hydro Power Plant |  |  | Small Hydro | 2.2 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gholian Small Hydro Project |  |  | Small Hydro | 0.8 | 2009-10-04 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Gogina - II Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Gogina Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Gogripur Hydro Power Project |  |  | Small Hydro | 2 | 2010-08-13 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Gondar Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant |  |  | Small Hydro | 12 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 10 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 11 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 12 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 13 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 14 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 2 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 3 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 4 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 5 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 6 |  |  | Small Hydro | 24 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 7 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 8 |  |  | Small Hydro | 14 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Greenko Group Small Hydro Power Plant 9 |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gulari Micro Hydel Project |  |  | Small Hydro | 0.02 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Gumma Small Hydro Power Plant |  |  | Small Hydro | 3 | 2000-07-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gumma-II Small Hydro Power Project |  |  | Small Hydro | 2.5 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gunshola Hydro Power Generations Project |  |  | Small Hydro | 3 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Gurahan Small Hydro Power Project |  |  | Small Hydro | 1.5 | 2003-05-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Gurdittiwala Small Hydro Project |  |  | Small Hydro | 2 | 2018-03-08 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Haftal Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Hamal Small Hydro Power Project |  |  | Small Hydro | 2 | 2006-09-06 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Hanu Small Hydro Project |  |  | Small Hydro | 9 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Haripur Nallah Small Hydro Power Project |  |  | Small Hydro | 3 | 2004-07-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Holi II Small Hydro Power Plant |  |  | Small Hydro | 7 | 2010-10-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Holi Small Hydro Power Plant |  |  | Small Hydro | 3 | 2004-06-26 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Hul-II Small Hydro Power Plant |  |  | Small Hydro | 3.4 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Hunder Small Hydo Project |  |  | Small Hydro | 0.4 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Hurla Small Hydro Power Project |  |  | Small Hydro | 3 | 2003-08-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Hysrund Small Hydro Power Project |  |  | Small Hydro | 3.3 | 2012-02-24 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ichoo Small Hydro Project |  |  | Small Hydro | 5 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Igo-Marcellong Small Hydro Project |  |  | Small Hydro | 3 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Iku II Small Hydro Power Plant |  |  | Small Hydro | 5 | 2009-11-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Iku Khad Small Hydro Power Plant |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Iqbal Small Hydro Project |  |  | Small Hydro | 3.75 | 1956-12-01 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Iqu II Small Hydro Power Plant |  |  | Small Hydro | 5 | 2005-11-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Iqu Small Hydro Power Plant |  |  | Small Hydro | 4.5 | 2000-05-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Istargad Micro Hydel Project |  |  | Small Hydro | 0.2 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Jabbal Small Hydro Power Project |  |  | Small Hydro | 2 | 2006-09-06 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Jagera Small Hydro Project |  |  | Small Hydro | 1 | 2003-07-31 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Jail Small Hydro Power Project |  |  | Small Hydro | 1 | 2013-08-14 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Jakhana Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Janki Chutti Micro Hydel Project |  |  | Small Hydro | 0.2 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Jirah Small Hydro Power Project |  |  | Small Hydro | 4 | 2006-07-25 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Jiwa Kothari Small Hydro Power Project |  |  | Small Hydro | 1 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Jogni-II Small Hydro Power Project |  |  | Small Hydro | 5 | 2012-08-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Joiner Small Hydro Power Plant |  |  | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Joli Small Hydro Power Plant |  |  | Small Hydro | 1.4 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Jugthana Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kaachrang Small Hydro Power Project |  |  | Small Hydro | 3 | 2011-05-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kachela Small Hydro Power Plant |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kakroi Micro Hydro Power Station |  |  | Small Hydro | 0.3 | 1987-12-01 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Kalath Small Hydro Power Project |  |  | Small Hydro | 1.2 | 2010-08-05 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kalhel Chatri Small Hydro Power Plant |  |  | Small Hydro | 2.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kaliganga-I Small Hydro Project |  |  | Small Hydro | 4 | 2020-07-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kalm Small Hydro Power Project |  |  | Small Hydro | 2 | 2011-11-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kanganwal Small Hydro Project |  |  | Small Hydro | 1.3 | 2001-08-28 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Kanolgad Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kanyali kot Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Karmi - I Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Karmi - II Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Karmi - III Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Karnah Small Hydro Project |  |  | Small Hydro | 2 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Karnuwasharam Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kartaul Small Hydro Power Project |  |  | Small Hydro | 2.4 | 2006-07-25 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kedarnath - I Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kedarnath - II Micro Hydel Project |  |  | Small Hydro | 0.2 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kesta Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2011-05-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Khalara Small Hydro Power Project |  |  | Small Hydro | 2.5 | 2012-05-18 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Khanpur Small Hydro Project |  |  | Small Hydro | 1.1 | 2010-04-24 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Khanyara Small Hydro Power Project |  |  | Small Hydro | 2 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Khapugad Micro Hydel Project |  |  | Small Hydro | 0.04 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Khari Hydro Electric Project |  |  | Small Hydro | 3.75 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Khatra Small Hydro Project |  |  | Small Hydro | 1 | 2001-01-23 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Khauli Small Hydro Power Plant |  |  | Small Hydro | 12 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Khukni Small Hydro Power Station |  |  | Small Hydro | 1.4 | 2011-08-31 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Killa & Burga Combined Hydro Project |  |  | Small Hydro | 1.75 | 2005-11-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Killar Small Hydro Power Plant |  |  | Small Hydro | 0.3 | 1995-12-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Killi Behl Small Hydro Power Plant |  |  | Small Hydro | 7.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kiunr Small Hydro Power Project |  |  | Small Hydro | 5 | 2012-02-09 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kotagad Small Hydro Power Project |  |  | Small Hydro | 3.5 | 2012-11-07 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kotlu Small Hydro Power Project |  |  | Small Hydro | 1.8 | 2003-05-14 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kunjar Small Hydro Project |  |  | Small Hydro | 2 | 2017-06-23 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Kunwari Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Kurhed Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2004-07-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kurpan Small Hydro Power Project |  |  | Small Hydro | 5 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kurtha Small Hydro Power Project |  |  | Small Hydro | 5 | 2015-01-06 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kuwarsi Small Hydro Power Project |  |  | Small Hydro | 5 | 2008-11-14 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Lambagar Micro Hydel Project |  |  | Small Hydro | 0.2 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Lamchula Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Lathi Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Lehrun Hydro Power Project |  |  | Small Hydro | 3 | 2010-07-23 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Leond Small Hydro Power Project |  |  | Small Hydro | 2 | 2012-02-15 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Liti - I Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Liti - II Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Lohgarh & Maholi Combined Hydro Project |  |  | Small Hydro | 2 | 2005-10-10 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Lower Aleo Small Hydro Power Project |  |  | Small Hydro | 2.5 | 2010-11-11 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Lower Baijnath Kuhl Small Hydro Power Project |  |  | Small Hydro | 1 | 2000-12-27 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Luni Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2000-05-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Luni Small Hydro Power Project |  |  | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Luni-II Small Hydro Power Project |  |  | Small Hydro | 5 | 2005-12-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Luni-III Small Hydro Power Project |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Magpie Hydel Construction Operation Industries Pvt. Ltd. Small Hydro Project 1 |  |  | Small Hydro | 10 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Magpie Hydel Construction Operation Industries Pvt. Ltd. Small Hydro Project 2 |  |  | Small Hydro | 10 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Malana Top Small Hydro Power Project |  |  | Small Hydro | 5 | 2012-01-04 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Manal Small Hydro Power Project |  |  | Small Hydro | 3 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mangalam Energy Development Company Pvt. Ltd. Small Hydro Project |  |  | Small Hydro | 3 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Manglad Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2007-07-24 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Mangrol Mini Hydel Power Station |  |  | Small Hydro | 2 | 1992-11-28 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Mangrol Mini Hydel Power Station |  |  | Small Hydro | 4 | 1992-11-29 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Manihar Small Hydro Power Project |  |  | Small Hydro | 2 | 2011-07-11 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Manjhal Small Hydro Power Project |  |  | Small Hydro | 1 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Manuni Small Hydro Electric Project |  |  | Small Hydro | 3.5 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Manuni-II Small Hydro Power Project |  |  | Small Hydro | 4.8 | 2010-03-06 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Marhi Mini Hydel Power Project |  |  | Small Hydro | 5 | 2004-07-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Marpachoo Small Hydro Project |  |  | Small Hydro | 0.75 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Masli Small Hydro Power Plant |  |  | Small Hydro | 5 | 2002-10-28 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Maujhi II Small Hydro Electric Project |  |  | Small Hydro | 5 | 2007-07-25 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Maujhi Small Hydro Electric Project |  |  | Small Hydro | 4.5 | 2001-05-16 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Milkhet Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Mohammadpur Small Hydro Power Station |  |  | Small Hydro | 9.3 | 1952-12-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Mukerian Hydel Channel II |  |  | Small Hydro | 18 | 2017-05-19 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Mussapur Small Hydro Power Station |  |  | Small Hydro | 1.4 | 2011-06-17 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Nadampur Small Hydro Project |  |  | Small Hydro | 0.8 | 1985-12-14 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Nakkian Super Passage Hydro Project |  |  | Small Hydro | 0.3 | 2020-02-19 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Namik Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Napalchu Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Narangwal Small Hydro Project |  |  | Small Hydro | 1.5 | 1999-06-07 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Neogal II Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2000-05-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Neogal Small Hydro Power Project |  |  | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Nidampur Small Hydro Project |  |  | Small Hydro | 0.8 | Pre-2000 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Nirgajani Small Hydro Power Station |  |  | Small Hydro | 5 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Niti Micro Hydel Project |  |  | Small Hydro | 0.03 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Nogli Last Small Hydro Power Project |  |  | Small Hydro | 3 | 2017-04-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Nogli Stage I Small Hydro Power Project |  |  | Small Hydro | 5 | 1969-12-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | P & R Group Small Hydro Project |  |  | Small Hydro | 7.5 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Pahalgam Mini Hydel Project |  |  | Small Hydro | 4.5 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Pallor Small Hydro Power Project |  |  | Small Hydro | 3 | 2002-09-18 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Pallor-II Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Pangi Small Hydro Power Project |  |  | Small Hydro | 3 | 2004-07-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Panwi Small Hydro Power Project |  |  | Small Hydro | 4 | 2001-08-03 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Pathri Small Hydro Power Station |  |  | Small Hydro | 11.04 | 1956-01-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Patikari Power Small Hydro Power Plant |  |  | Small Hydro | 16 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Phoola Small Hydro Project |  |  | Small Hydro | 0.6 | 2014-06-21 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Pugal Phase I Mini Hydel Station |  |  | Small Hydro | 1.5 | 1994-10-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Pugal Phase II Mini Hydel Station |  |  | Small Hydro | 0.65 | 1992-07-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | RD Combined Hydro Project 1 |  |  | Small Hydro | 6 | 2016-10-23 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | RD Combined Hydro Project 2 |  |  | Small Hydro | 3.8 | 2017-01-11 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Raajratna Energy Holdings Pvt. Ltd. (REHPL) Hydro Project |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Rakchad Small Hydro Electric Project |  |  | Small Hydro | 5 | 2001-08-03 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ramgad Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Raowal & Bangsipura Combined Hydro Project |  |  | Small Hydro | 0.85 | 2011-08-29 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Raskat Mini Hydel Power Project |  |  | Small Hydro | 0.8 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ratmoli Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Rayil Small Hydro Project |  |  | Small Hydro | 2 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Right Main Canal Mahi Mini Hydel Station Phase I |  |  | Small Hydro | 0.8 | 1993-11-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Right Main Canal Mahi Mini Hydel Station Phase II |  |  | Small Hydro | 0.17 | 1991-03-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Rohti Small Hydro Project |  |  | Small Hydro | 0.8 | 1989-03-21 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Rongtong Small Hydro Power Project |  |  | Small Hydro | 2 | 1986-06-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Ropar Small Hydro Project |  |  | Small Hydro | 1.7 | 2007-05-27 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Rotan Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Rukti II Small Hydro Power Project |  |  | Small Hydro | 5 | 2009-03-09 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Rukti Small Hydro Power Project |  |  | Small Hydro | 1.5 | 1980-12-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sahoke & Harigarh Combined Hydro Project |  |  | Small Hydro | 1.2 | 2006-11-01 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Sahu Small Hydro Power Project |  |  | Small Hydro | 5 | 2003-05-14 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Saikothi Small Hydro Power Project |  |  | Small Hydro | 15 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sainj Small Hydro Power Project |  |  | Small Hydro | 5 | 2004-07-26 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sal-I Small Hydro Power Project |  |  | Small Hydro | 2 | 2000-06-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sal-II Small Hydro Power Project |  |  | Small Hydro | 3 | 2007-09-11 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Salag Small Hydro Power Project |  |  | Small Hydro | 0.15 | 2000-05-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Salar Small Hydro Project |  |  | Small Hydro | 1.5 | 2003-04-26 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Salawa Small Hydro Power Station |  |  | Small Hydro | 3 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sanjak Small Hydro Project |  |  | Small Hydro | 1.26 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sarbari III Small Hydro Power Plant |  |  | Small Hydro | 2 | 2013-08-27 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sarbari Small Hydro Power Plant |  |  | Small Hydro | 4.5 | 2003-05-14 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sarda Energy & Minerals Ltd. Small Hydro Project |  |  | Small Hydro | 4.8 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Sarma Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Sateshwar Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Sechi Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2001-08-03 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sechi-II Small Hydro Power Project |  |  | Small Hydro | 4.5 | 2008-03-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sela Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Serai Small Hydro Power Project |  |  | Small Hydro | 2 | 2013-10-17 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sewa III Small Hydo Project |  |  | Small Hydro | 9 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Shamshar Small Hydro Power Project |  |  | Small Hydro | 1.5 | 2002-11-02 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shansha Small Hydro Power Project |  |  | Small Hydro | 4 | 2013-07-19 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sharan Small Hydro Power Project |  |  | Small Hydro | 2.6 | 2002-05-25 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shatul Small Hydro Power Project |  |  | Small Hydro | 4.75 | 2008-04-28 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shaung Small Hydro Power Project |  |  | Small Hydro | 3 | 2016-04-15 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sheetla Small Hydro Power Station |  |  | Small Hydro | 3.6 | Pre-2000 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shimla Small Hydro Power Project |  |  | Small Hydro | 5 | 2011-06-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Shyang Mini Hydel Power Project |  |  | Small Hydro | 3 | 2009-11-05 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sidhana & Baloke Combined Hydro Project |  |  | Small Hydro | 1.2 | 2007-10-25 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Sidhwan Bet & Mansian Combined Hydro Project |  |  | Small Hydro | 0.5 | 2010-09-22 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Sidhwan Hydro Power Project |  |  | Small Hydro | 0.7 | 2014-05-11 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Singrauli Small Hydel Power Plant |  |  | Small Hydro | 8 | 2018-03-05 | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Siunr Small Hydro Power Project |  |  | Small Hydro | 1.5 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sodhi Brothers Hydro Power Project |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Solang Small Hydro Power Plant |  |  | Small Hydro | 1 | 2000-08-10 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Soldan Small Hydro Power Project |  |  | Small Hydro | 5 | 2012-10-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Somani Group Small Hydro Plant 1 |  |  | Small Hydro | 4.5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Somani Group Small Hydro Plant 2 |  |  | Small Hydro | 5.4 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sorag Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Sravanthi Group Small Hydro Power Plant |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Stakna Small Hydro Project |  |  | Small Hydro | 4 | Pre-2000 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sudhar Small Hydro Project |  |  | Small Hydro | 1.4 | 2010-05-03 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Suil-I Small Hydro Power Project |  |  | Small Hydro | 5 | 2006-09-06 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Suman Sarwari Small Hydro Power Plant |  |  | Small Hydro | 5 | 2002-08-28 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sumoor Small Hydro Project |  |  | Small Hydro | 0.1 | 1993-12-01 | Ladakh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunehar Small Hydro Power Plant |  |  | Small Hydro | 5 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sup Small Hydro Power Project |  |  | Small Hydro | 1 | 2001-09-19 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Surah Small Hydro Power Project |  |  | Small Hydro | 1.5 | 2008-10-03 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Suratgarh Mini Hydel Power Station |  |  | Small Hydro | 4 | 1992-02-01 | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Swad Small Hydro Power Project |  |  | Small Hydro | 5 | 2008-10-03 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Swaddi Kalan, Khudai Chak & Bharowal Combined Hydro Project |  |  | Small Hydro | 0.75 | 2013-01-21 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Swati Power Hydro Project |  |  | Small Hydro | 21.5 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Talewal Small Hydro Project |  |  | Small Hydro | 0.6 | 2019-12-31 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Tangling Mini Hydel Power Project |  |  | Small Hydro | 5 | 2010-12-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Taraila Small Hydro Power Project |  |  | Small Hydro | 5 | 2003-05-14 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Taraila-II Small Hydro Power Project |  |  | Small Hydro | 5 | 2005-12-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Taraila-III Small Hydro Power Project |  |  | Small Hydro | 5 | 2007-12-31 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Terkiana Head Works Small Hydro Project |  |  | Small Hydro | 0.65 | 2010-08-31 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Thirot Small Hydro Power Plant |  |  | Small Hydro | 4.5 | 1995-12-01 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Thuhi Small Hydro Project |  |  | Small Hydro | 0.8 | Pre-2000 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Thuhi Small Hydro Project |  |  | Small Hydro | 0.8 | 1989-03-14 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Tibri & Babehali Combined Hydro Project |  |  | Small Hydro | 2.7 | 2006-10-06 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Timbi Small Hydro Power Project |  |  | Small Hydro | 3 | 2000-03-30 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Titang Small Hydro Power Project |  |  | Small Hydro | 0.9 | 2000-08-17 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Toli Micro Hydel Project |  |  | Small Hydro | 0.1 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Toss Small Hydro Power Project |  |  | Small Hydro | 10 | 2004-07-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Tugal Small Hydro Project |  |  | Small Hydro | 1.5 | 1999-09-08 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Tugalwala Small Hydro Project |  |  | Small Hydro | 0.85 | 2019-05-29 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Tulang Small Hydro Power Project |  |  | Small Hydro | 3 | 2004-07-20 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | UREDA Small Hydro Project |  |  | Small Hydro | 22.5 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Ubharah Small Hydro Power Project |  |  | Small Hydro | 2.4 | 2005-06-08 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Udhanwal Small Hydro Project |  |  | Small Hydro | 0.65 | 2018-03-02 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Awa Small Hydro Power Project |  |  | Small Hydro | 5 | 2005-12-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Bari Doab Canal (UBDC) Stage I |  |  | Small Hydro | 45 | 1971-08-30 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Bari Doab Canal (UBDC) Stage II |  |  | Small Hydro | 46.35 | 1989-08-06 | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Khauli Small Hydro Power Plant |  |  | Small Hydro | 5 | 2005-11-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Sindh I Small Hydro Project |  |  | Small Hydro | 22.6 | Pre-2000 | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Upper Taraila Small Hydro Power Project |  |  | Small Hydro | 5 | 2005-12-22 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Urgam Small Hydro Project |  |  | Small Hydro | 3 | 1997-12-01 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttar Bharat Hydro Power Project |  |  | Small Hydro | 25.5 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Uttarkashi Micro Hydel Project |  |  | Small Hydro | 0.02 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Wan Micro Hydel Project |  |  | Small Hydro | 0.05 | Pre-2000 | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Wanger Homte Hydro Electric Project |  |  | Small Hydro | 24.6 | Pre-2000 | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Western Yamuna Canal Hydro Power Project Power House A |  |  | Small Hydro | 16 | 1986-05-29 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Western Yamuna Canal Hydro Power Project Power House B |  |  | Small Hydro | 16 | 1987-05-15 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Western Yamuna Canal Hydro Power Project Power House C |  |  | Small Hydro | 16 | 1989-03-27 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Western Yamuna Canal Hydro Power Project Power House D |  |  | Small Hydro | 14.4 | 2004-04-16 | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Others (districts not specified) [Biomass & bagasse based cogen.] Dadra and Naga |  |  | Bio Power | 3.75 | Pre-2000 | Dadra and Nagar Haveli an | India_Electricity_Infrastructure.xlsx
India | IN_S | Adilaxmi Industries Andhra Pradesh East Godavari 0.41 2014-04-01 |  |  | Bio Power | 0.41 | 2014-04-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Agri Gold Projects Ltd Andhra Pradesh Prakasam 6 2003-06-19 |  |  | Bio Power | 6 | 2003-06-19 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Ambika Sugars (Previously M/s. SREL) Tamil Nadu Cuddalore 40 |  |  | Bio Power | 40 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Ananda Enterprises (India) Pvt Ltd Andhra Pradesh West Godavari 2 2014-04-01 |  |  | Bio Power | 2 | 2014-04-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Andhra Sugars Ltd. Andhra Pradesh West Godavari 7 1999-01-21 |  |  | Bio Power | 7 | 1999-01-21 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Arashi Hi-Tech Bio-Power Ltd. Tamil Nadu Coimbatore 1.6 |  |  | Bio Power | 1.6 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Aroma Biotech Pvt Ltd Andhra Pradesh West Godavari 2.2 2012-05-12 |  |  | Bio Power | 2.2 | 2012-05-12 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Arunachala Sugars Ltd. Tamil Nadu Tiruvannamalai 19 |  |  | Bio Power | 19 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Astro Energy and Bio Systems Ltd. Tamil Nadu Madurai 10 |  |  | Bio Power | 10 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Athani Farmers Sugar factory Ltd Karnataka Belagavi 24 01.01.2012 |  |  | Bio Power | 24 | 2012-01-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Auro Energy Ltd. Tamil Nadu Thanjavur 16 |  |  | Bio Power | 16 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Aurobindo Agro Energy Pvt. Ltd. Tamil Nadu Sivaganga 15 |  |  | Bio Power | 15 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Auromira Bio Power India (P) Ltd Tamil Nadu Tirunelveli 15 |  |  | Bio Power | 15 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Balaji Agro Oils Ltd Andhra Pradesh Krishna 4.5 2003-06-01 |  |  | Bio Power | 4.5 | 2003-06-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Balaji Boiled & Raw Rice Mill Andhra Pradesh East Godavari 0.89 2016-06-01 |  |  | Bio Power | 0.89 | 2016-06-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Balaji Sugars and Chemicals Pvt Ltd Karnataka Vijayapura 18 |  |  | Bio Power | 18 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bannari Amman Sugars Ltd. Karnataka Chamarajanagar 20 |  |  | Bio Power | 20 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bannari Amman Sugars Ltd. Karnataka Mysuru 36.3 10.03.2004 |  |  | Bio Power | 36.3 | 2004-10-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bannari Amman Sugars Ltd. Tamil Nadu Erode 20 |  |  | Bio Power | 20 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Bannari Amman Sugars and Chemicals Ltd. Tamil Nadu Tiruvannamalai 28.8 |  |  | Bio Power | 28.8 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhagyanagar Solvents & Extractions Pvt. Ltd. Karnataka Raichur 7.5 01.09.2003 |  |  | Bio Power | 7.5 | 2003-01-09 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bilagi Sugar Mill Ltd Karnataka Bagalkote 8 01.12.2009 |  |  | Bio Power | 8 | 2009-01-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bollineni Castings & Steels Ltd Andhra Pradesh Sri Potti Sriramulu Nellore 6 200 |  |  | Bio Power | 6 | 2003-10-07 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Buddha Deva Power Ltd Telangana Nalgonda 6 |  |  | Bio Power | 6 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | C.M.D.A., Koyambedu Veg. Market Bio-metharation plant Tamil Nadu Chennai 0.25 |  |  | Bio Power | 0.25 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Chamundeshwari Sugars Ltd Karnataka Mandya 26 02.04.2008 |  |  | Bio Power | 26 | 2008-02-04 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Cheyyar Co.op Sugar Mills Tamil Nadu Tiruvannamalai 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Chitra Bio Energy Ltd. Tamil Nadu Pudukkottai 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Chodavaram Co-op. Sugars Ltd Andhra Pradesh Visakhapatnam 14 2003-04-06 |  |  | Bio Power | 14 | 2003-04-06 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Clarion Power Corp.Ltd Andhra Pradesh Prakasam 12 2004-01-23 |  |  | Bio Power | 12 | 2004-01-23 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Core Green Sugar & Fuels Pvt Ltd Karnataka Yadgir 24 16.10.2011 |  |  | Bio Power | 24 | 2011-10-16 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Coromandel Sugars Ltd Karnataka Mandya 12 06.02.2000 |  |  | Bio Power | 12 | 2000-06-02 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Davanagere Sugar Co. Ltd Karnataka Davangere 24 24.03.2004 |  |  | Bio Power | 24 | 2004-03-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Delta Paper Mills Ltd Andhra Pradesh West Godavari 9.9 2007-12-01 |  |  | Bio Power | 9.9 | 2007-12-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Dhanalakshmi Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 8 12.03.2010 |  |  | Bio Power | 8 | 2010-12-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Dhanalakshmi Srinivasan Sugars Pvt Ltd. Tamil Nadu Perambalur 25 |  |  | Bio Power | 25 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Dharani Sugars & Chemical Ltd. Tamil Nadu Tiruvannamalai 15 |  |  | Bio Power | 15 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Dharani Sugars & Chemical Ltd. Tamil Nadu Viluppuram 22 |  |  | Bio Power | 22 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Dharwad Bio Energy Pvt. Ltd. Karnataka Dharwad 10 31.01.2013 |  |  | Bio Power | 10 | 2013-01-31 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Doodhganga Krishna Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 24 25.0 |  |  | Bio Power | 24 | 2004-03-25 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Karnataka Bagalkote 16 01.06.2008 |  |  | Bio Power | 16 | 2008-01-06 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Tamil Nadu Cuddalore 24.5 |  |  | Bio Power | 24.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Tamil Nadu Karur 22 |  |  | Bio Power | 22 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Tamil Nadu Pudukkottai 18 |  |  | Bio Power | 18 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | EID Parry India Ltd. Tamil Nadu Tiruchirappalli 18 |  |  | Bio Power | 18 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | ETA Power Gen.Pvt.Ltd. Tamil Nadu Virudhunagar 10 |  |  | Bio Power | 10 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Empee Distilleries (Pvt) Ltd. Tamil Nadu Pudukkottai 10 |  |  | Bio Power | 10 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Empee Power company (I) Ltd Andhra Pradesh Sri Potti Sriramulu Nellore 20 2009-1 |  |  | Bio Power | 20 | 2009-12-02 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Empee Sugars & Chemicals Ltd. Tamil Nadu Tirunelveli 50 |  |  | Bio Power | 50 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Falcon Tyres Ltd. Karnataka Mysuru 6 01.03.2009 |  |  | Bio Power | 6 | 2009-01-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | G.K. Bio Energy Pvt. Ltd. Tamil Nadu Erode 1.5 |  |  | Bio Power | 1.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | GEM Sugars Ltd Karnataka Bagalkote 16.5 31.10.2002 |  |  | Bio Power | 16.5 | 2002-10-31 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | GMR Industries Ltd. Andhra Pradesh Srikakulam 16 2001-08-15 |  |  | Bio Power | 16 | 2001-08-15 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | GSR Sugars Pvt Ltd Telangana Nizamabad 16.1 16.05.2007 |  |  | Bio Power | 16.1 | 2007-05-16 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Ganapati Sugars Industries Ltd Telangana Sangareddy 15 1.01.2003 |  |  | Bio Power | 15 | 2003-01-01 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Gayatri Agro Industrial Power Ltd Telangana Nalgonda 6 28.2.2001 |  |  | Bio Power | 6 | 2001-02-28 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Gayatri Sugar Ltd Telangana Nizamabad 9 23.05.2001 |  |  | Bio Power | 9 | 2001-05-23 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Global Power Tech. Equipments Pvt.Ltd. Tamil Nadu Tiruvannamalai 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Godavari Bio Refineries Ltd Karnataka Bagalkote 21.6 07.01.2011 |  |  | Bio Power | 21.6 | 2011-07-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Godavari Bio Refineries Ltd Karnataka Bagalkote 24 01.09.2002 |  |  | Bio Power | 24 | 2002-01-09 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Gokak SC & ST Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 14 24.12.200 |  |  | Bio Power | 14 | 2009-12-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Gowthami Bio Energies Ltd Telangana Khammam 6 23.7.2001 |  |  | Bio Power | 6 | 2001-07-23 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Gowthami Solvent Oil Ltd Andhra Pradesh West Godavari 2.75 1996-03-31 |  |  | Bio Power | 2.75 | 1996-03-31 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Greenko Energies Pvt Ltd Andhra Pradesh Guntur 6 2002-07-19 |  |  | Bio Power | 6 | 2002-07-19 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Greenko Energies Pvt Ltd Andhra Pradesh YSR Kadapa 6 |  |  | Bio Power | 6 | Pre-2000 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Gujarat Ambuja Exports Ltd (Biomass based Cogen) Karnataka Haveri 2.44 21.01.201 |  |  | Bio Power | 2.44 | 2013-01-21 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Gujarat Ambuja Exports Ltd Karnataka Haveri 2.85 01.04.2014 |  |  | Bio Power | 2.85 | 2014-01-04 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | HCL Agro Power Ltd Andhra Pradesh Krishna 6 2000-10-24 |  |  | Bio Power | 6 | 2000-10-24 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Hassan Biomass Power Co. Pvt. Ltd. Karnataka Hassan 8 17.03.2003 |  |  | Bio Power | 8 | 2003-03-17 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Haveri Bio Energy Pvt. Ltd. Karnataka Haveri 10 01.04.2014 |  |  | Bio Power | 10 | 2014-01-04 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hiranyakeshi Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 26 15.11.2008 |  |  | Bio Power | 26 | 2008-11-15 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hiranyakeshi Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 26 27.08.2011 |  |  | Bio Power | 26 | 2011-08-27 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | IOT Mabagas Ltd. Tamil Nadu N.A. 2 |  |  | Bio Power | 2 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Ind-Barath Energies Ltd Telangana Nalgonda 6 6.10.2000 |  |  | Bio Power | 6 | 2000-06-10 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Indian Cane Power Ltd Karnataka Bagalkote 28 17.05.2008 |  |  | Bio Power | 28 | 2008-05-17 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Indian Sugar Manufacturing Co. Ltd Karnataka Vijayapura 19.5 24.02.2013 |  |  | Bio Power | 19.5 | 2013-02-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Indra Power Energies Ltd. Karnataka Koppal 6 13.02.2004 |  |  | Bio Power | 6 | 2004-02-13 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Indur Green Power Pvt Ltd Telangana Nizamabad 6 15.2.2003 |  |  | Bio Power | 6 | 2003-02-15 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Jamakhandi Sugars Ltd Karnataka Bagalkote 12 08.02.2002 |  |  | Bio Power | 12 | 2002-08-02 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Jamakhandi Sugars Ltd Karnataka Bagalkote 30 27.02.2012 |  |  | Bio Power | 30 | 2012-02-27 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Jeypore Sugars Company Ltd (Unit II) Andhra Pradesh West Godavari 16.8 2003-10-1 |  |  | Bio Power | 16.8 | 2003-10-19 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Jeypore Sugars Company Ltd Andhra Pradesh West Godavari 12 2003-10-19 |  |  | Bio Power | 12 | 2003-10-19 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Jocil Limited Andhra Pradesh Guntur 6 2001-03-23 |  |  | Bio Power | 6 | 2001-03-23 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Jyothi Bio Energy Ltd Andhra Pradesh Prakasam 4.5 2000-11-17 |  |  | Bio Power | 4.5 | 2000-11-17 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Jyothi Bio Energy Ltd Andhra Pradesh Prakasam 6 2003-11-14 |  |  | Bio Power | 6 | 2003-11-14 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | KCP Sugar Industries & Corp.Ltd Andhra Pradesh Krishna 12 2005-12-26 |  |  | Bio Power | 12 | 2005-12-26 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | KCP Sugar Industries & Corp.Ltd Andhra Pradesh Krishna 5 2005-12-26 |  |  | Bio Power | 5 | 2005-12-26 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | KPR Sugar Mills Pvt Ltd Karnataka Vijayapura 30 23.11.2012 |  |  | Bio Power | 30 | 2012-11-23 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kakatiya Cement Sugars and Industries Ltd Telangana Khammam 15 12.04.2002 |  |  | Bio Power | 15 | 2002-12-04 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Kedarnath Sugar and Agro Chemicals Ltd Karnataka Bagalkote 18 02.03.2010 |  |  | Bio Power | 18 | 2010-02-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Koganti Power Pvt. Ltd. Karnataka Raichur 7.5 26.11.2005 |  |  | Bio Power | 7.5 | 2005-11-26 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Konark Power Ltd. Karnataka Tumakuru 73 05.05.2005 |  |  | Bio Power | 7.03 | 2005-05-05 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Koppal Green Power Ltd. Karnataka Koppal 6 01.01.2005 |  |  | Bio Power | 6 | 2005-01-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kothari Sugars & Chemicals Ltd. Tamil Nadu Perambalur 12 |  |  | Bio Power | 12 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Kothari Sugars & Chemicals Ltd. Tamil Nadu Perambalur 22 |  |  | Bio Power | 22 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Krishna Sahakari Sakkare Karkhane Niyamita Karnataka Belagavi 12 08.02.2013 |  |  | Bio Power | 12 | 2013-08-02 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Krishnaveni Sugars Ltd Andhra Pradesh West Godavari 28 2003-10-19 |  |  | Bio Power | 28 | 2003-10-19 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Krishnaveni Sugars Ltd Telangana Mahabubnagar 14 |  |  | Bio Power | 14 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Lalitha Enterprises Andhra Pradesh East Godavari 0.5 2003-08-15 |  |  | Bio Power | 0.5 | 2003-08-15 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | M.R.K.Co.op Sugar Mills Tamil Nadu Cuddalore 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | MGRRice Industries Andhra Pradesh East Godavari 0.89 2013-07-01 |  |  | Bio Power | 0.89 | 2013-07-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Madras Sugars & Chemicals Ltd. Tamil Nadu Tirunelveli 25 |  |  | Bio Power | 25 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Mahatma Gandhi Sahakari Sakkare Karkhane Niyamita Karnataka Bidar 13 04.07.2009 |  |  | Bio Power | 13 | 2009-04-07 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Malavalli Power Plant Pvt. Ltd. Karnataka Mandya 4.5 19.07.2001 |  |  | Bio Power | 4.5 | 2001-07-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Manali Petrochemicals Ltd. Tamil Nadu Thiruvallur 4.7 |  |  | Bio Power | 4.7 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Manali Sugar Ltd Karnataka Vijayapura 15 20.04.2013 |  |  | Bio Power | 15 | 2013-04-20 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Manchikonda Bio energy Pvt. Ltd Karnataka Raichur 6 01.03.2016 |  |  | Bio Power | 6 | 2016-01-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Mata Energy Ltd Telangana Nalgonda 6 |  |  | Bio Power | 6 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Matix Power (p) Ltd Andhra Pradesh Guntur 4.5 2001-08-08 |  |  | Bio Power | 4.5 | 2001-08-08 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Matrix Agro Pvt Ltd Karnataka Kalaburagi 6 09.12.2016 |  |  | Bio Power | 6 | 2016-09-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Mohan Breweries & Distillaries Ltd Tamil Nadu Kancheepuram 18 |  |  | Bio Power | 18 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | NCS Sugars ltd. Andhra Pradesh Vizianagaram 20 2007-06-15 |  |  | Bio Power | 20 | 2007-06-15 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | NSL Sugars Ltd Karnataka Ballari 28 30.09.2011 |  |  | Bio Power | 28 | 2011-09-30 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | NSL Sugars Ltd Karnataka Kalaburagi 34 12.04.2012 |  |  | Bio Power | 34 | 2012-12-04 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | NSL Sugars Ltd Karnataka Mandya 26 30.06.2004 |  |  | Bio Power | 26 | 2004-06-30 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Naga Hanuman Solvent Oils Pvt Ltd Andhra Pradesh West Godavari 1.2 2013-12-01 |  |  | Bio Power | 1.2 | 2013-12-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Green Power Ltd / My Home Power Ltd Telangana Medak 9 5.2.2002 |  |  | Bio Power | 9 | 2002-05-02 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Nandi Sahakari Sakkare Karkhane Niyamita Karnataka Vijayapura 21 31.03.2006 |  |  | Bio Power | 21 | 2006-03-31 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Naranja Sahakari Sakkare Karkhane Niyamita Karnataka Bidar 14 01.05.2005 |  |  | Bio Power | 14 | 2005-01-05 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Nava Bharat Agro Products Ltd Andhra Pradesh West Godavari 0.95 2014-09-12 |  |  | Bio Power | 0.95 | 2014-09-12 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nava Bharat Agro Products Ltd Andhra Pradesh West Godavari 1 2015-03-15 |  |  | Bio Power | 1 | 2015-03-15 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nava Bharat Ventures Ltd. Andhra Pradesh East Godavari 9 2005-11-23 |  |  | Bio Power | 9 | 2005-11-23 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nava Bharath Ltd Andhra Pradesh West Godavari 6 2017-07-01 |  |  | Bio Power | 6 | 2017-07-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nirani Sugars Ltd Karnataka Bagalkote 14 05.03.2010 |  |  | Bio Power | 14 | 2010-05-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Nirani Sugars Ltd Karnataka Bagalkote 16 13.06.2008 |  |  | Bio Power | 16 | 2008-06-13 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Nirani Sugars Ltd Karnataka Bagalkote 42 18.06.2011 |  |  | Bio Power | 42 | 2011-06-18 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Nizam Deccan Sugar Ltd Telangana Nizamabad 20 17.01.2006 |  |  | Bio Power | 20 | 2006-01-17 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | OM Shakthi Reenergies Ltd Andhra Pradesh Chittoor 6 2004-01-24 |  |  | Bio Power | 6 | 2004-01-24 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Orient Green Power Ltd. Tamil Nadu Coimbatore 10 |  |  | Bio Power | 10 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) (Waste to Energy) Andhra Pradesh N.A. 53.16 |  |  | Bio Power | 53.16 | Pre-2000 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) (Waste to Energy) Karnataka N.A. 1 |  |  | Bio Power | 1 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) (Waste to Energy) Tamil Nadu N.A. 6.4 |  |  | Bio Power | 6.4 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) (Waste to Energy) Telangana N.A. 45.8 |  |  | Bio Power | 45.8 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Biomass & bagasse based cogen.] Karnataka N.A. |  |  | Bio Power | 543.39 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Biomass & bagasse based cogen.] Tamil Nadu N.A |  |  | Bio Power | 138.2 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Andhra Pradesh N.A. |  |  | Bio Power | 48.02 | Pre-2000 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Karnataka N.A. 20.2 |  |  | Bio Power | 20.2 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Kerala N.A. 2.27 |  |  | Bio Power | 2.27 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Tamil Nadu N.A. 43.5 |  |  | Bio Power | 43.55 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Non-Bagasse based cogen.] Telangana N.A. 3.3 |  |  | Bio Power | 3.3 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Andhra Pradesh N.A |  |  | Bio Power | 49.19 | Pre-2000 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Karnataka N.A. 25. |  |  | Bio Power | 25.94 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Kerala N.A. 0.23 |  |  | Bio Power | 0.23 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Tamil Nadu N.A. 27 |  |  | Bio Power | 27.57 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Others (districts not specified) [Waste to Energy (Off-grid)] Telangana N.A. 14. |  |  | Bio Power | 14.47 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Pallavi Enterprises Andhra Pradesh Krishna 2.5 2010-02-10 |  |  | Bio Power | 2.5 | 2010-02-10 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Parrys Sugar Industries Ltd Karnataka Uttara Kannada 24 02.06.2008 |  |  | Bio Power | 24 | 2008-02-06 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Perpetual Energy Systems Ltd. Andhra Pradesh Vizianagaram 6 2003-03-23 |  |  | Bio Power | 6 | 2003-03-23 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Ponni Sugars Limited Tamil Nadu Erode 19 |  |  | Bio Power | 19 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Power Onicks Ltd. Karnataka Ballari 6 05.01.2005 |  |  | Bio Power | 6 | 2005-05-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Prabhulingeshwara Sugar Works Ltd Karnataka Bagalkote 38.5 14.11.2000 |  |  | Bio Power | 38.5 | 2000-11-14 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Prathyusha Power Pvt. Ltd. Tamil Nadu Tirunelveli 10 |  |  | Bio Power | 10 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | RK Power Gen Pvt. Ltd. Karnataka Chitradurga 20 01.01.2004 |  |  | Bio Power | 20 | 2004-01-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Raichur Bio Energies Pvt. Ltd. Karnataka Raichur 9 04.02.2016 |  |  | Bio Power | 9 | 2016-04-02 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajashree Sugars & Chemicals Ltd. Tamil Nadu Theni 12 |  |  | Bio Power | 12 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajashree Sugars & Chemicals Ltd. Tamil Nadu Viluppuram 20 |  |  | Bio Power | 20 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajashree Sugars & Chemicals Ltd. Tamil Nadu Viluppuram 22 |  |  | Bio Power | 22 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajkumar Impex(P) Ltd. Tamil Nadu Thoothukkudi 6 |  |  | Bio Power | 6 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Ravikiran Power Project Pvt. Ltd. Karnataka Koppal 7.5 01.06.2005 |  |  | Bio Power | 7.5 | 2005-01-06 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Rayalaseema Green Energy Ltd Andhra Pradesh Kurnool 5.5 2001-02-14 |  |  | Bio Power | 5.5 | 2001-02-14 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Raytar Sahakari Sakkare Karkhane Niyamita Karnataka Bagalkote 12.5 08.12.2001 |  |  | Bio Power | 12.5 | 2001-08-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Renuka Textiles Limited Tamil Nadu Theni 4.5 |  |  | Bio Power | 4.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Rithwik Energy Systems Ltd Andhra Pradesh Chittoor 6 2002-08-28 |  |  | Bio Power | 6 | 2002-08-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Rithwik Power Projects Ltd Telangana Khammam 6 13.11.2002 |  |  | Bio Power | 6 | 2002-11-13 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Roshni Power Tech Ltd Andhra Pradesh Krishna 6 2001-08-30 |  |  | Bio Power | 6 | 2001-08-30 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | S.V Sugar Mills Ltd. Tamil Nadu Kancheepuram 45 |  |  | Bio Power | 45 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | SLS Power Ltd Andhra Pradesh Sri Potti Sriramulu Nellore 6 2001-08-30 |  |  | Bio Power | 6 | 2001-08-30 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Saastha Energy(P) Ltd Tamil Nadu N.A. 2 |  |  | Bio Power | 2 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Sakti Sugars Ltd. Tamil Nadu Erode 24.5 |  |  | Bio Power | 24.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Sakti Sugars Ltd. Tamil Nadu Sivaganga 35 |  |  | Bio Power | 35 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Samsons Distilleries Pvt. Ltd. Karnataka Davangere 2 18.06.2003 |  |  | Bio Power | 2 | 2003-06-18 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Saritha Sugars Ltd Andhra Pradesh Sri Potti Sriramulu Nellore 6 01.04.2001 |  |  | Bio Power | 6 | 2001-01-04 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Saro Power and Infrastructures Ltd Telangana Mahabubnagar 6 24.4.2003 |  |  | Bio Power | 6 | 2003-04-24 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Satish Sugars Ltd Karnataka Belagavi 31 11.05.2012 |  |  | Bio Power | 31 | 2012-11-05 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Satyakala Power Projects (P) Ltd Andhra Pradesh Krishna 4 2001-11-02 |  |  | Bio Power | 4 | 2001-11-02 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Satyamaharshi Power Corpn Ltd Andhra Pradesh Guntur 6 2004-07-13 |  |  | Bio Power | 6 | 2004-07-13 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Seven Hills Papers (P) Ltd Andhra Pradesh East Godavari 1.2 2009-02-25 |  |  | Bio Power | 1.2 | 2009-02-25 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Shakti Sugars Ltd. Tamil Nadu Erode 32 |  |  | Bio Power | 32 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Shalivahana Green Energy Ltd Telangana Adilabad 6 1.12.2002 |  |  | Bio Power | 6 | 2002-01-12 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Shamanur Sugars Ltd Karnataka Davangere 22 13.08.1999 |  |  | Bio Power | 22 | 1999-08-13 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shiraguppi Sugar Works Ltd Karnataka Belagavi 14 01.05.2013 |  |  | Bio Power | 14 | 2013-01-05 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivasagar Sugar & Agro Products Ltd Karnataka Belagavi 8 30.06.2013 |  |  | Bio Power | 8 | 2013-06-30 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivashakthi Sugars Ltd Karnataka Belagavi 20 01.06.2013 |  |  | Bio Power | 20 | 2013-01-06 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Gowthamee Rice Industries (P) Limited Andhra Pradesh East Godavari 0.58 20 |  |  | Bio Power | 0.58 | 2014-02-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Gowthamee Rice Industries (P) Limited Andhra Pradesh East Godavari 0.88 20 |  |  | Bio Power | 0.88 | 2016-06-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Papers Ltd Andhra Pradesh East Godavari 4 2003-02-23 |  |  | Bio Power | 4 | 2003-02-23 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Renuka Sugars Ltd Karnataka Belagavi 30 01.12.2012 |  |  | Bio Power | 30 | 2012-01-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Renuka Sugars Ltd Karnataka Belagavi 38 07.03.2000 |  |  | Bio Power | 38 | 2000-07-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Renuka Sugars Ltd Karnataka Belagavi 38 11.01.2012 |  |  | Bio Power | 38 | 2012-11-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Renuka Sugars Ltd Karnataka Kalaburagi 25 01.12.2009 |  |  | Bio Power | 25 | 2009-01-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shree Vani Sugars & Industries Ltd Andhra Pradesh Chittoor 9 2003-08-08 |  |  | Bio Power | 9 | 2003-08-08 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Shriraam City Union Finance Ltd. Tamil Nadu Thanjavur 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Shriram Investments Ltd. Tamil Nadu Dindigul 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Sindhura Paper Pvt Ltd Andhra Pradesh West Godavari 3 2017-07-01 |  |  | Bio Power | 3 | 2017-07-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Singaraya Hills Green Power Genco (p) Ltd. Andhra Pradesh Prakasam 8 2008-07-13 |  |  | Bio Power | 8 | 2008-07-13 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sirius Overseas Pvt. Ltd Andhra Pradesh East Godavari 9 2009-01-04 |  |  | Bio Power | 9 | 2009-01-04 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Soubhagya Lakshmi Sugars Ltd Karnataka Belagavi 18 01.12.2013 |  |  | Bio Power | 18 | 2013-01-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | South India Paper Mills Ltd Karnataka Belagavi 7.8 19.05.2001 |  |  | Bio Power | 7.8 | 2001-05-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sree Godavari Kraft Paper (p) ltd Andhra Pradesh West Godavari 3 2008-11-15 |  |  | Bio Power | 3 | 2008-11-15 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Gowthami Rice Industries Ltd Andhra Pradesh East Godavari 0.75 2009-03-25 |  |  | Bio Power | 0.75 | 2009-03-25 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Kalyani Agro Products & Industries Limited Andhra Pradesh West Godavari 4 20 |  |  | Bio Power | 4 | 2002-12-03 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Lalitha Enterprises Industries Ltd (Unit II) Andhra Pradesh East Godavari 4. |  |  | Bio Power | 4.7 | 2009-02-25 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Murali Mohana Para Boiled Rice Mill Andhra Pradesh East Godavari 0.65 2003-0 |  |  | Bio Power | 0.65 | 2003-08-26 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Ramadas Paper Boards (P) Ltd Andhra Pradesh East Godavari 4 2006-06-27 |  |  | Bio Power | 4 | 2006-06-27 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Sarvaraya Sugars Ltd Andhra Pradesh East Godavari 19.65 2008-12-25 |  |  | Bio Power | 19.65 | 2008-12-25 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Satyanarayana Raw & Boiled Rice (P) Ltd Andhra Pradesh West Godavari 0.75 20 |  |  | Bio Power | 0.75 | 2008-03-31 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sripathi Paper & Board (P) Ltd Tamil Nadu Virudhunagar 4.95 09.03.2011 |  |  | Bio Power | 4.95 | 2011-09-03 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Subashri Bio Energy (P) Ltd. Tamil Nadu Namakkal 2.5 |  |  | Bio Power | 2.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Subramania Siva Co-op Sugar Mills Tamil Nadu Dharmapuri 5 |  |  | Bio Power | 5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Suchand Power Gen.(p) Ltd Andhra Pradesh Kurnool 6 2002-11-28 |  |  | Bio Power | 6 | 2002-11-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sudha Agro Oil & Chemicals Industries Ltd Andhra Pradesh East Godavari 4 2001-12 |  |  | Bio Power | 4 | 2001-12-27 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sudulagunta Sugars Ltd Andhra Pradesh Chittoor 8 1999-06-09 |  |  | Bio Power | 8 | 1999-06-09 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Surya Chandra Paper Mills Ltd Andhra Pradesh East Godavari 3 2007-11-27 |  |  | Bio Power | 3 | 2007-11-27 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Surya Teja Power Projects Pvt Ltd Telangana Mahabubnagar 6 31.03.2007 |  |  | Bio Power | 6 | 2007-03-31 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Synergy Sakthi Renewable energy Ltd. Tamil Nadu Dharmapuri 10 |  |  | Bio Power | 10 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | TCP Ltd. Tamil Nadu Sivaganga 9 |  |  | Bio Power | 9 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Terra Energy Ltd. Tamil Nadu Cuddalore 18.68 |  |  | Bio Power | 18.68 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Terra Energy Ltd. Tamil Nadu Thanjavur 28.42 |  |  | Bio Power | 28.42 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | The Etikoppaka Co.op Agrl. & Industrial Society Ltd. Andhra Pradesh Visakhapatna |  |  | Bio Power | 4.5 | 2001-03-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Ugar Sugars Works Ltd Karnataka Belagavi 44 28.05.1998 |  |  | Bio Power | 44 | 1998-05-28 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ugar Sugars Works Ltd Karnataka Kalaburagi 15 28.10.2010 |  |  | Bio Power | 15 | 2010-10-28 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Vamshi Industries Ltd. Andhra Pradesh East Godavari 4 2001-04-20 |  |  | Bio Power | 4 | 2001-04-20 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Varam Power Projects (P) Ltd Andhra Pradesh Srikakulam 6 2001-12-01 |  |  | Bio Power | 6 | 2001-12-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Veda Bio Fuel Pvt Ltd Andhra Pradesh Vizianagaram 3 2016-03-15 |  |  | Bio Power | 3 | 2016-03-15 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Veeraiah Non-Conventional Power Projects Ltd. Andhra Pradesh Krishna 4 2002-10-2 |  |  | Bio Power | 4 | 2002-10-26 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Velagapudi Power Generation Ltd Andhra Pradesh Guntur 4 2006-11-13 |  |  | Bio Power | 4 | 2006-11-13 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Venkatarama Oil Industries Limited. Andhra Pradesh East Godavari 1.3 2015-08-01 |  |  | Bio Power | 1.3 | 2015-08-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Venkateshwara Power Projects Ltd Karnataka Belagavi 15 03.11.2004 |  |  | Bio Power | 15 | 2004-03-11 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Vijaya Agro Products (p) Ltd Andhra Pradesh Krishna 4 2001-12-24 |  |  | Bio Power | 4 | 2001-12-24 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Vijaynagar Bio- Tech Ltd Andhra Pradesh Vizianagaram 1.2 2013-02-20 |  |  | Bio Power | 1.2 | 2013-02-20 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Vijaynagar Sugars Ltd Karnataka Belagavi 35.5 04.03.2010 |  |  | Bio Power | 35.5 | 2010-04-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Vishnu Vidyuth India Ltd Andhra Pradesh Visakhapatnam 7.5 2013-01-11 |  |  | Bio Power | 7.5 | 2013-01-11 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Vishwanath Sugars Ltd Karnataka Belagavi 14 06.01.2006 |  |  | Bio Power | 14 | 2006-06-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bellary TPS |  | Subcritical | Coal | 1700 | 2007-12-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadradri TPP |  | Supercritical | Coal | 1080 | 2020-03-01 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Damodaram Sanjeevaiah or Krishnapatnam TPP |  | Supercritical | Coal | 2400 | 2014-08-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | ITPCL or Cuddalore TPP |  | Subcritical | Coal | 1200 | 2015-09-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Kakatiya TPS |  | Subcritical | Coal | 1100 | 2010-05-01 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Kothagudem TPS |  | Subcritical | Coal | 1800 | 1997-03-01 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Kudgi STPP |  | Supercritical | Coal | 2400 | 2016-12-25 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Mettur TPS |  | Subcritical | Coal | 1440 | 1987-01-07 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Muthiara TPP |  | Subcritical | Coal | 1200 | 2014-12-02 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli (EXT) TPS I |  | Subcritical | Coal | 420 | 2002-10-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli (EXT) TPS II |  | Subcritical | Coal | 500 | 2012-02-04 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli (New) TPP /Neyveli Extension |  | Subcritical | Coal | 1000 | 2019-12-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli TPS (Z) |  | Subcritical | Coal | 250 | 2002-10-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Neyveli TPS II |  | Subcritical | Coal | 1470 | 1986-03-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | North Chennai TPS |  | Subcritical | Coal | 1830 | 1994-10-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | OPG Power Generation Private Ltd. |  | Subcritical | Coal | 414 | 2024-01-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Raichur TPS |  | Subcritical | Coal | 1720 | 1985-03-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ramagudem -B TPS |  | Subcritical | Coal | 62.5 | 1971-10-01 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Ramagundam STPP/Telangana Phase I |  | Ultra-Supercritical | Coal | 1600 | 2023-09-09 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Ramagundam STPS |  | Subcritical | Coal | 2600 | 1983-11-01 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Rayalaseema TPS |  | Subcritical | Coal | 1650 | 1994-03-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sembcorp Gayatri Power Ltd. Power Project |  | Supercritical | Coal | 1320 | 2016-11-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Simhadri TPP |  | Subcritical | Coal | 2000 | 2002-02-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Simhapuri TPS |  | Subcritical | Coal | 600 | 2012-03-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Singareni TPP |  | Subcritical | Coal | 1200 | 2016-03-13 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | TCP Limited |  | Supercritical | Coal | 63.5 | 2024-12-23 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Thamminapatnam TPS |  | Subcritical | Coal | 1000 | 2012-10-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Thermal Powertech Corporation Ltd/ Painampuram/Muthukur Mandal |  | Supercritical | Coal | 1320 | 2015-02-07 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Torangallu TPS SBU |  | Subcritical | Coal | 860 | 1999-05-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin (P) TPP |  | Subcritical | Coal | 300 | 2013-01-31 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin Joint Venture |  | Subcritical | Coal | 1000 | 2015-03-10 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin TPS |  | Subcritical | Coal | 1050 | 1979-07-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin Thermal Power Plant |  | Subcritical | Coal | 525 | 2021-12-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Udupi TPP |  | Subcritical | Coal | 1200 | 2010-07-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Vallur TPP |  | Subcritical | Coal | 1500 | 2012-03-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Vijayawada or Dr. Narla Tata Rao TPS |  | Subcritical | Coal | 2560 | 1979-11-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Vizag or Hinduja Power TPP |  | Subcritical | Coal | 1040 | 2015-12-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Yadadri Thermal Power Station |  | Supercritical | Coal | 1600 | 2025-01-25 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Yermarus TPP |  | Supercritical | Coal | 1600 | 2016-03-29 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Aliyar Hydroelectric Power Project |  |  | Hydro | 60 | 1970-03-21 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Almatti Dam Power House |  |  | Hydro | 290 | 2004-03-26 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadra Left Bank Canal Power House |  |  | Hydro | 26 | 1965-03-29 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Kattalai Barrage I Hydroelectric Power Project |  |  | Hydro | 30 | 2006-07-04 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Kattalai Barrage II Hydroelectric Power Project |  |  | Hydro | 30 | 2013-08-27 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Kattalai Barrage III Hydroelectric Power Project |  |  | Hydro | 30 | 2012-06-28 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Gerusoppa (Sharavathy Tail Race) Power House |  |  | Hydro | 240 | 2001-02-20 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ghat Prabha Dam Power House |  |  | Hydro | 32 | 1992-06-14 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hampi Canal Power House |  |  | Hydro | 36 | 1958-01-02 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Idamalayar Hydroelectric Power Project |  |  | Hydro | 75 | 1987-02-03 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Idukki Hydroelectric Power Project |  |  | Hydro | 780 | 1976-02-12 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Jog (Mahatma Gandhi) Hydroelectric Power Project |  |  | Hydro | 139.2 | 1949-08-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kadmparai Power House |  |  | Hydro | 400 | 1987-10-17 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Kadra Dam Power House |  |  | Hydro | 150 | 1997-06-02 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kakkad Hydroelectric Power Project |  |  | Hydro | 50 | 2012-02-16 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Kalinadi Nagjhari Power House |  |  | Hydro | 900 | 1979-08-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kalinadi Nagjhari Supa Dam Power House |  |  | Hydro | 100 | 1985-08-23 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kodasali Dam Power House |  |  | Hydro | 120 | 1998-06-20 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kodayar I & II Power House |  |  | Hydro | 100 | 1970-12-09 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Kundah I to V Hydroelectric Power Project |  |  | Hydro | 555 | 1960-07-08 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Kuttiyadi Hydroelectric Old, Additional & Extension Power House |  |  | Hydro | 225 | 1972-09-11 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Lingnamakki Dam Power House |  |  | Hydro | 55 | 1979-08-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Jurala Hydroelectric Power Project |  |  | Hydro | 240 | 2015-09-30 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Mettur I to IV Hydroelectric Power Project |  |  | Hydro | 120 | 1988-01-04 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Periyar Hydroelectric Power Project |  |  | Hydro | 180 | 1997-09-27 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Sileru Hydroelectric Power Project |  |  | Hydro | 460 | 1976-03-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Mettur Dam Hydroelectric Power Project |  |  | Hydro | 50 | 1937-06-13 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Mettur Tunnel |  |  | Hydro | 200 | 1965-08-16 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Moyar Power House |  |  | Hydro | 40 | 1952-04-10 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Munirabad Power House |  |  | Hydro | 28 | 1962-01-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Sagar (N.J.Sagar) Hydroelectric Power Project |  |  | Hydro | 815.6 | 1978-03-07 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Sagar Left Bank Canal Power House (N.J.Sagar LBC) |  |  | Hydro | 60 | 1983-06-05 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Sagar Right Bank Canal Power House (N.J.Sagar RBC) |  |  | Hydro | 90 | 1983-02-24 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nagarjuna Sagar Tail Pond Dam (N.J.Sagar TPD) |  |  | Hydro | 50 | 2017-01-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Neriamangalam Hydroelectric Power Project |  |  | Hydro | 52.65 | 1961-01-27 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Pallivasal Hydro Power Project |  |  | Hydro | 60 | 2025-03-01 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Pallivasal Hydroelectric Power Project |  |  | Hydro | 37.5 | 1948-02-02 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Panniar Hydroelectric Power Project |  |  | Hydro | 30 | 1963-12-29 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Papanasam Hydroelectric Power Project |  |  | Hydro | 32 | 1944-07-08 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Parson's Valley Hydroelectric Power Project |  |  | Hydro | 30 | 2000-06-22 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Hydroelectric Power Project |  |  | Hydro | 168 | 1958-10-12 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Pinnapuram (Standalone Pumped Storage ) Hydro Power Project |  |  | Hydro | 1680 | 2025-06-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Pochampad (Sriram Sagar Project) Hydroelectric Power Project |  |  | Hydro | 36 | 1987-02-20 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Poringalkuthu Hydroelectric Power Project |  |  | Hydro | 36 | 1957-03-06 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Priyadarshni Jurala Hydroelectric Power Project |  |  | Hydro | 234 | 2008-03-28 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Pulichinthala Hydroelectric Power Project |  |  | Hydro | 120 | 2016-09-25 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Pykara Hydroelectric Power Project |  |  | Hydro | 59.2 | 1932-06-09 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Pykara Ultimate Hydroelectric Power Project |  |  | Hydro | 150 | 2005-09-06 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Sabarigiri Hydroelectric Power Project |  |  | Hydro | 340 | 1960-04-18 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Sarkarpathy Hydroelectric Power Project |  |  | Hydro | 30 | 1966-08-14 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Sengulam Hydroelectric Power Project |  |  | Hydro | 48 | 1954-05-01 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Sharavathi Hydroelectric Power Project |  |  | Hydro | 1035 | 1964-08-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivasamudram Hydroelectric Power Project |  |  | Hydro | 42 | 1902-08-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sholayar Hydroelectric Power Project |  |  | Hydro | 54 | 1956-05-09 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Sholayar I Power House |  |  | Hydro | 84 | 1971-04-22 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Srisailam Left Bank Power House |  |  | Hydro | 900 | 2001-04-26 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Srisailam Right Bank (RB) Power House |  |  | Hydro | 770 | 1982-08-30 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Suruliyar Hydroelectric Power Project |  |  | Hydro | 35 | 1978-08-27 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | T B Dam/Tungabhadra Dam Hydroelectric Power Project |  |  | Hydro | 36 | 1957-01-26 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Thottiyar Hydro Power Project |  |  | Hydro | 40 | 2024-10-01 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Upper Sileru I & II Hydroelectric Power Project |  |  | Hydro | 240 | 1967-10-14 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Varahi Power House |  |  | Hydro | 460 | 2009-01-11 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kaiga Generating Station |  |  | Nuclear | 880 | 2000-03-16 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kudankulam Atomic Power Project |  |  | Nuclear | 2000 | 2014-12-31 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Madras Atomic Power Station |  |  | Nuclear | 440 | 1984-01-27 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Basin Bridge Gas Turbine Power Station |  |  | Oil & Gas | 120 | 1996-02-12 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | GMR Rajahmundry Energy Ltd. |  |  | Oil & Gas | 768 | 2015-07-04 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | GMR Vemagiri Combined Cycle Power Plant |  |  | Oil & Gas | 370 | 2006-01-13 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | GVK Jegurupadu Gas Combined Cycle Gas Turbine |  |  | Oil & Gas | 235.4 | 1996-07-04 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Karaikal Gas Power Plant |  |  | Oil & Gas | 32.5 | 1999-10-01 | Puducherry | India_Electricity_Infrastructure.xlsx
India | IN_S | Kayamkulam (Rajiv Gandhi) Gas Combined Cycle Power Plant |  |  | Oil & Gas | 359.58 | 1998-11-02 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Kovilkalappal (Thirumakotai) Gas Combined Cycle Gas Turbine Power Station |  |  | Oil & Gas | 107.88 | 2001-02-05 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Kuttalam Gas Turbine Power Station |  |  | Oil & Gas | 100 | 2003-11-27 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Lanco Kondapalli Combined Cycle Gas Turbine Power Plant Phase II |  |  | Oil & Gas | 366 | 2009-12-05 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Pillaiperumalnallur (PPN) Power Plant Phase I |  |  | Oil & Gas | 330.5 | 2001-04-26 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Valuthur Gas Turbine Power Station |  |  | Oil & Gas | 186.2 | 2002-12-24 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Yelahanka Combined Cycle Power Plant |  |  | Oil & Gas | 370.05 | 2025-02-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | APICTO Ltd. Small Hydro Power Project |  |  | Small Hydro | 13 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Abletech Electro Engineers Pvt. Ltd. Small Hydro Power Project |  |  | Small Hydro | 4.8 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Adyanpara Small Hydro Electric Project |  |  | Small Hydro | 3.5 | 2015-03-09 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Agradalli Mini Hydel Power Station |  |  | Small Hydro | 0.75 | 2008-10-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Agrahara Mini Hydel Power Station |  |  | Small Hydro | 1.26 | 2012-09-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Akkihebbal Mini Hydel Power Station |  |  | Small Hydro | 4.5 | 2007-09-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Aliyar Mini Hydel Project |  |  | Small Hydro | 2.5 | 2002-09-23 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Amaravathi Small Hydro Project |  |  | Small Hydro | 4 | 2006-09-21 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Aniyooru Mini Hydel Station |  |  | Small Hydro | 24 | 2019-11-21 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Aniyur Mini Hydel Power Station |  |  | Small Hydro | 9 | 2009-08-13 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Anweri Mini Hydel Station |  |  | Small Hydro | 1.5 | 1997-05-04 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Aremadanahalli Mini Hydel Power Station |  |  | Small Hydro | 1.5 | 2013-09-02 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Attigala Small Hydro Power Station |  |  | Small Hydro | 0.35 | 1998-07-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Auromira Energy Group Hydro Project |  |  | Small Hydro | 18 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Baje Mini Hydel Station |  |  | Small Hydro | 3.8 | 2015-07-10 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Barapole Small Hydro Electric Project |  |  | Small Hydro | 15 | 2013-12-04 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Basavanna(Aidab havi) Mini Hydel Power Station |  |  | Small Hydro | 24.75 | 2013-02-05 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Beedalli Mini Hydel Station |  |  | Small Hydro | 3 | 2016-06-13 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bellamkonda Branch Canal Small Hydro Project |  |  | Small Hydro | 0.55 | 2004-11-17 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Bellamkonda Branch canal Hydro Power Project Scheme II |  |  | Small Hydro | 0.55 | 1999-08-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadra Left Bank Canal Mini Hydel Station |  |  | Small Hydro | 1.5 | 2018-04-05 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadra Right Bank Canal Power Station |  |  | Small Hydro | 0.4 | 2005-01-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhadra Right Bank Canal Powerhouse |  |  | Small Hydro | 13.2 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Barrage I Small Hydro Electric Project |  |  | Small Hydro | 10 | 2009-07-01 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Barrage II Small Hydro Electric Project |  |  | Small Hydro | 10 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavani Hydro Power Project |  |  | Small Hydro | 1.4 | 2000-04-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhima-I (Sonna) Mini Hydel Station |  |  | Small Hydro | 10.5 | 2010-08-04 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhoruka Power Corporation Hydro Project 1 |  |  | Small Hydro | 6.25 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhoruka Power Corporation Hydro Project 2 |  |  | Small Hydro | 24 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Bonal Tank Mini Hydel Project |  |  | Small Hydro | 1.25 | 2011-08-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Brindavan Mini Hydel Power Station |  |  | Small Hydro | 12 | 2006-06-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Burgugadda Tank Small Hydro Project |  |  | Small Hydro | 1.2 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Charmadi Mini Hydel Power Station |  |  | Small Hydro | 4.5 | 2008-07-05 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Chayadevi Mini Hydel Power Station |  |  | Small Hydro | 24 | 2007-06-22 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Chembukadavu-I Small Hydro Electric Project |  |  | Small Hydro | 2.7 | 2003-08-19 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Chembukadavu-II Small Hydro Electric Project |  |  | Small Hydro | 3.75 | 2003-09-04 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Chettipeta Mini Hydel |  |  | Small Hydro | 1 | Pre-2000 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Chilakaluripet Major Block Small Hydro Project |  |  | Small Hydro | 1 | 2000-07-13 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Chimmony Small Hydro Electric Project |  |  | Small Hydro | 2.5 | 2015-05-22 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Chunchanakatte Small Hydro Power Station |  |  | Small Hydro | 18 | 1997-10-13 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Chunchidoddi Mini Hydel Power Station |  |  | Small Hydro | 10.25 | 2004-12-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Deccan Cement Ltd. Small Hydro Project |  |  | Small Hydro | 3.7 | 1996-02-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Dhanalakshmi Cotton & Rice Mills Limited Small Hydro Project 1 |  |  | Small Hydro | 1.59 | 1997-12-23 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Dhanalakshmi Cotton & Rice Mills Limited Small Hydro Project 2 |  |  | Small Hydro | 2.61 | 1997-07-23 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Doddatappale Mini Hydel Power Station |  |  | Small Hydro | 3 | 2011-01-22 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Dondela Mini Hydel Power Station |  |  | Small Hydro | 13 | 2009-07-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Donkarayi Canal Hydroelectric Power Plant |  |  | Small Hydro | 25 | Pre-2000 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Dummagudem Hydel Project |  |  | Small Hydro | 24 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Duphadal Small Hydro Electric Power Station |  |  | Small Hydro | 2.8 | 1997-04-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Energy Development Hydro Project |  |  | Small Hydro | 7 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Espar Pak Limited Small Hydro Project |  |  | Small Hydro | 1.3 | 2000-04-08 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Flovel Small Hydro Project 1 |  |  | Small Hydro | 4.5 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Flovel Small Hydro Project 2 |  |  | Small Hydro | 4.8 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Gajanur Mini Hydel Station |  |  | Small Hydro | 0.65 | 2014-06-06 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ganekal Mini Hydel Scheme |  |  | Small Hydro | 0.35 | 1993-12-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ganganahal Mini Hydel Power Station |  |  | Small Hydro | 2 | 2013-07-30 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Gayatri Hydro Power Project |  |  | Small Hydro | 2.2 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Gilada Group Small Hydro Power Project |  |  | Small Hydro | 6 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Gokak Mini Hydel Station |  |  | Small Hydro | 10.8 | 1997-04-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Gonal 2 Mini Hydel Power Station |  |  | Small Hydro | 2 | 2019-08-27 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Gonal 3 Mini Hydel Power Station |  |  | Small Hydro | 5 | 2011-11-04 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Gugal Mini Hydel Power Station |  |  | Small Hydro | 10 | 2007-09-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hanumanthapura Mini Hydel Station |  |  | Small Hydro | 0.5 | 2002-09-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Harangi Mini Hydel Station |  |  | Small Hydro | 15 | 1999-07-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hebbakavadi Mini Hydel Station |  |  | Small Hydro | 1.75 | 2002-04-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hemagir Mini Hydel Power Station |  |  | Small Hydro | 4 | 2005-06-28 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hemavathi Left Bank Canal Mini Hydel Station |  |  | Small Hydro | 16 | 2001-04-20 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hemavathi Right Bank Canal Mini Hydel Station |  |  | Small Hydro | 3 | 2000-07-10 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hemavathi River Bed Mini Hydel Power Station |  |  | Small Hydro | 8 | 2007-04-28 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hongadalla Mini Hydel Station |  |  | Small Hydro | 24 | 2019-05-08 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hosmath Mini Hydel Power Station |  |  | Small Hydro | 4.8 | 2011-08-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Hullahhalla Mini Hydel Power Station |  |  | Small Hydro | 12 | 2009-04-07 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Iggalur Mini Hydel Station |  |  | Small Hydro | 1.5 | 2015-01-23 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Iruttukanam Small Hydro Electric Project |  |  | Small Hydro | 4.5 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Jyothi Jalashakthi Pvt. Ltd. Mini Hydel Power Station |  |  | Small Hydro | 0.3 | 2005-11-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | KCP Limited Small Hydro Project |  |  | Small Hydro | 8.25 | 1998-03-24 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | KRS Dam Mini Hydel Power Station |  |  | Small Hydro | 4 | 2009-11-02 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kabini Dam Mini Hydel Station |  |  | Small Hydro | 20 | 2003-06-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kabini RBC Mini Hydel Station |  |  | Small Hydro | 5 | 2002-12-31 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kadamane I Mini Hydel Power Station |  |  | Small Hydro | 9 | 2007-04-30 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kadamane II Mini Hydel Power Station |  |  | Small Hydro | 15 | 2010-08-04 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kallada Small Hydro Electric Project |  |  | Small Hydro | 15 | 1994-01-05 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Kallam Spinning Mill Limited Hydro Power Project |  |  | Small Hydro | 4 | 2002-01-01 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Kalmala Mini Hydel Scheme |  |  | Small Hydro | 0.4 | 1990-01-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kare Power Resource Mini Hydel Station |  |  | Small Hydro | 24.75 | 2015-09-16 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kare Power Resources Hydro Project |  |  | Small Hydro | 24 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Karikkayam Small Hydro Electric Project |  |  | Small Hydro | 15 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Karnataka Power Corporation Limited (KPCL) Hydro Project 1 |  |  | Small Hydro | 17.2 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Karnataka Power Corporation Limited (KPCL) Hydro Project 2 |  |  | Small Hydro | 9 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kattepura Mini Hydel Station |  |  | Small Hydro | 5 | 2013-09-05 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kemphole Mini Hydel Power Station |  |  | Small Hydro | 18 | 2005-01-10 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kenchanagudam Mini Hydel Station |  |  | Small Hydro | 6 | 2007-05-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kilara Small Hydro Electric Power Station |  |  | Small Hydro | 2 | 2000-03-31 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kodagu Hydel Project |  |  | Small Hydro | 3 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Kuttiady Tailrace Small Hydro Project |  |  | Small Hydro | 4.5 | 2008-06-19 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | L.K. Power Corporation Hydro Project |  |  | Small Hydro | 2 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Link Canal Mini Hydel Station |  |  | Small Hydro | 1.5 | 2003-07-17 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Bhavani Micro Hydel Project |  |  | Small Hydro | 8 | 1990-04-03 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Bhavani Right Bank Canal Project |  |  | Small Hydro | 8 | 1998-02-10 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Meenmutty Small Hydro Electric Project |  |  | Small Hydro | 3.5 | 2006-05-02 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | MGHE Tail Race Mini Hydel Power Station |  |  | Small Hydro | 22 | 2007-12-06 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Machagundal Mini Hydel Station |  |  | Small Hydro | 0.5 | 2017-05-31 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Maddur Branch Canal Mini Hydel Power Station |  |  | Small Hydro | 2 | 2011-01-22 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Madhavamantri Mini Hydel Station |  |  | Small Hydro | 3 | 2001-07-09 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Madupetty Small Hydro Electric Station |  |  | Small Hydro | 2 | 1997-12-01 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Mahadevapura-II Mini Hydel Station |  |  | Small Hydro | 6 | 2014-03-28 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Malampuzha Small Hydro Electric Project |  |  | Small Hydro | 2.5 | 2001-11-26 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Malankara Small Hydro Electric Station |  |  | Small Hydro | 10.5 | 2005-08-06 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Mallapur Mini Hydro Power Station Project |  |  | Small Hydro | 9 | 1993-11-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Malligere Mini Hydel Power Station |  |  | Small Hydro | 0.75 | 2007-09-27 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Mandagere Mini Hydel Power Station |  |  | Small Hydro | 3.5 | 2004-09-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Mani Dam Power House |  |  | Small Hydro | 9 | 1993-03-29 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Maniyar Small Hydro Power Project |  |  | Small Hydro | 12 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Manjanadka Mini Hydel Power Station |  |  | Small Hydro | 10 | 2009-06-27 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Mankulam Micro Hydroelectric Power Plant |  |  | Small Hydro | 0.11 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Mannapitlu Mini Hydel Power Station |  |  | Small Hydro | 15 | 2009-09-17 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Maravakandy Small Hydro Project |  |  | Small Hydro | 0.75 | 1992-10-14 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Meenvallam Small Hydro Electric Project |  |  | Small Hydro | 3 | 2014-12-01 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Mouneshwara Mini Hydel Power Station |  |  | Small Hydro | 24.75 | 2013-08-14 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Mukurthy Small Hydro Project |  |  | Small Hydro | 0.7 | 2001-06-27 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Mulibettu Mini Hydel Station |  |  | Small Hydro | 10.5 | 2015-06-27 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | NATL Hydro Power Project |  |  | Small Hydro | 4.01 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | NCL Energy Limited Small Hydro Project |  |  | Small Hydro | 7.5 | 2000-09-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Narayanapura LBC Small Hydro Electric Power Station |  |  | Small Hydro | 11.6 | 1999-07-14 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Neerukatte Mini Hydel Power Station |  |  | Small Hydro | 15 | 2009-09-09 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Neria Mini Hydel Power Station |  |  | Small Hydro | 18 | 2006-04-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Nippulavagu Small Hydro Project Phase I |  |  | Small Hydro | 4 | 2002-02-06 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nippulavagu Small Hydro Project Phase II |  |  | Small Hydro | 3.3 | 2002-11-07 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nippulavagu Small Hydro Project Phase III |  |  | Small Hydro | 4 | 2003-11-21 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Nizam Sagar Hydroelectric Power Plant |  |  | Small Hydro | 10 | 1954-02-23 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Nugu Mini Hydel Station |  |  | Small Hydro | 3 | 2002-12-31 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Palair Hydro Electric Station |  |  | Small Hydro | 2 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Paschim Hydro Energy Small Hydro Project |  |  | Small Hydro | 9 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Pathankayam Small Hydro Electric Plant |  |  | Small Hydro | 8 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Pedda Vagu Mini Hydel Project |  |  | Small Hydro | 1.2 | 2011-04-15 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Peddapalli Mini Hydro Station |  |  | Small Hydro | 9.16 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Peechi Small Hydro Electric Project |  |  | Small Hydro | 1.25 | 2013-01-07 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Pendanandipadu Branch Canal Mini Hydel Scheme |  |  | Small Hydro | 0.65 | 2001-05-17 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Penna Ahobilam Hydroelectric Power Plant (PABH HES) |  |  | Small Hydro | 20 | Pre-2000 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Peppara Small Hydro Electric Project |  |  | Small Hydro | 3 | 1996-06-15 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Vaigai Mini I Hydro Project |  |  | Small Hydro | 4 | 2010-10-02 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Vaigai Mini II Hydro Project |  |  | Small Hydro | 2.5 | 2011-01-21 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Vaigai Mini III Hydro Project |  |  | Small Hydro | 4 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Periyar Vaigai Mini IV Hydro Project |  |  | Small Hydro | 2.5 | Pre-2000 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Perla Mini Hydel Power Station |  |  | Small Hydro | 24 | 2009-09-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Perunchani Small Hydro Project |  |  | Small Hydro | 1.3 | 2005-12-21 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Perunthenaruvi Small Hydro Electric Project |  |  | Small Hydro | 6 | 2017-10-22 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Pioneer Power Corporation Ltd. Small Hydro Power Project |  |  | Small Hydro | 24.75 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ponmudi Small Hydro Electric Station |  |  | Small Hydro | 32.4 | 1963-12-29 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Poozhithode Small Hydro Electric Project |  |  | Small Hydro | 4.8 | 2011-06-25 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Poringalkuthu Left Bank Extension Project |  |  | Small Hydro | 16 | 1999-03-20 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Poringalkuthu small hydroelectric project |  |  | Small Hydro | 24 | 2022-05-04 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Prassana Power Ltd. Small Hydro Power Project |  |  | Small Hydro | 6 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Punachi Small Hydro Project |  |  | Small Hydro | 2 | 1992-11-12 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Pykara Micro Power House |  |  | Small Hydro | 2 | 1989-10-09 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | RNS Infrastructures Small Hydro Power Project |  |  | Small Hydro | 11.4 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Rajankollur Small Hydro Power Station |  |  | Small Hydro | 2 | 1999-08-06 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ranganatha Swami Mini Hydel Power Station |  |  | Small Hydro | 24.75 | 2007-07-29 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ranni Perinad Small Hydro Electric Project |  |  | Small Hydro | 4 | 2012-02-16 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Rayabasavanna Mini Hydel Power Station |  |  | Small Hydro | 1.4 | 2013-08-31 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Rayalaseema Power Projects Limited Small Hydro Plant |  |  | Small Hydro | 3 | 1998-11-21 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | SKJ Power Limited Small Hydro Project |  |  | Small Hydro | 1.5 | 1999-01-27 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | SPML Infra Small Hydro Project |  |  | Small Hydro | 20 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sagar Power Limited Small Hydro Project |  |  | Small Hydro | 4.3 | 1997-11-27 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sagar Power Limited Small Hydro Project II |  |  | Small Hydro | 4 | 1998-09-07 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Saraswati Hydro Power Project |  |  | Small Hydro | 2 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Sardar Power Ltd. Small Hydro Project |  |  | Small Hydro | 2 | 2008-12-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sathanur Small Hydro Project |  |  | Small Hydro | 7.5 | 1999-03-10 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Sattegala Mini Hydel Power Station |  |  | Small Hydro | 6.25 | 2006-09-14 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Servalar Small Hydro Project |  |  | Small Hydro | 20 | 1986-03-23 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Shahapur Mini Hydel Power Station |  |  | Small Hydro | 13.2 | 1997-03-18 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shamburi Mini Hydel Power Station |  |  | Small Hydro | 24 | 2009-09-28 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shamili Hydel Power Project |  |  | Small Hydro | 12 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shanmukhasubramanya Mini Hydel Station |  |  | Small Hydro | 10 | 2016-12-12 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sheshadri Iyer Mini Hydel Station |  |  | Small Hydro | 6.6 | 2001-08-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shimsha Hydro Electric Power Station |  |  | Small Hydro | 17.2 | 1940-04-18 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shimsha Mini Hydel Power Station |  |  | Small Hydro | 24 | 2001-10-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shiva Mini Hydel Station |  |  | Small Hydro | 3 | 1998-09-10 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivani Power Spinners Hydro Project |  |  | Small Hydro | 0.75 | 2000-03-11 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Shivapur TLBC Hydro Electric Power Station |  |  | Small Hydro | 18 | 1992-11-29 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sholayar II Power House |  |  | Small Hydro | 25 | 1971-03-29 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Shri Dhanalaxmi Group Small Hydro Project |  |  | Small Hydro | 2 | 1997-11-24 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Siddapura Mini Hydel Power Station |  |  | Small Hydro | 12 | 2009-06-21 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sindhanooru Mini Hydel Station |  |  | Small Hydro | 0.8 | 2011-12-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Singatalur Mini Hydel Station |  |  | Small Hydro | 18 | 2012-08-30 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Singur Hydro Electric Station |  |  | Small Hydro | 15 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Sirwar Mini Hydro Power Station Project |  |  | Small Hydro | 1 | 1992-11-26 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sneha Renewable Energies Hydrel Project |  |  | Small Hydro | 0.9 | Pre-2000 | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Soham Phalguni Power Project 1 |  |  | Small Hydro | 22 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Soham Phalguni Power Project 2 |  |  | Small Hydro | 22 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Soham Phalguni Power Project 3 |  |  | Small Hydro | 15 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Somanamaradi Mini Hydel Power Station |  |  | Small Hydro | 13.8 | 2009-01-19 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Somasila Reservoir Left Flank Mini Hydel Scheme |  |  | Small Hydro | 10 | 2005-11-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Somasila Reservoir Left Flank Mini Hydel Scheme II |  |  | Small Hydro | 2 | 2008-10-01 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Somavathi Mini Hydel Station |  |  | Small Hydro | 6 | 2011-10-24 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Someshwara Mini Hydel Power Station |  |  | Small Hydro | 24.75 | 2005-07-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sonathi Mini Hydel Station |  |  | Small Hydro | 13.5 | 2011-12-25 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Jayalakshmi Power Corporation Small Hydro Project |  |  | Small Hydro | 4 | 2000-01-19 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sri Maruthi Power-gen (India) Small Hydro Project |  |  | Small Hydro | 6 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sriramadevarakatte Mini Hydel Station |  |  | Small Hydro | 1.5 | 2001-10-01 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sugur Mini Hydel Power Station |  |  | Small Hydro | 4.5 | 2004-04-03 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Suvarnamukhi Mini Hydel Station |  |  | Small Hydro | 2 | 2014-10-26 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Thirumala Hydro Power Project |  |  | Small Hydro | 2.4 | 2000-02-02 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Thirumurthy Mini Hydel Project |  |  | Small Hydro | 1.95 | 2000-03-20 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Trident Addanki Branch Canal Small Hydro Project |  |  | Small Hydro | 3 | 2001-02-28 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Trident Power Corporation Mini Hydro Project |  |  | Small Hydro | 4 | Pre-2000 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Trident Power Corporation Scheme I |  |  | Small Hydro | 2 | 1999-10-13 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Trident Power Corporation Scheme II |  |  | Small Hydro | 2 | 1999-08-26 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Tunga Mini Hydel Station |  |  | Small Hydro | 24 | 2014-06-13 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Tungabhadra Steel Products Ltd. |  |  | Small Hydro | 2.4 | 1999-09-17 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Ullunkal Small Hydro Electric Project |  |  | Small Hydro | 7 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Upper Kallar Small Hydro Electric Project |  |  | Small Hydro | 2 | Pre-2000 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Urumi - I Small Hydro Electric Project |  |  | Small Hydro | 3.75 | 2004-01-25 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Urumi - II Small Hydro Electric Project |  |  | Small Hydro | 2.4 | 2004-01-25 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Vaigai Hydro Power Project |  |  | Small Hydro | 6 | 1990-03-04 | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Varahi Tail Race - I Mini Hydel Power Station |  |  | Small Hydro | 22.5 | 2005-06-29 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Varahi Tail Race - II Mini Hydel Power Station |  |  | Small Hydro | 15 | 2009-04-17 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Vellathooval Small Hydro Electric Project |  |  | Small Hydro | 3.6 | 2026-08-21 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Vilangad Small Hydro Electric Project |  |  | Small Hydro | 7.5 | 2014-09-01 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Yeleru Reservoir Project Gap 2 Phase I |  |  | Small Hydro | 3 | 2000-01-17 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Yeleru Reservoir Project Gap 2 Phase II |  |  | Small Hydro | 1.5 | 2011-04-06 | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Yennehole -I Mini Hydel Station |  |  | Small Hydro | 15 | 2014-10-16 | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | kuthungal Small Hydro Electric Project |  |  | Small Hydro | 21 | 2001-06-01 | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_W | A P I Agro Madhya Pradesh Raisen 1.1 |  |  | Bio Power | 1.1 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | A. A. Energy Maharashtra Gadchiroli 10 30.04.2010 |  |  | Bio Power | 10 | 2010-04-30 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | ASN Industries Pvt Ltd Madhya Pradesh Ratlam 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Abellon Clean Energy Ltd Gujarat Ahmedabad 9.9 |  |  | Bio Power | 9.9 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Aditya Food Madhya Pradesh Bhopal 0.3 |  |  | Bio Power | 0.3 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Agrawal Vidut Ltd. Chhattisgarh Raipur 8.5 |  |  | Bio Power | 8.5 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ambika Solvex Pvt Ltd Madhya Pradesh Ratlam 1.2 |  |  | Bio Power | 1.2 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ambika Solvex Pvt Ltd Madhya Pradesh Ujjain 3 |  |  | Bio Power | 3 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Amreli Power Projects Pvt Ltd Gujarat Amreli 10 |  |  | Bio Power | 10 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Anant Urja Pvt Ltd Madhya Pradesh Narsimhapur 1.2 |  |  | Bio Power | 1.2 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ankur Scientific Energy Technologies Pvt Ltd Gujarat Vadodara 1.2 |  |  | Bio Power | 1.2 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Armstrong Energy Pvt. Ltd. Maharashtra Nashik 6 29.03.2008 |  |  | Bio Power | 6 | 2008-03-29 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Arya Energy Ltd Madhya Pradesh Bhopal 12 |  |  | Bio Power | 12 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Aryan Sugar Ltd. Maharashtra Solapur 10 2015-01-11 |  |  | Bio Power | 10 | 2015-01-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Ashok SSKL Maharashtra Ahilyanagar 15 2013-11-12 |  |  | Bio Power | 15 | 2013-11-12 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Babanroji Shinde Sugar and allied ind Maharashtra Solapur 25 2015-02-21 |  |  | Bio Power | 25 | 2015-02-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bajrang Agro Industries Pvt Ltd Madhya Pradesh Dhar 1.2 |  |  | Bio Power | 1.2 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Baliraja Sakhar Karkhana Ltd. Maharashtra Parbhani 15 2015-06-17 |  |  | Bio Power | 15 | 2015-06-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Baramati Agro Ltd Maharashtra Chhatrapati Sambhajinagar 14.75 2013-11-20 |  |  | Bio Power | 14.75 | 2013-11-20 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Baramati Agro Ltd. Maharashtra Pune 22 2010-04-24 |  |  | Bio Power | 22 | 2010-04-24 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhairavnath Sugar Works Ltd. Maharashtra Dharashiv 14.5 2012-05-02 |  |  | Bio Power | 14.5 | 2012-05-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhairavnath Sugar Works Ltd. Maharashtra Solapur 12 2012-02-28 |  |  | Bio Power | 12 | 2012-02-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhairavnath Sugar Works Ltd. Maharashtra Solapur 12.5 2015-03-26 |  |  | Bio Power | 12.5 | 2015-03-26 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhairavnath Sugar Works Ltd. Maharashtra Solapur 14.5 2014-11-29 |  |  | Bio Power | 14.5 | 2014-11-29 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhavnagar Biomass Power Projects Pvt Ltd Gujarat Bhavnagar 10 |  |  | Bio Power | 10 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhima SSKL Maharashtra Pune 19.5 2012-12-02 |  |  | Bio Power | 19.5 | 2012-12-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhima Sahakari Sakhar Karkhana Ltd. Maharashtra Solapur 25 2018-03-10 |  |  | Bio Power | 25 | 2018-03-10 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhimashankar SSKL Maharashtra Pune 19 2013-11-04 |  |  | Bio Power | 19 | 2013-11-04 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Chhatrapati Sambhaji Raje Sakhar Udyog Ltd. Maharashtra Chhatrapati Sambhajinaga |  |  | Bio Power | 6 | 2013-01-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Chopada SSKL Maharashtra Jalgaon 1.5 1996-05-28 |  |  | Bio Power | 1.5 | 1996-05-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Claris Lifesciences Ltd Gujarat Ahmedabad 4.2 |  |  | Bio Power | 4.2 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Daund Sugar Ltd. Maharashtra Pune 18 2009-12-27 |  |  | Bio Power | 18 | 2009-12-27 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Deepak Spinners Ltd Madhya Pradesh Guna 3 |  |  | Bio Power | 3 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Dnyaneshwar SSK Maharashtra Ahilyanagar 12 2007-07-31 |  |  | Bio Power | 12 | 2007-07-31 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dnyaneshwar Sahakari Sakhar Karkhana Ltd Maharashtra Ahilyanagar 19.5 2017-12-06 |  |  | Bio Power | 19.5 | 2017-12-06 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dr B. Ambedkar SSKL Maharashtra Dharashiv 16 2007-05-25 |  |  | Bio Power | 16 | 2007-05-25 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dudhaganga-Vedganga SSKL Maharashtra Kolhapur 20 2012-02-19 |  |  | Bio Power | 20 | 2012-02-19 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dwarkadhish Sakhar Karkhana Ltd. Maharashtra Nashik 13 2010-12-27 |  |  | Bio Power | 13 | 2010-12-27 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Ecofren Power Project Ltd. Chhattisgarh Durg 8 |  |  | Bio Power | 8 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | G M T Mining & Power Pvt.Ltd. Maharashtra Nagpur 10 |  |  | Bio Power | 10 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | GAPS Power & Infrastructure (P) Ltd. Maharashtra Chhatrapati Sambhajinagar 13 30 |  |  | Bio Power | 13 | 2008-11-30 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Gangakhed Sugars Energy Ltd. Maharashtra Parbhani 30 2011-10-01 |  |  | Bio Power | 30 | 2011-10-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Gangamai Industries & Constru Ltd Maharashtra Ahilyanagar 31 2011-12-05 |  |  | Bio Power | 31 | 2011-12-05 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Garg Casteels Pvt Ltd Gujarat Bhavnagar 2.2 |  |  | Bio Power | 2.2 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Gokul Mauli Sugars Ltd. Maharashtra Solapur 14.85 2018-03-01 |  |  | Bio Power | 14.85 | 2018-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Green Power Sugars Ltd. Maharashtra Satara 15 2015-04-03 |  |  | Bio Power | 15 | 2015-04-03 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Greta Energy Pvt. Ltd. Maharashtra Chandrapur 15 10.08.2012 |  |  | Bio Power | 15 | 2012-10-08 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Gujarat Energy Development Agency Gujarat Vadodara 0.5 |  |  | Bio Power | 0.5 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | H. R. Johnsons Madhya Pradesh Dewas 3.5 |  |  | Bio Power | 3.5 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | I.S.A. Power Pvt Ltd Chhattisgarh Dhamtari 8 |  |  | Bio Power | 8 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ind-Barath Energies (Maharashtra) Ltd. Maharashtra Nanded 20 08.01.2009 |  |  | Bio Power | 20 | 2009-08-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Indreshwar Sugar Mills Ltd. Maharashtra Solapur 12 2011-12-19 |  |  | Bio Power | 12 | 2011-12-19 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jagruti Sugar & Allied Industries Ltd Maharashtra Latur 13 2011-12-14 |  |  | Bio Power | 13 | 2011-12-14 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jai Hind Sugar Pvt. Ltd. Maharashtra Solapur 14.5 2015-12-18 |  |  | Bio Power | 14.5 | 2015-12-18 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jaishriram Sugar & Agro Products Ltd. Maharashtra Ahilyanagar 5 2014-12-20 |  |  | Bio Power | 5 | 2014-12-20 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jakraya Sugars Maharashtra Solapur 11 2011-07-01 |  |  | Bio Power | 11 | 2011-07-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jarandeshwar Sugar Mills Pvt. Ltd. Maharashtra Satara 30 2018-04-03 |  |  | Bio Power | 30 | 2018-04-03 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Javandnia Sugar Madhya Pradesh Narsimhapur 0.7 |  |  | Bio Power | 0.7 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Jawahar SSKL,Kolhapur Maharashtra Kolhapur 24 2001-11-23 |  |  | Bio Power | 24 | 2001-11-23 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jawahar SSSK Maharashtra Kolhapur 3 2007-12-10 |  |  | Bio Power | 3 | 2007-12-10 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jaymahesh Sugar Ltd Maharashtra Beed 30 2013-01-07 |  |  | Bio Power | 30 | 2013-01-07 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jaywant Sugars Ltd. Maharashtra Satara 10 2015-04-22 |  |  | Bio Power | 10 | 2015-04-22 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Junagadh Power Projects Pvt Ltd Gujarat Junagadh 10 |  |  | Bio Power | 10 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | KVK Bio-Energy Pvt Ltd. Chhattisgarh Janjgir-Champa 15 |  |  | Bio Power | 15 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kalchuri Trading and Investment Corporation Madhya Pradesh Jabalpur 1 |  |  | Bio Power | 1 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kalindi Power and Steel Ltd Chhattisgarh Mahasamund 8 |  |  | Bio Power | 8 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kancheshwar Sugar Ltd. Maharashtra Dharashiv 15 2015-02-11 |  |  | Bio Power | 15 | 2015-02-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Karmayogi Shankarraoji Patil SSKL Maharashtra Pune 15 2013-11-13 |  |  | Bio Power | 15 | 2013-11-13 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Kashap Sweetner Madhya Pradesh Ratlam 0.4 |  |  | Bio Power | 0.4 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Khandala Taluka Shetkari Sahakari Sakhar Karkhana Ltd. Maharashtra Satara 9.5 20 |  |  | Bio Power | 9.5 | 2018-04-04 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Khetan Chemicles Madhya Pradesh Dhar 2.1 |  |  | Bio Power | 2.1 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kisanveer Satara SSKL Maharashtra Satara 22 2012-02-14 |  |  | Bio Power | 22 | 2012-02-14 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Kranti SSKL Maharashtra Sangli 19.7 2010-02-16 |  |  | Bio Power | 19.7 | 2010-02-16 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Krishna Protiens Madhya Pradesh Jabalpur 0.7 |  |  | Bio Power | 0.7 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kukadi SSKL Maharashtra Ahilyanagar 12 2013-12-06 |  |  | Bio Power | 12 | 2013-12-06 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Kumbhi Kasari SSKL Maharashtra Kolhapur 17.5 2014-01-08 |  |  | Bio Power | 17.5 | 2014-01-08 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Kundan Namkeen Madhya Pradesh Bhopal 0.3 |  |  | Bio Power | 0.3 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Lanxess India Pvt Ltd Madhya Pradesh Jabalpur 3.9 |  |  | Bio Power | 3.9 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Logod Insulation Madhya Pradesh Dhar 0.6 |  |  | Bio Power | 0.6 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Lokmangal Mauli Maharashtra Dharashiv 30 2013-11-28 |  |  | Bio Power | 30 | 2013-11-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Lokmangal Sugar Ethanol & Cogen. Ind. Ltd. Maharashtra Solapur 31.5 2012-07-02 |  |  | Bio Power | 31.5 | 2012-07-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Loknete Baburao Patil Agro Industries Ltd. Maharashtra Solapur 19.5 2014-07-03 |  |  | Bio Power | 19.5 | 2014-07-03 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | M S M Energy Maharashtra Parbhani 10 15.11.2010 |  |  | Bio Power | 10 | 2010-11-15 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Maharashtra Shetkari Sugar Ltd. Maharashtra Parbhani 20 2014-02-16 |  |  | Bio Power | 20 | 2014-02-16 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Maharashtra Vidyut Nigam Ltd. Maharashtra Wardha 10 20.05.2013 |  |  | Bio Power | 10 | 2013-05-20 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Mahavir Energy and Coal Benefication Ltd. Chhattisgarh Raigarh 12 |  |  | Bio Power | 12 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Majalgaon SSKL Maharashtra Beed 22 2013-11-23 |  |  | Bio Power | 22 | 2013-11-23 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Malegaon SSKL Maharashtra Pune 21 2009-12-14 |  |  | Bio Power | 21 | 2009-12-14 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Manas Agro ind and infra Maharashtra Wardha 15 2013-11-28 |  |  | Bio Power | 15 | 2013-11-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Manjara SSKL Maharashtra Latur 18 2013-11-12 |  |  | Bio Power | 18 | 2013-11-12 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Matoshri Laxmi Sugar Co-Generation Industries Ltd. Maharashtra Solapur 12 2014-0 |  |  | Bio Power | 12 | 2014-03-12 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Mula SSK,Ahemadnagar Maharashtra Ahilyanagar 30 2006-12-11 |  |  | Bio Power | 30 | 2006-12-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Narmada Sugar Madhya Pradesh Barwani 3 |  |  | Bio Power | 3 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Natural Sugar & Allied Industries Ltd Maharashtra Dharashiv 13 2014-01-11 |  |  | Bio Power | 13 | 2014-01-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Neeraj Power Pvt Ltd. Chhattisgarh Raipur 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Nira Bhima SSKL Maharashtra Pune 18 2014-04-11 |  |  | Bio Power | 18 | 2014-04-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Olam Agro India Ltd. previously M/s Hemarus Technologies Ltd. Maharashtra Kolhap |  |  | Bio Power | 20 | 2010-11-23 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Orient Green Power (M/s. Padmasri Dr.D.Y.Patil Sahakari Sakhar Karkahna) Maharas |  |  | Bio Power | 20 | 2015-02-09 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Orient Green Power Ltd. Madhya Pradesh Jabalpur 10 |  |  | Bio Power | 10 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) (Waste to Energy) Goa N.A. 1.9400000000000002 |  |  | Bio Power | 1.94 | Pre-2000 | Goa | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) (Waste to Energy) Gujarat N.A. 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) (Waste to Energy) Madhya Pradesh N.A. 15.4 |  |  | Bio Power | 15.4 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) (Waste to Energy) Maharashtra N.A. 12.59 |  |  | Bio Power | 12.59 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Biomass & bagasse based cogen.] Chhattisgarh N |  |  | Bio Power | 144.89 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Biomass & bagasse based cogen.] Gujarat N.A. 1 |  |  | Bio Power | 17.3 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Biomass & bagasse based cogen.] Madhya Pradesh |  |  | Bio Power | 24.7 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Biomass & bagasse based cogen.] Maharashtra N. |  |  | Bio Power | 536.2 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Non-Bagasse based cogen.] Chhattisgarh N.A. 2. |  |  | Bio Power | 2.5 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Non-Bagasse based cogen.] Gujarat N.A. 12 |  |  | Bio Power | 12 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Non-Bagasse based cogen.] Madhya Pradesh N.A. |  |  | Bio Power | 14.85 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Non-Bagasse based cogen.] Maharashtra N.A. 16. |  |  | Bio Power | 16.4 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Waste to Energy (Off-grid)] Chhattisgarh N.A. |  |  | Bio Power | 10.83 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Waste to Energy (Off-grid)] Gujarat N.A. 455 |  |  | Bio Power | 45.05 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Waste to Energy (Off-grid)] Madhya Pradesh N.A |  |  | Bio Power | 32.71 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Others (districts not specified) [Waste to Energy (Off-grid)] Maharashtra N.A. 6 |  |  | Bio Power | 62.01 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Pandurang SSK (Phase I) Maharashtra Solapur 9 2006-06-22 |  |  | Bio Power | 9 | 2006-06-22 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Piyush Sugar And Power Pvt. Ltd. Maharashtra Ahilyanagar 6 2018-01-31 |  |  | Bio Power | 6 | 2018-01-31 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Pragya Energy Pvt Ltd Madhya Pradesh Katni 1.2 |  |  | Bio Power | 1.2 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Pravara Renewable Energy Ltd (Boot-M/s. Padmashri Vikhe Patil SSKL) Maharashtra |  |  | Bio Power | 30 | 2015-11-05 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Prigya Bekari Madhya Pradesh Ujjain 0.2 |  |  | Bio Power | 0.2 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Purna SSKL Maharashtra Hingoli 18 2011-06-27 |  |  | Bio Power | 18 | 2011-06-27 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Purti Sakhar Karkh. Ltd. Maharashtra Nagpur 22 2007-03-18 |  |  | Bio Power | 22 | 2007-03-18 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | R. R. Energy Ltd. Chhattisgarh Raigarh 15 |  |  | Bio Power | 15 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | R.K. Namkeen Madhya Pradesh Shajapur 0.3 |  |  | Bio Power | 0.3 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Rajarambapu Patil SSKL Maharashtra Sangli 28 2016-12-26 |  |  | Bio Power | 28 | 2016-12-26 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Rajarambapu Patil SSKL(W) Maharashtra Sangli 12 2006-11-11 |  |  | Bio Power | 12 | 2006-11-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Rake power Ltd Maharashtra Nagpur 10 25.07.2008 |  |  | Bio Power | 10 | 2008-07-25 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Ramkrishna Solvex Pvt Ltd Madhya Pradesh Anuppur 3 |  |  | Bio Power | 3 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ramnik Power & Alloys Pvt Ltd Madhya Pradesh Balaghat 6 |  |  | Bio Power | 6 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Raosahebdada Pawar Ghodganga Sahakari Sakhar Karkhana Ltd Maharashtra Pune 20.5 |  |  | Bio Power | 20.5 | 2018-08-16 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Real (N.R.I.) Power Pvt Ltd Chhattisgarh Bilaspur 7.5 |  |  | Bio Power | 7.5 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Rena Sahakari Sakhar Karkhana Ltd. Maharashtra Latur 12 2018-03-21 |  |  | Bio Power | 12 | 2018-03-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Rukmini Power and Steel Ltd. Chhattisgarh Raigarh 10 |  |  | Bio Power | 10 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | S. M. Shankarrao Mohite- Patil SSKL Maharashtra Solapur 33 2011-03-06 |  |  | Bio Power | 33 | 2011-03-06 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sadashivrao Mandlik Maharashtra Kolhapur 12 2012-02-09 |  |  | Bio Power | 12 | 2012-02-09 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sadguru Sri Sri Sakhar Karkhana Maharashtra Sangli 12 2014-03-21 |  |  | Bio Power | 12 | 2014-03-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sahakar Shiromani Vasantrao Kale SSKL Maharashtra Solapur 18 2016-01-16 |  |  | Bio Power | 18 | 2016-01-16 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sahakarmaharshi Bhausaheb Thorat SSKL Maharashtra Ahilyanagar 30 2016-03-28 |  |  | Bio Power | 30 | 2016-03-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Saikrupa SSKL Maharashtra Ahilyanagar 5.5 2010-10-22 |  |  | Bio Power | 5.5 | 2010-10-22 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Saikrupa Sakhar Karkhana Maharashtra Ahilyanagar 40 2011-03-31 |  |  | Bio Power | 40 | 2011-03-31 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Saisa Biscuits Madhya Pradesh Bhopal 0.4 |  |  | Bio Power | 0.4 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Samarth SSKL Maharashtra Jalna 18 2011-01-07 |  |  | Bio Power | 18 | 2011-01-07 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Samrudhi Sugars Ltd Maharashtra Jalna 12 2014-04-03 |  |  | Bio Power | 12 | 2014-04-03 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sanjivni(T) SSKL Maharashtra Ahilyanagar 12 2011-12-03 |  |  | Bio Power | 12 | 2011-12-03 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sant Muktai Sugar & Energy Ltd. Maharashtra Jalgaon 12 2017-01-21 |  |  | Bio Power | 12 | 2017-01-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sant Tukaram SSKL Maharashtra Pune 15 2016-06-13 |  |  | Bio Power | 15 | 2016-06-13 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sar Senapati Santaji Ghorpade Sugar Factory Ltd. Maharashtra Kolhapur 22 2014-12 |  |  | Bio Power | 22 | 2014-12-24 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Saradambika Power Plant Pvt. Ltd. Maharashtra Chandrapur 10 30.06.2008 |  |  | Bio Power | 10 | 2008-06-30 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sh. Chhatrapati Shahu Maharashtra Kolhapur 21.5 2008-03-15 |  |  | Bio Power | 21.5 | 2008-03-15 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shalivahana Projects Ltd. Maharashtra Yavatmal 10 17.01.2008 |  |  | Bio Power | 10 | 2008-01-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sharad SSKL Maharashtra Kolhapur 13 2018-01-20 |  |  | Bio Power | 13 | 2018-01-20 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sharad SSKL Maharashtra Kolhapur 2 2008-01-15 |  |  | Bio Power | 2 | 2008-01-15 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sharayu Agro Industries Ltd. Maharashtra Satara 30 2016-10-27 |  |  | Bio Power | 30 | 2016-10-27 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shivratna Udyog Ltd Maharashtra Solapur 12.5 2015-02-21 |  |  | Bio Power | 12.5 | 2015-02-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shraddha Energy & Infraprojects Pvt. Ltd. Maharashtra Jalna 12 2015-06-15 |  |  | Bio Power | 12 | 2015-06-15 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shree Renuka Sugars Ltd. (Boot- M/s Ajinkyatara SSKL) Maharashtra Satara 24 2012 |  |  | Bio Power | 24 | 2012-11-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shree Renuka Sugars Ltd. (Boot- M/s DBRK SSKL) Maharashtra Kolhapur 30 2011-06-0 |  |  | Bio Power | 30 | 2011-06-07 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shree Renuka Sugars Ltd. (Boot- M/s Mohanrao Shinde SSKL) Maharashtra Sangli 15 |  |  | Bio Power | 15 | 2010-03-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shree Siddheshwar Sahakari Sakhar Karkhana Ltd. Maharashtra Solapur 38 2017-12-2 |  |  | Bio Power | 38 | 2017-12-29 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shreenath Mhaskoba SSKL Maharashtra Pune 10 2012-01-20 |  |  | Bio Power | 10 | 2012-01-20 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Ambalika Sugars Pvt. Ltd. Maharashtra Ahilyanagar 38 2012-11-29 |  |  | Bio Power | 38 | 2012-11-29 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Chhatrapati Sahakari Sakhar Karkhana Ltd. Maharashtra Pune 18 2017-12-12 |  |  | Bio Power | 18 | 2017-12-12 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Datta Sakhar Karkhana (A unit of Dalmia Bharat Sugar and Ind. Ltd Maharasht |  |  | Bio Power | 23 | 2014-03-16 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Gurudatt Sugars Ltd. Maharashtra Kolhapur 15 2013-11-22 |  |  | Bio Power | 15 | 2013-11-22 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Pandurang SSKL (Phase II) Maharashtra Solapur 10 2012-02-22 |  |  | Bio Power | 10 | 2012-02-22 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Shankar SSKL Maharashtra Solapur 20 2011-03-23 |  |  | Bio Power | 20 | 2011-03-23 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Vithal SSKL Maharashtra Solapur 29.8 2010-05-27 |  |  | Bio Power | 29.8 | 2010-05-27 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shriram Jawahar Shetkari Sahakari Sakhar Udyog Maharashtra Satara 1.5 2010-05-09 |  |  | Bio Power | 1.5 | 2010-05-09 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shudha Agro Oil and Chemical Industries Ltd Chhattisgarh Bilaspur 9.9 |  |  | Bio Power | 9.9 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Siddhanath Sugar Mills Ltd. Maharashtra Solapur 26 2010-12-15 |  |  | Bio Power | 26 | 2010-12-15 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sinewave Power Ltd. Maharashtra Sangli 10 23.01.2014 |  |  | Bio Power | 10 | 2014-01-23 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sitaram Maharaj S K Maharashtra Solapur 10 2013-12-11 |  |  | Bio Power | 10 | 2013-12-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Someshwar SSKL Maharashtra Pune 18 2010-05-21 |  |  | Bio Power | 18 | 2010-05-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sonhira SSKL Maharashtra Sangli 22 2011-04-29 |  |  | Bio Power | 22 | 2011-04-29 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | South Asian Agro Industries Ltd Chhattisgarh Raipur 9.8 |  |  | Bio Power | 9.8 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Spark Green Energy (Ahmednagar) P. Ltd Maharashtra Ahilyanagar 25 |  |  | Bio Power | 25 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sri Guruprabha Power Ltd Maharashtra Jalgaon 10 30.11.2009 |  |  | Bio Power | 10 | 2009-11-30 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sri Panchjanya Power Pvt. Ltd. Maharashtra Hingoli 10 09.09.2010 |  |  | Bio Power | 10 | 2010-09-09 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Swaraj India Agro Ltd. Maharashtra Satara 19.5 2015-11-21 |  |  | Bio Power | 19.5 | 2015-11-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Team Ferro Alloys Pvt. Ltd. Maharashtra Gondia 8 30.12.2005 |  |  | Bio Power | 8 | 2005-12-30 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | The Saswad Mali Sugar Factory Ltd Maharashtra Solapur 14.8 2013-12-19 |  |  | Bio Power | 14.8 | 2013-12-19 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Udagiri Sugar & Power Ltd. Maharashtra Sangli 14 2013-03-03 |  |  | Bio Power | 14 | 2013-03-03 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Urjankur Shree Datta Co.Ltd Maharashtra Kolhapur 36 2013-04-01 |  |  | Bio Power | 36 | 2013-04-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Urjankur Shree Tatyasaheb Kore Power Maharashtra Kolhapur 44 2013-04-01 |  |  | Bio Power | 44 | 2013-04-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Utech Sugar Ltd. Maharashtra Ahilyanagar 14.9 2017-12-28 |  |  | Bio Power | 14.9 | 2017-12-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Utopian Sugars Ltd. Maharashtra Solapur 14.8 2014-12-02 |  |  | Bio Power | 14.8 | 2014-12-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | VARAM Bio-Energy Pvt. Ltd. Maharashtra Bhandara 10 18.02.2009 |  |  | Bio Power | 10 | 2009-02-18 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vaidhyanath SSKL Maharashtra Beed 21 2013-02-08 |  |  | Bio Power | 21 | 2013-02-08 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vandana Vidhyt Ltd Chhattisgarh Bilaspur 8 |  |  | Bio Power | 8 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Vasantraodada Patil SSKL Maharashtra Nashik 17 2012-02-18 |  |  | Bio Power | 17 | 2012-02-18 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vayunandana Power Ltd. Maharashtra Gadchiroli 10 09.12.2010 |  |  | Bio Power | 10 | 2010-09-12 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vighnahar SSK,Pune Maharashtra Pune 18 2005-12-23 |  |  | Bio Power | 18 | 2005-12-23 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vikas SSKL Maharashtra Latur 18 2011-02-15 |  |  | Bio Power | 18 | 2011-02-15 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vishwasrao Naik SSKL Maharashtra Sangli 15 2012-12-28 |  |  | Bio Power | 15 | 2012-12-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vitthal Refined Sugars Ltd. Maharashtra Solapur 26 2017-12-01 |  |  | Bio Power | 26 | 2017-12-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vitthal Sugars Manufacturing Limited Maharashtra Solapur 12 2011-03-21 |  |  | Bio Power | 12 | 2011-03-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vitthalrao Shinde SSKL Maharashtra Solapur 38 2011-03-11 |  |  | Bio Power | 38 | 2011-03-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Yash Agro Energy Ltd. Maharashtra Chandrapur 8 |  |  | Bio Power | 8 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Yashwantrao Mohite Krishna SSKL Maharashtra Satara 16 2010-12-14 |  |  | Bio Power | 16 | 2010-12-14 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Yedeshwari Agro Products Ltd Maharashtra Beed 10 2014-01-17 |  |  | Bio Power | 10 | 2014-01-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Akaltara TPS |  | Subcritical | Coal | 1800 | 2013-08-13 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Akrimota TPS |  | Subcritical | Coal | 250 | 2005-03-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Amaravati TPS |  | Subcritical | Coal | 1350 | 2013-03-25 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Amarkantak TPS |  | Subcritical | Coal | 210 | 2008-06-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Anuppur TPP |  | Subcritical | Coal | 1250 | 2015-04-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Avantha Bhandar TPS |  | Subcritical | Coal | 600 | 2014-03-31 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Balco Korba TPP |  | Subcritical | Coal | 600 | 2015-07-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bandakhar TPP |  | Subcritical | Coal | 300 | 2015-06-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Baradarha TPS |  | Subcritical | Coal | 1200 | 2014-02-23 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bela TPS |  | Subcritical | Coal | 270 | 2013-03-20 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhavnagar TPP |  | Subcritical | Coal | 500 | 2016-05-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhilai TPS |  | Subcritical | Coal | 500 | 2008-04-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhusawal TPS |  | Subcritical | Coal | 1870 | 1982-09-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bina TPS |  | Subcritical | Coal | 500 | 2012-08-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Binjkote TPP |  | Subcritical | Coal | 600 | 2017-04-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Butibori TPP |  | Subcritical | Coal | 600 | 2012-08-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Chakabura TPP |  | Subcritical | Coal | 30 | 2014-03-28 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Chandrapur (Maharashtra) STPS |  | Subcritical | Coal | 2920 | 1985-05-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dahanu TPS |  | Subcritical | Coal | 500 | 1995-01-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dhariwal TPP |  | Subcritical | Coal | 600 | 2013-11-03 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dr. Shyama Prasad Mukherjee TPS |  | Subcritical | Coal | 500 | 2007-03-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | EMCO Energy Warora TPS/ GMR Warora |  | Subcritical | Coal | 600 | 2013-02-07 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Gadarwara STPS |  | Supercritical | Coal | 1600 | 2019-03-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Gandhi Nagar TPS |  | Subcritical | Coal | 630 | 1990-03-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Gupta Energy or GEPL TPP |  | Subcritical | Coal | 120 | 2012-05-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | JSW Ratnagiri TPP |  | Subcritical | Coal | 300 | 2010-08-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Jaypee Nigrie STPP |  | Supercritical | Coal | 1320 | 2014-08-29 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kasaipalli TPP |  | Subcritical | Coal | 270 | 2011-12-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Khaparkheda TPS |  | Subcritical | Coal | 1340 | 1989-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Khargone Super Critical Power Plant |  | Ultra-Supercritical | Coal | 1320 | 2019-09-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Koradi TPS |  | Subcritical | Coal | 2190 | 1982-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Korba STPS |  | Subcritical | Coal | 2600 | 1983-03-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Korba West or Hasdeo TPS |  | Subcritical | Coal | 1340 | 1983-03-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kutchh Lignite TPS |  | Subcritical | Coal | 150 | 1997-03-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Lara STPS |  | Supercritical | Coal | 1600 | 2018-03-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Mahan TPP |  | Subcritical | Coal | 1200 | 2013-02-24 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Marwa TPS |  | Subcritical | Coal | 1000 | 2014-03-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Mauda TPS |  | Subcritical | Coal | 2320 | 2012-04-19 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Mihan TPS |  | Subcritical | Coal | 246 | 2012-02-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Mundra TPS |  | Subcritical | Coal | 4620 | 2009-08-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Mundra UMTPP |  | Supercritical | Coal | 4000 | 2012-02-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Nasik TPS |  | Subcritical | Coal | 630 | 1979-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Nawapara TPP |  | Subcritical | Coal | 600 | 2016-08-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Niwari TPP |  | Subcritical | Coal | 90 | 2013-12-10 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | O.P. Jindal or Tamnar I TPS/ Raigarh TPP |  | Subcritical | Coal | 1000 | 2007-12-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Paras TPS |  | Subcritical | Coal | 500 | 2007-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Parli TPS |  | Subcritical | Coal | 750 | 2007-02-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Pathadi TPP |  | Subcritical | Coal | 600 | 2009-06-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Raikheda TPP |  | Supercritical | Coal | 1370 | 2015-03-02 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ratija TPS |  | Subcritical | Coal | 100 | 2013-02-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | SVPL TPP |  | Subcritical | Coal | 63 | 2011-12-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sabarmati (D-F Stations) TPP |  | Subcritical | Coal | 362 | 1978-10-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Salaya TPP/Essar Power Gujarat |  | Subcritical | Coal | 1200 | 2012-02-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Sanjay Gandhi TPS |  | Subcritical | Coal | 1340 | 1993-03-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sasan UMTPP |  | Supercritical | Coal | 3960 | 2013-05-30 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Satpura TPS |  | Subcritical | Coal | 500 | 2013-03-22 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Seioni TPP or Jhabua Power Seoni TPP |  | Subcritical | Coal | 600 | 2016-03-22 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Shirpur TPP |  | Subcritical | Coal | 300 | 2018-09-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Shri Singhaji or Malwa TPP |  | Subcritical | Coal | 2520 | 2013-10-18 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sikka TPS |  | Subcritical | Coal | 500 | 2015-03-29 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Singhitarai TPP |  | Supercritical | Coal | 600 | 2025-07-19 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sipat STPS |  | Supercritical | Coal | 2980 | 2007-05-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Solapur Super critical Thermal Power Plant |  | Supercritical | Coal | 1320 | 2017-04-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Surat (Lignite) TPS |  | Subcritical | Coal | 500 | 1999-11-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Tamnar TPP |  | Subcritical | Coal | 2400 | 2014-03-10 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Tirora TPS |  | Supercritical | Coal | 3300 | 2012-09-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Trombay TPS |  | Subcritical | Coal | 750 | 1984-01-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Uchpinda TPP |  | Subcritical | Coal | 1440 | 2015-11-01 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ukai TPS |  | Subcritical | Coal | 1110 | 1979-01-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Vindhyachal STPS |  | Subcritical | Coal | 4760 | 1987-10-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Wanakbori TPS |  | Subcritical | Coal | 2270 | 1982-03-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Wardha Warora TPP |  | Subcritical | Coal | 540 | 2010-06-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bansagar Tons I Hydroelectric Power Project |  |  | Hydro | 315 | 1991-09-27 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bansagar Tons II Hydroelectric Power Project |  |  | Hydro | 30 | 2002-02-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bansagar Tons III Hydroelectric Power Project |  |  | Hydro | 60 | 2000-07-18 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bargi Hydroelectric Power Project |  |  | Hydro | 90 | 1988-06-03 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhandardhara II Hydroelectric Power Project |  |  | Hydro | 34 | 1999-05-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhira Hydroelectric Power Project |  |  | Hydro | 150 | 1927-08-10 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhira PSS (Pump Storage Scheme) Hydroelectric Power Project |  |  | Hydro | 150 | 1927-06-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhira Tail Race Hydroelectric Power Project |  |  | Hydro | 80 | 1987-09-13 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhivpuri Hydroelectric Power Project |  |  | Hydro | 75 | 1997-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Gandhi Sagar Hydroelectric Power Project |  |  | Hydro | 115 | 1960-11-19 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ghatgarh Hydroelectric Power Project |  |  | Hydro | 250 | 2008-01-07 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Hasdeobango Hydroelectric Power Project |  |  | Hydro | 120 | 1994-03-21 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Indira Sagar Hydroelectric Power Project |  |  | Hydro | 1000 | 2004-01-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kadana Hydroelectric Power Project |  |  | Hydro | 240 | 1990-01-09 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Khopoli Hydroelectric Power Project |  |  | Hydro | 72 | 2001-08-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Koyna Dam Power House |  |  | Hydro | 36 | 1980-10-03 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Koyna I,II,III & IV Hydroelectric Power Project |  |  | Hydro | 1920 | 1962-05-16 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Madhikheda Hydroelectric Power Project |  |  | Hydro | 60 | 2006-08-28 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Omkareshwar Hydroelectric Power Project |  |  | Hydro | 520 | 2007-11-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Pench Hydroelectric Power Project |  |  | Hydro | 160 | 1986-09-09 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Rajghat Hydroelectric Power Project |  |  | Hydro | 45 | 1999-09-29 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sardar Sarovar Canal Head Power House (CHPH) |  |  | Hydro | 250 | 2004-05-03 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Sardar Sarovar River Bed Power House (RBPH) |  |  | Hydro | 1200 | 2005-02-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Tillari Hydroelectric Power Project |  |  | Hydro | 60 | 1986-10-10 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Ukai Hydroelectric Power Project |  |  | Hydro | 300 | 1974-07-08 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Vaitarna Hydroelectric Power Project |  |  | Hydro | 60 | 1976-06-26 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Kakrapar Atomic Power Station |  |  | Nuclear | 1840 | 1993-05-06 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Tarapur Atomic Power Station |  |  | Nuclear | 1400 | 1969-10-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | DGEN Mega Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 1200 | 2014-11-26 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Dhuvaran Gas Based Combined Cycle Power Plant |  |  | Oil & Gas | 594.72 | 2004-01-28 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Essar Hazira Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 515 | 1997-10-02 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Hazira GSEG Gas Combined Cycle Gas Turbine Power Plant Ext. |  |  | Oil & Gas | 351 | 2012-02-18 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Jhanor-Gandhar Gas Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 657.39 | 1994-03-17 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Kawas Gas Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 656.2 | 1992-03-22 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Pipavav Combined Cycle Gas Turbine Power Plant |  |  | Oil & Gas | 702 | 2013-03-22 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Ratnagiri Gas and Power Private Ltd. |  |  | Oil & Gas | 1967.08 | 1998-11-12 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | SUGEN Combined Cycle Power Plant |  |  | Oil & Gas | 1147.5 | 2009-02-04 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Trombay Unit 7 Gas Power Plant |  |  | Oil & Gas | 180 | 1993-07-29 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | UNOSUGEN Combined Cycle Power Plant |  |  | Oil & Gas | 382.5 | 2013-01-20 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Uran Gas Combined Cycle Gas Turbine |  |  | Oil & Gas | 672 | 1985-06-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Utran Gas Based Power Station Combined Cycle Power Plant |  |  | Oil & Gas | 374 | 2009-07-10 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Ambai Hydro Electric Project |  |  | Small Hydro | 4 | 2012-06-30 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Amhata Hydro Energy Project |  |  | Small Hydro | 3.8 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ascent Hydro Projects |  |  | Small Hydro | 2.2 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bansagar Hydel Power Station Phase IV |  |  | Small Hydro | 20 | 2006-08-20 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhandardara Hydro Electric Project |  |  | Small Hydro | 12 | 2001-08-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhatghar Hydro Electric Plant |  |  | Small Hydro | 16 | 1977-08-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhatsa Hydro Electric Plant (Bhatsa HEP) |  |  | Small Hydro | 15 | 1991-09-28 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhivpuri Mini Hydel Project |  |  | Small Hydro | 3 | 1997-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Birsinghpur Hydro Electric Plant |  |  | Small Hydro | 20 | 1991-11-01 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Chhattisgarh Small Hydro project Bunched |  |  | Small Hydro | 24.9 | 2025-09-30 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Chitri Hydro Electric Plant |  |  | Small Hydro | 2 | 2010-12-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | DLZ Group Hydro Project (Maharashtra) |  |  | Small Hydro | 4.9 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Daman Ganga I & II Small Hydro Power Project |  |  | Small Hydro | 5.6 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Darana Hydro Electric Plant |  |  | Small Hydro | 4.9 | 2010-12-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Deoghar Hydro Electric Project |  |  | Small Hydro | 1.5 | 2010-04-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dhom Balkawadi Hydro Electric Plant |  |  | Small Hydro | 4 | 2010-06-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dhom Hydro Electric Plant |  |  | Small Hydro | 2 | 1992-03-31 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dimbhe Hydro Electric Plant |  |  | Small Hydro | 5 | 1998-10-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dolvahal Hydro Electric Plant |  |  | Small Hydro | 2 | 2007-12-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Dudhganga Hydro Electric Plant |  |  | Small Hydro | 24 | 2000-02-27 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Gangrel Mini Hydel Project |  |  | Small Hydro | 1.2 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Gangrel Hydro Electric Power Station |  |  | Small Hydro | 10 | 2004-04-02 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Gautami Godavari Hydro Electric Plant |  |  | Small Hydro | 1.2 | 2013-03-12 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Ghatprabha Hydro Electric Plant |  |  | Small Hydro | 8 | 2013-04-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Govt. of Maharashtra Small Hydro Project |  |  | Small Hydro | 3 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Gujarat Electricity Board (GEB) Project 1 |  |  | Small Hydro | 5 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Gujarat Electricity Board (GEB) Project 2 |  |  | Small Hydro | 3 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Gullu Small Hydro Electric Project |  |  | Small Hydro | 24 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Indira Sagar Project |  |  | Small Hydro | 15 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Jatashankari Hydro Power Project |  |  | Small Hydro | 7 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kachchh Branch Canal Small Hydro Project |  |  | Small Hydro | 6.66 | 2020-02-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Kadvi Hydro Electric Plant |  |  | Small Hydro | 1.5 | 2011-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Kanher Hydro Electric Plant |  |  | Small Hydro | 4 | 1991-08-18 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Karanjwan Hydro Electric Plant |  |  | Small Hydro | 3 | 2001-10-26 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Kasari Hydro Electric Plant |  |  | Small Hydro | 2.5 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Khadakvasla Dam Foot Hydro Electric Project |  |  | Small Hydro | 0.7 | 2012-06-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Khadakwasla Hydro Electric Plant |  |  | Small Hydro | 8 | 1991-03-31 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Khadakwasla II Hydro Electric Plant |  |  | Small Hydro | 8 | 1991-08-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Khodshi Power Projects HEP |  |  | Small Hydro | 4.9 | 2013-12-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Konal Hydro Power Project |  |  | Small Hydro | 10 | 2010-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Korba Mini Hydel Power Plant |  |  | Small Hydro | 1.7 | 2003-01-12 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Kumbhi Hydro Electric Plant |  |  | Small Hydro | 2.5 | 2011-02-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 1 |  |  | Small Hydro | 4 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 2 |  |  | Small Hydro | 16 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 3 |  |  | Small Hydro | 9 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 4 |  |  | Small Hydro | 4 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MAHAGENCO Small Hydro Station 5 |  |  | Small Hydro | 2 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Mahan III Hydro Power Project |  |  | Small Hydro | 24.75 | Pre-2000 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Majalgaon Small Hydro Project |  |  | Small Hydro | 1.5 | 2008-01-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Majalgaon Small Hydro Project |  |  | Small Hydro | 0.75 | 2007-12-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Manikdoh Hydro Electric Plant |  |  | Small Hydro | 6 | 1995-11-22 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Miyagam Branch Canal Small Hydro Project |  |  | Small Hydro | 1.5 | 2018-05-15 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Nilwande Low Level Hydro Electric Project |  |  | Small Hydro | 7 | 2012-06-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Nira Deoghar Hydro Electric Project |  |  | Small Hydro | 6 | 2009-11-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Nira Deoghar Hydro Electric Project II |  |  | Small Hydro | 10 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | OREVA Energy Pvt. Ltd. Small Hydro Project |  |  | Small Hydro | 1 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Paithan Small Hydro Project |  |  | Small Hydro | 12 | 1984-11-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Panam Canal Small Hydro Power Project |  |  | Small Hydro | 2 | 1994-03-24 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Patgaon Hydro Electric Project |  |  | Small Hydro | 2.5 | 2011-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Pawana Hydro Electric Plant |  |  | Small Hydro | 10 | 1988-06-11 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Pench Kamathi Khari LBC Hydro Electric Project |  |  | Small Hydro | 4.4 | 2011-12-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Radhanagari HEP |  |  | Small Hydro | 4.8 | 1952-12-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Rani Avanti Bai Sagar Project |  |  | Small Hydro | 10 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | SAS Hydel Power Projects |  |  | Small Hydro | 9.75 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sabarmati Hydro Project |  |  | Small Hydro | 4 | Pre-2000 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Saurashtra Branch Canal Small Hydro Project I |  |  | Small Hydro | 15 | 2018-12-01 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Saurashtra Branch Canal Small Hydro Project II |  |  | Small Hydro | 15 | 2019-02-27 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Shivaji Mohite Group Hydro Project |  |  | Small Hydro | 3.5 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sikasar Hydel Power Station |  |  | Small Hydro | 7 | 2006-09-03 | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sirmour Small Hydro Power Project |  |  | Small Hydro | 24 | Pre-2000 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sonawade Hydro Electric Plant |  |  | Small Hydro | 4 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sterling & Wilson Group Hydro Project |  |  | Small Hydro | 2.5 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Surya Hydro Electric Plant (Surya HEP) |  |  | Small Hydro | 6 | 1999-01-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Surya Left Bank Canal Hydro Electric Plant (Surya LBC HEP) |  |  | Small Hydro | 0.75 | 1998-06-04 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Tawa Hydro Electric Generation Power Plant |  |  | Small Hydro | 13.5 | 1997-01-21 | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Tembhu Barej Hydro Electric Project |  |  | Small Hydro | 4.5 | 2010-12-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Terwanmedhe Hydro Electric Plant (Terwanmedhe HEP) |  |  | Small Hydro | 0.2 | 1998-03-31 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Ujjani Hydro Electric Plant |  |  | Small Hydro | 12 | 1994-05-02 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vadodara Branch Canal Small Hydro Project I |  |  | Small Hydro | 1.05 | 2019-06-20 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Vadodara Branch Canal Small Hydro Project II |  |  | Small Hydro | 0.7 | 2019-02-19 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Vadodara Branch Canal Small Hydro Project III |  |  | Small Hydro | 0.4 | 2018-12-21 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Vadodara Branch Canal Small Hydro Project IV |  |  | Small Hydro | 0.4 | 2018-12-24 | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Vaitarna Dam Foot Hydro Electric Plant |  |  | Small Hydro | 1.5 | 1987-09-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vajra Fall Hydro Electric Project |  |  | Small Hydro | 3 | 2002-12-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vajra Fall Hydro Electric Project II |  |  | Small Hydro | 3 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Veer Nira LBC Hydro Electric Plant |  |  | Small Hydro | 4.8 | 2012-03-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Vir Hydro Electric Plant |  |  | Small Hydro | 9 | 1975-02-17 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Wan Small Hydro Project |  |  | Small Hydro | 1.5 | 2007-12-21 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Warana Group Small Hydro Project 1 |  |  | Small Hydro | 2 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Warana Group Small Hydro Project 2 |  |  | Small Hydro | 2.5 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Warana Group Small Hydro Project 3 |  |  | Small Hydro | 2.5 | Pre-2000 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Warana Hydro Electric Plant |  |  | Small Hydro | 16 | 1999-09-01 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Yeldari Small Hydro Project |  |  | Small Hydro | 22.5 | 1968-05-10 | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Yewateshwar Hydro Electric Plant |  |  | Small Hydro | 0.07 | 1998-09-02 | Maharashtra | India_Electricity_Infrastructure.xlsx

## Planned_Generation
Country | Node | Project_Name | Technology_Code | Technology_Name | Fuel | Capacity_MW | Expected_COD | Status | Developer | Source
Bangladesh | BD | Project / Plant | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rooppur Nuclear Power Plant Unit-1 | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rooppur Nuclear Power Plant Unit-2 | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Patuakhali 1320 MW Coal PP (RNPL) | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Rupsha 800 MW CCPP | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Sonagazi 75 MW Solar Plant (EGCB) | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Moulvibazar 10 MW Solar Power Plant | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Additional LNG-based Gas Power (Multiple) | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Large-scale Solar Expansion | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Offshore Wind (Pilot) | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Ammonia Co-firing (Coal Plants) | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Hydrogen Co-firing (Gas Plants) | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | CCS on Gas Power Plants | [6 empty] | Bangladesh_Power_Sector.xlsx
Bangladesh | BD | Hydrogen-fired Power Plants | [6 empty] | Bangladesh_Power_Sector.xlsx
Bhutan | BT | Project / Plant | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Punatsangchhu-II HP (PHP-II) — Full Commissioning | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Kholongchhu Hydropower Project | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Bunakha Reservoir Hydropower Project | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Chamkharchhu I Hydropower Project | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Dorjilung Hydropower Project | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Nikachhu HP — Full Output Stabilization | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Gelephu Solar Power Plant | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | DSP Solar Expansion | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Rooftop Solar Program (National) | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Mini/Micro Hydel Expansion | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Shakti Hydropower Project (proposed) | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Bhutan | BT | Amochhu Reservoir Project | [6 empty] | Bhutan_Power_Infrastructure.xlsx
Nepal | NP | Project/Plant | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Middle Bhotekoshi HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Trishuli 3B HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tanahun HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rahughat HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tamakoshi-V HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Modi 'A' HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Modi HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Kulekhani III HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Trishuli 3A HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Budi Gandaki HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Chainpur HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rolwaling HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tamakoshi V HEP (Tamkoshi Khola) | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Modi (UMAHEP) | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Modi (UMHEP) | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Solar Plants (63 projects via competitive bidding) | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rahughat HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Trishuli 3A | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khani Khola-1 HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Baleph A HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khani Khola (Dolakha) HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Lower Irkhuwa HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Badi Gad HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Rawa Khola HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Phalankhu Khola HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Tadi HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Upper Mailung A HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Tadi Khola HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Middle Midim HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Nepal | NP | Khorounga Khola HEP | [6 empty] | Nepal_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Project / Plant | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sobadhanavi NG Combined Cycle (1st CCY GT) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale, various zones) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (Kollonawa, 1st utility-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sobadhanavi NG CCY Steam Turbine (1st CCY ST) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | 2nd NG CCY GT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS Kollonawa (100 MW / 100 MWh) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda A extension (life ext.) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda B extension | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Barge Plant extension | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa GT-07 RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | 2nd NG CCY Steam Turbine | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG Internal Combustion Engine (200 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS Southern Region (100 MW / 400 MWh) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (100 MW / 400 MWh, 3rd unit) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kelanitissa New GT (gas turbine) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS Western (50 MW / 50 MWh) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG Gas Turbine (100 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mini Hydro | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Biomass | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (100 MW / 400 MWh, 5th unit) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda A RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sapugaskanda B RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Barge Plant RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (200 MW / 800 MWh) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | KCCP1 (Kelanitissa CCY-1) RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | KCCP2 (Kelanitissa CCY-2) RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Uthuru Janani RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Maha Oya Pumped Storage Power Plant (PSPP) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 Gas Turbine (300 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV (grid-scale) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind (various) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Westcoast CCY RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT additions (2036) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT (2037) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV 2036–2037 | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 IC Engine (200 MW, 2038) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV 2038 | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind 2038 | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | India–Sri Lanka HVDC Interconnection (500 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT (200 MW, 2039) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV 2039–2043 | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Wind 2039–2042 | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT additions 2040–2043 | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Offshore Wind (500 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Nuclear Power Plant (600 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | NG/H2 GT (200 MW, 2044) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Solar PV 2044 | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | BESS (50 MW / 200 MWh, 2044) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Lakvijaya Units 2 & 3 RETIREMENT | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Siyambalanduwa Solar (100 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Ridiyagama Solar (100 MW, floating/ground) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Valaichenai Solar (100 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sampur Phase I (50 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Sampur Phase II (70 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Trincomalee Solar I (100 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Trincomalee Solar II (100 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kilinochchi Solar I (50 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kilinochchi Solar II (100 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mannar Extension Wind (50 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mannar Phase II Wind (250 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Mullikulam Wind (100 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Kalpitiya Wind (120 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Pooneryn Wind (234 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Veravil Wind (200 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Sri Lanka | LK | Karachchi Wind (120 MW) | [6 empty] | SriLanka_Electricity_Infrastructure.xlsx
Maldives | MV | Project / Plant Name | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | POISED — Remaining Solar PV + BESS (126 outer islands) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ASPIRE — Existing PPA installations | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ARISE — Solar PV + BESS (hybridization + floating Addu) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ASSURE — BESS + EMS + Solar IPPs (20 outer islands) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ASSURE — Pilot Wind Power | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ASSURE — Pilot Ocean Energy | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | ASSURE — Pilot Solar Desalination | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Rooftop PV — Greater Male' Households (net-metering) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Rooftop PV — Addu City and Other Islands (net-metering) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | WTE Plant — K. Thilafushi | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | WTE Plant — Addu City | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | WTE Plant — R. Vandhoo | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Rooftop PV — Gulhifalhu/Thilafushi Commercial Buildings (PPA) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Wind Turbines — Gulhifalhu / Thilafushi | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Floating Solar PV + BESS — Greater Male' Region | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Solar PV Hybrid Plants — Outer Inhabited Islands (additional) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Solar PV — Resort and Industrial Islands | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | LNG Power Plant — Gulhifalhu (feasibility study recommended) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Rooftop PV under ASSURE — Greater Male' (Magey Solar Program) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Green Hydrogen Pilot | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Marine Renewable Energy Road Map + Pilots | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | Solar PV — Solar Street Lights + Island Councils Program (expanded) | [6 empty] | Maldives_Energy_Infrastructure.xlsx
Maldives | MV | EV Charging Infrastructure | [6 empty] | Maldives_Energy_Infrastructure.xlsx
India | IN_E | Hiranmaye TPP |  |  | Coal |  |  | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Kandarei TPP |  |  | Coal |  |  | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Kodarma TPP |  |  | Coal |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Lanco Babandh TPP |  |  | Coal |  |  | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Malibrahmani Power Station |  |  | Coal |  |  | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Matrishri Usha Jayaswal TPP |  |  | Coal |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | New NabiNagar TPP (Majhiyan) |  |  | Coal |  |  | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Patratu TPS |  |  | Coal |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Raghunathpur TPS |  |  | Coal |  |  | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Sagardighi TPS |  |  | Coal |  |  | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Siriya TPS or Banka Power Project |  |  | Coal |  |  | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Super Critical Buxar Thermal Power Plant |  |  | Coal |  |  | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | Talabira TPP |  |  | Coal |  |  | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Talcher or Kaniha Talcher STPS |  |  | Coal |  |  | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | Tori TPP |  |  | Coal |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | Bhasmey Hydro Power Project |  |  | Hydro |  |  | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Panan Hydro Power Project |  |  | Hydro |  |  | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Rammam III Hydro Power Project |  |  | Hydro |  |  | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | Rangit-II Hydro Power Project |  |  | Hydro |  |  | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Rangit-IV Hydro Power Project |  |  | Hydro |  |  | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Teesta- VI Hydro Power Project |  |  | Hydro |  |  | Sikkim | India_Electricity_Infrastructure.xlsx
India | IN_E | Damodar Valley Corporation (DVC) Jharkhand 10.0 |  |  | Solar |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | GVREL Jharkhand 155.0 |  |  | Solar |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | GVREL Jharkhand 80.0 |  |  | Solar |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | GVREL West Bengal 75.0 |  |  | Solar |  |  | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | NHPC Limited Odisha 40.0 |  |  | Solar |  |  | Odisha | India_Electricity_Infrastructure.xlsx
India | IN_E | SECI Jharkhand 100.0 |  |  | Solar |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | SJVN GREEN ENERGY LIMITED Bihar 75.0 |  |  | Solar |  |  | Bihar | India_Electricity_Infrastructure.xlsx
India | IN_E | SPD Jharkhand 8.0 |  |  | Solar |  |  | Jharkhand | India_Electricity_Infrastructure.xlsx
India | IN_E | SPD West Bengal 10.0 |  |  | Solar |  |  | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_E | SPD West Bengal 14.0 |  |  | Solar |  |  | West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_NE | Dibang Hydro Power Project |  |  | Hydro |  |  | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | HEO Hydro Electric Project |  |  | Hydro |  |  | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Lower Kopili Hydro Power Project |  |  | Hydro |  |  | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | Subansiri Lower Hydro Power Project |  |  | Hydro |  |  | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | Tato-I Hydro Electric Project |  |  | Hydro |  |  | Arunachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_NE | SJVN GREEN ENERGY LIMITED Assam 50.0 |  |  | Solar |  |  | Assam | India_Electricity_Infrastructure.xlsx
India | IN_NE | SJVN GREEN ENERGY LIMITED Assam 70.0 |  |  | Solar |  |  | Assam | India_Electricity_Infrastructure.xlsx
India | IN_N | Barsingar Lignite TPP |  |  | Coal |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Bithnok TPP |  |  | Coal |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Ghatampur TPP |  |  | Coal |  |  | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Singrauli STPS |  |  | Coal |  |  | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Yamuna Nagar or Deenbandhu Chotu Ram TPS |  |  | Coal |  |  | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Chanju-III Hydro Power Project |  |  | Hydro |  |  | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Dhaulasidh Hydro Power Project |  |  | Hydro |  |  | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Kiru Hydro Power Project |  |  | Hydro |  |  | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Kwar Hydro Power Project |  |  | Hydro |  |  | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Lakhwar Hydro Power Project |  |  | Hydro |  |  | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Lata Tapovan Hydro Power Project |  |  | Hydro |  |  | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Lower Kalnai Hydro Power Project |  |  | Hydro |  |  | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Luhri Stage-I Hydro Power Project |  |  | Hydro |  |  | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Pakal Dul Hydro Power Project |  |  | Hydro |  |  | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Parnai Hydro Power Project |  |  | Hydro |  |  | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Phata Byung Hydro Power Project |  |  | Hydro |  |  | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Ratle Hydro Power Project |  |  | Hydro |  |  | Jammu and Kashmir | India_Electricity_Infrastructure.xlsx
India | IN_N | Shahpurkandi Hydro Power Project |  |  | Hydro |  |  | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Shongtong Karcham Hydro Power Project |  |  | Hydro |  |  | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunni Dam Hydro Power Project |  |  | Hydro |  |  | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Tangnu Romai- I Hydro Power Project |  |  | Hydro |  |  | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Tapovan Vishnugad Hydro Power Project |  |  | Hydro |  |  | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Tehri Pumped Storage Hydro Power Project |  |  | Hydro |  |  | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Tidong-I Hydro Power Project |  |  | Hydro |  |  | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Vishnugad Pipalkoti Hydro Power Project |  |  | Hydro |  |  | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | Gorakhpur Haryana Anu Vidyut Pariyojana |  |  | Nuclear |  |  | Haryana | India_Electricity_Infrastructure.xlsx
India | IN_N | Rajasthan Atomic Power Station |  |  | Nuclear |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | BETA Combined Cycle Power Plant Module I |  |  | Oil & Gas |  |  | Uttarakhand | India_Electricity_Infrastructure.xlsx
India | IN_N | ABC RENEWABLE ENERGY RJ-01 Private Limited Rajasthan 400.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ABC RJ LAND 01 Private Limited Rajasthan 380.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ABU RENEWABLES INDIA PRIVATE LIMITED Rajasthan 340.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ACME Sun Power Private Limited Rajasthan 320.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ACME Surya Power Private Limited Rajasthan 250.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ACME Venus Urja Private Limited Rajasthan 400.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | AM Green Energy Private Limited, Bikaner Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Acme Renewtech Fifth Private Limited Rajasthan 250.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Eighteen Limited (AREH18L) Rajasthan 50.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 250.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 284.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 500.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 717.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Four Limited Rajasthan 765.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Holding Seventeen Private Limited Rajasthan 600.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Park Rajasthan Limited Rajasthan 1000.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Park Rajasthan Limited – AREPRL – a JV of State Govt. & A |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Solar Energy AP Three Limited Rajasthan 150.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Amplus Tungabhadra Private Limited Uttar Pradesh 50.0 |  |  | Solar |  |  | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Apraava Energy Private Limited Rajasthan 250.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Apraava Energy Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Apraava Energy Private Limited Rajasthan 50.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Auxo Sunlight Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Avaada RJSustainable Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Avaada RJSustainable Private Limited Rajasthan 700.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Avaada Surya Power Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Avaada Suryaenergy Private Limited Rajasthan 1100.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | CESC Limited (Developer Company) Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | EG Mega Urja Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | EG Saur Urja Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Energizent Power Private Limited Rajasthan 205.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Enfinity Global Surya Kiran Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Frugal Energy Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Furies Solren Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Furies Solren Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Hazel Hybren Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Helia Energy Park Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | IB Vogt Solar Seven Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Inox Wind Energy Limited Rajasthan 500.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Izhma Solar Private Limited Rajasthan 200.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | JGRJ One Solar Private Limited Rajasthan 100.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | JGRJ One Solar Private Limited Rajasthan 50.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | JGRJ Two Solar Private Limited Rajasthan 400.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Beta Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Cosmic Private Limited Rajasthan 100.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Cosmic Private Limited Rajasthan 150.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Energy Private Limited Rajasthan 130.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Energy Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Energy Private Limited Rajasthan 50.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green India Six Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Stellar Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Nirjara Energy Private Limited Rajasthan 50.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Khidrat Renewable Energy Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | M/s Hinduja Renewables Energy Private Limited (LoA has been cancelled) Uttar Pra |  |  | Solar |  |  | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | M/s. Essel Surya Urja Company of Rajasthan Limited -ESUCRL- A JV of Rajasthan St |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Martial Solren Private Limited Rajasthan 200.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | NEEPCO Limited (SPD) Rajasthan 100.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | NEEPCO Limited (SPD) Rajasthan 200.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | NHPC Limited Rajasthan 192.86 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Limited Rajasthan 78.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Limited Uttar Pradesh 20.0 |  |  | Solar |  |  | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC REL Rajasthan 250.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC REL Rajasthan 325.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC REL Rajasthan 500.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Renewables Energy Limited Uttar Pradesh 600.0 |  |  | Solar |  |  | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Renewables Energy Limited Uttar Pradesh 800.0 |  |  | Solar |  |  | Uttar Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Others Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Proteus Energy Private Limited Rajasthan 217.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Purvah Green Power Private Limited (Developer Company) Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Radiant Star Solar Park Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Dinkar Jyoti Private Limited Rajasthan 100.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Dinkar Urja Private Limited Rajasthan 200.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Samir Shakti Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar (Shakti Five) Private Limited Rajasthan 400.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar (Shakti Six) Private Limited (400+400) Rajasthan 400.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar (Shakti Six) Private Limited Rajasthan 1000.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar (Shakti Three) Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power P. Limited Rajasthan 200.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power P. Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power P. Limited Rajasthan 400.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited (2 x 300) Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 100.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 150.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 200.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 250.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 400.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Solar Power Private Limited Rajasthan 70.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Surya Jyoti Private Limited Rajasthan 210.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | ReNew Surya Pratap Private Limited Rajasthan 210.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Renew Sun Power Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Resco Global Wind Services Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Resco Global Wind Services Private Limited Rajasthan 76.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Himachal Pradesh 15.0 |  |  | Solar |  |  | Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Punjab 100.0 |  |  | Solar |  |  | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Rajasthan 100.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Rajasthan 370.1 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | SPV - Deshraj Solar Energy Private Limited Rajasthan 150.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | SPV - HRP Green Power Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | SRIPL5, SRIPL8, SRIPL9 Rajasthan 200.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | SRIPL5, SRIPL8, SRIPL9 Rajasthan 50.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Saimaa Solar Private Limited Rajasthan 150.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Shikhar Surya (One) Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Sone Solar Private Limited Punjab 40.0 |  |  | Solar |  |  | Punjab | India_Electricity_Infrastructure.xlsx
India | IN_N | Sourya Manthan Renewable Energy Private Limited Rajasthan 100.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Sprng Power Private Limited Rajasthan 250.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunbreeze Renewables Nine Private Limited Rajasthan 1000.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunbreeze Renewables Nine Private Limited Rajasthan 400.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | TEQ Green Power XIII Private Limited Rajasthan 120.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | TEQ Green Power XVI Private Limited Rajasthan 50.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | TP SAURYA LIMITED Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Tejorupa Renewables India Project Private Limited Rajasthan 250.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Tepsol Sun Sparkle Private Limited Rajasthan 300.0 |  |  | Solar |  |  | Rajasthan | India_Electricity_Infrastructure.xlsx
India | IN_N | Acme Renewtech Sixth Private Limited Gujarat, Andhra Pradesh & Rajasthan 250.0 |  |  | Solar |  |  | Gujarat, Andhra Pradesh & | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five A Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five B Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five B Limited N.A. 83.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five C Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Five Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Four A Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Four B Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Four Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Seven A Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six A Limited N.A. 167.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six A Limited N.A. 200.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six A Limited N.A. 234.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six A Limited N.A. 50.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six B Limited N.A. 134.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six B Limited N.A. 150.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six B Limited N.A. 167.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Green Energy Twenty Six B Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Five Limited N.A. 100.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Five Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Five Limited N.A. 67.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Five Limited N.A. 99.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Seven Limited N.A. 100.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Seven Limited N.A. 150.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Seven Limited N.A. 200.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Seven Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Adani Renewable Energy Fifty Six Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Azure Power Fifty One Private Limited N.A. 100.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Azure Power Fifty One Private Limited N.A. 50.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Azure Power Fifty Two Private Limited N.A. 167.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Azure Power Fifty Two Private Limited N.A. 333.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Damodar Valley Corporation (DVC) Jharkand & West Bengal 10.0 |  |  | Solar |  |  | Jharkand & West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_N | Eden Renewable Bercy Private Limited N.A. 300.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Gorbea Solar Private Limited N.A. 200.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Green Infra Renewable Projects Limited N.A. 298.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Green Valley Renewable Energy GVREL - A JV of DVC & NTPC Green Energy Limited Jh |  |  | Solar |  |  | Jharkand & West Bengal | India_Electricity_Infrastructure.xlsx
India | IN_N | JSW Renew Energy Eleven Limited N.A. 700.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Jakson Limited N.A. 50.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Juniper Green Energy Private Limited N.A. 300.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | MRS Green Energy Private Limited N.A. 100.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Renewable Energy Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | NTPC Renewable Energy Limited N.A. 500.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Pace Digitek Private Limited N.A. 100.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Pavni (Raj) Solar Private Limited (erstwhile: AEW India North One Private Limite |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Project Nine Renewable Power Private Limited Rajasthan, Karnataka & Andhra Prade |  |  | Solar |  |  | Rajasthan, Karnataka & An | India_Electricity_Infrastructure.xlsx
India | IN_N | Reliance NU Suntech Private Limited N.A. 930.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | SAEL Industries Limited N.A. 250.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | SAEL SOLAR MHP1 Private Limited N.A. 300.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | SAEL SOLAR MHP2 Private Limited N.A. 300.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | SJVN GREEN ENERGY LIMITED Punjab & Himachal Pradesh 18.0 |  |  | Solar |  |  | Punjab & Himachal Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_N | Sembcorp Green Infra Private Limited N.A. 150.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | Sunsure Solarpark Fourteen Private Limited N.A. 300.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_N | The Singareni Collieries Company Limited N.A. 76.0 |  |  | Solar |  |  | N.A. | India_Electricity_Infrastructure.xlsx
India | IN_S | Bhavanapadu Thermal Power Plant Phase I |  |  | Coal |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Ennore SEZ Expansion SCTPP |  |  | Coal |  |  | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | North Chennai TPS |  |  | Coal |  |  | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Singareni TPP |  |  | Coal |  |  | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Tuticorin (P) TPP |  |  | Coal |  |  | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Udangudi Power Station |  |  | Coal |  |  | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Yadadri Thermal Power Station |  |  | Coal |  |  | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Chitravathi Pumped Storage Project |  |  | Hydro |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Gandikota Pumped Storage Project |  |  | Hydro |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Kundah Pumped Storage Phase-I, II & III |  |  | Hydro |  |  | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Lower Sileru (Extension) Hydroelectric Power Project |  |  | Hydro |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Mankulam Hydro Power Project |  |  | Hydro |  |  | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | Polavaram Hydro Power Project |  |  | Hydro |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Saundatti Pumped Storage Project |  |  | Hydro |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Sharavathy Pumped Storage Project |  |  | Hydro |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Upper Sileru Pumped Storage Project |  |  | Hydro |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | BHAVINI PFBR Atomic Power Station |  |  | Nuclear |  |  | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | Kudankulam Atomic Power Project |  |  | Nuclear |  |  | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | ACME Hybrid Urja Private Limited Karnataka 280.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | ACME Omega Urja Private Limited Karnataka 300.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | ACME Platinum Urja Private Limited Karnataka 350.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | APSPCL - a JV of NREDCAP, APGENCO & SECI Andhra Pradesh 100.0 |  |  | Solar |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | APSPCL - a JV of NREDCAP, APGENCO & SECI Andhra Pradesh 750.0 |  |  | Solar |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Ayana Kadapa Renewable Power Private Limited Andhra Pradesh 250.0 |  |  | Solar |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Clean Renewable Energy Hybrid Eight Private Limited (SPV of Hero Solar Energy Pr |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | INGEL Tamil Nadu 200.0 |  |  | Solar |  |  | Tamil Nadu | India_Electricity_Infrastructure.xlsx
India | IN_S | IRCON RENEWABLE POWER LIMITED Karnataka 100.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | NHPC Limited Andhra Pradesh 100.0 |  |  | Solar |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | NHPC Limited Kerala 50.0 |  |  | Solar |  |  | Kerala | India_Electricity_Infrastructure.xlsx
India | IN_S | NTPC Limited Telangana 176.0 |  |  | Solar |  |  | Telangana | India_Electricity_Infrastructure.xlsx
India | IN_S | Purvah Green Power Private Limited (Developer Company) Andhra Pradesh 300.0 |  |  | Solar |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Purvah Green Power Private Limited (Developer Company) Karnataka 300.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Reliance Jio Infocomm Limited Karnataka 25.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | SECI Andhra Pradesh 300.0 |  |  | Solar |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | Sprng Soura Kiran Private Limited Andhra Pradesh 250.0 |  |  | Solar |  |  | Andhra Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_S | TEQ Green Power XVI Private Limited Karnataka 70.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 170.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 200.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 202.5 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 300.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_S | Tata Power Renewable Energy Limited Karnataka 400.0 |  |  | Solar |  |  | Karnataka | India_Electricity_Infrastructure.xlsx
India | IN_W | Akaltara TPS |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Amaravati TPS |  |  | Coal |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Avantha Bhandar TPS |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Bijora Ghanmukh TPP |  |  | Coal |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Binjkote TPP |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Deveri TPP/ Visa Thermal Power Plant |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Gadarwara STPS |  |  | Coal |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Gorgi Thermal Power Project |  |  | Coal |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Koradi TPS |  |  | Coal |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Korba West or Hasdeo TPS |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Lanco Vidarbha TPP |  |  | Coal |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Lara STPS |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Mahan TPP |  |  | Coal |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Nasik RattanIndia or Nasik (P) TPS |  |  | Coal |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Pathadi TPP |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Raikheda TPP |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Salora TPP |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Singhitarai TPP |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Sipat STPS |  |  | Coal |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | Ukai TPS |  |  | Coal |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhavali Pumped Storage Project |  |  | Hydro |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Bhivpuri Pumped Storage Project |  |  | Hydro |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Koyna Left Bank PSS Hydro Power Project |  |  | Hydro |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MP30 Gandhi Sagar Pumped Storage Project |  |  | Hydro |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Maheshwar Hydro Power Project |  |  | Hydro |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | ADANI RENEWABLE ENERGY EIGHT LIMITED Gujarat 115.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Adani Renewable Energy Holding Four Limited Gujarat 500.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Adani Renewable Energy Holding Four Limited Gujarat 750.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Amplus Kaveri Solar Private Limited Maharashtra 100.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Asnen Solar Private Limited Madhya Pradesh 200.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada GJGreen Private Limited Gujarat 300.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada GJSolar Private Limited Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada GJSustainable Private Limited [Lakadiya-SECI] Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada InClean Private Limited Gujarat 300.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada KNClean Private Limited Madhya Pradesh 700.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada KNClean Private Limited Madhya Pradesh 900.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada MHRenewable1 Private Limited Maharashtra 500.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada MPSolar Private Limited Madhya Pradesh 500.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada MPSustainable Private Limited Madhya Pradesh 750.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada SunEnergy Private Limited Maharashtra 400.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Avaada Sustainable Urja Private Limited Maharashtra 73.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Clean Renewable Energy Hybrid Eleven Private Limited(SPV of Hero Solar Energy Pr |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Ctrls Datacenters Limited Maharashtra 50.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Femund Solar Private Limited Gujarat 150.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | GSECL Gujarat 1200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | GSECL Gujarat 3325.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | GSECL Gujarat 600.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | GSECL Gujarat 700.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | HR Sabarmati Private Limited Gujarat 158.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | HR Sabarmati Private Limited Gujarat 52.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | INGEL Gujarat 600.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Gujarat 150.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Gujarat 600.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Maharashtra 350.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Energy Private Limited Maharashtra 50.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Gem Private Limited Maharashtra 100.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Juniper Green Gem Private Limited Maharashtra 200.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY Eleventh Solar Private Limited Maharashtra 183.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY Fifth Solar Private Limited Maharashtra 103.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY First Kusum Private Limited Maharashtra 185.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY Tenth Solar Private Limited Maharashtra 154.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | MSKVY Twentieth Solar Private Limited Maharashtra 129.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Maharashtra State Electricity Generating Co. Limited - MAHAGENCO Maharashtra 250 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Malaren Solar Private Limited Gujarat 150.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NHPC Limited Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NHPC Limited Gujarat 600.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC Limited Chhattisgarh 26.0 |  |  | Solar |  |  | Chhattisgarh | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC Limited Madhya Pradesh 20.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC Limited Maharashtra 13.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 1200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 137.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 225.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 245.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 275.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | NTPC REL Gujarat 721.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Ortusun Renewables Maharashtra 20.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Purvah Green Power Private Limited(Developer Company) Gujarat 300.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | RDS Solar Park Private Limited Gujarat 350.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar (Shakti Eight) Private Limited Gujarat 100.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar (Shakti Eight) Private Limited Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Gujarat 100.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Gujarat 300.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Madhya Pradesh 200.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | ReNew Solar Power Private Limited Maharashtra 100.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Reliance New Energy Maharashtra 93.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Resco Global Wind Services Private Limited Gujarat 100.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Resco Global Wind Services Private Limited Gujarat 500.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Resco Global Wind Services Private Limited Madhya Pradesh 200.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Resco Global Wind Services Private Limited Madhya Pradesh 240.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | Rewa Ultra Mega Solar Limited RUMSL- a JV of MPUVN and SECI Madhya Pradesh 170.0 |  |  | Solar |  |  | Madhya Pradesh | India_Electricity_Infrastructure.xlsx
India | IN_W | SJVN GREEN ENERGY LIMITED Gujarat 100.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | SJVN GREEN ENERGY LIMITED Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | SJVN GREEN ENERGY LIMITED Gujarat 260.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | SJVN GREEN ENERGY LIMITED Gujarat 70.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | SPV Maharashtra 1.3 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Skadar Solar Private Limited Maharashtra 200.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Sprng Green Power Private Limited Gujarat 300.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Sprng Power Earth Private Limited Gujarat 250.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx
India | IN_W | Tata Power Renewable Energy Limited Maharashtra 270.0 |  |  | Solar |  |  | Maharashtra | India_Electricity_Infrastructure.xlsx
India | IN_W | Teq Green Power Private Limited Gujarat 200.0 |  |  | Solar |  |  | Gujarat | India_Electricity_Infrastructure.xlsx

## Technology_Costs
Technology_Code | Technology_Name | Parameter | Unit | 2023 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Source | Notes
PWRSPV | Solar PV (utility-scale) | CAPEX | USD/kW | 560 | 536 | 474 | 413 | 379 | 345 | 311 | IN(base)=$560/kW ¦ BD=$840(×1.5) ¦ LK=$849(×1.5) ¦ NP=$896(×1.6) ¦ BT=$1008(×1.8) ¦ MV=$1680(×3.0) Anchor refs: IRENA 2024; ADB PADs; CEB LTGEP BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
PWRSPV | Solar PV (utility-scale) | Fixed O&M | USD/kW/yr | 8 | 8 | 7 | 6 | 6 | 5 | 5 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
PWRSPV | Solar PV (utility-scale) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
PWRSPV | Solar PV (utility-scale) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRSPV | Solar PV (utility-scale) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRSPV | Solar PV (utility-scale) | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEA NEP Annexure-A (4.64 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: High ¦ Node anchor: IN
PWRSPR | Solar PV (rooftop/distributed) | CAPEX | USD/kW | 850 | 813 | 720 | 627 | 576 | 524 | 472 | IN(base)=$850/kW ¦ BD=$1275(×1.5) ¦ LK=$982(×1.2) ¦ NP=$1360(×1.6) ¦ BT=$1530(×1.8) ¦ MV=$2550(×3.0) Anchor refs: CERC; CEB LTGEP BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
PWRSPR | Solar PV (rooftop/distributed) | Fixed O&M | USD/kW/yr | 9 | 9 | 8 | 7 | 7 | 6 | 6 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
PWRSPR | Solar PV (rooftop/distributed) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
PWRSPR | Solar PV (rooftop/distributed) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRSPR | Solar PV (rooftop/distributed) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRSPR | Solar PV (rooftop/distributed) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CERC/MNRE benchmarks; SL LTGEP $982/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline rates (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: IN
PWRCSP | Concentrated Solar Power | CAPEX | USD/kW | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | 7912 | BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
PWRCSP | Concentrated Solar Power | Fixed O&M | USD/kW/yr | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
PWRCSP | Concentrated Solar Power | Variable O&M | USD/MWh | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
PWRCSP | Concentrated Solar Power | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRCSP | Concentrated Solar Power | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRCSP | Concentrated Solar Power | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: NREL ATB 2024 (no SA-specific data) ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Trajectory: NREL ATB 2024 ¦ https://atb.nrel.gov/electricity/2024/concentrating_solar_power ¦ Confidence: Low ¦ Node anchor: ATB
PWRWON | Onshore Wind | CAPEX | USD/kW | 761 | 687 | 663 | 640 | 617 | 594 | 570 | IN(base)=$761/kW ¦ BD=$1218(×1.6) ¦ LK=$1391(×1.8) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP BD ×1.5-2.0: Limited BD wind experience [⚠ NO URL] LK ×1.5-2.3: ADB Mannar $2,481/kW (incl. harbor) (https://www.adb.org/results/helping-sri-lanka-go-green) | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
PWRWON | Onshore Wind | Fixed O&M | USD/kW/yr | 22 | 22 | 21 | 20 | 20 | 19 | 19 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
PWRWON | Onshore Wind | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
PWRWON | Onshore Wind | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRWON | Onshore Wind | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRWON | Onshore Wind | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEA NEP Annexure-A (6.32 Cr/MW) ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 Class 4 decline rates ¦ https://atb.nrel.gov/electricity/2024/land-based_wind ¦ Confidence: High ¦ Node anchor: IN
PWRWOF | Offshore Wind | CAPEX | USD/kW | 3800 | 3768 | 3442 | 2014 | 1960 | 1919 | 1886 | IN(base)=$2339/kW ¦ BD=N/A ¦ LK=$3781(×1.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
PWRWOF | Offshore Wind | Fixed O&M | USD/kW/yr | 114 | 114 | 105 | 97 | 90 | 84 | 80 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
PWRWOF | Offshore Wind | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
PWRWOF | Offshore Wind | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRWOF | Offshore Wind | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRWOF | Offshore Wind | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) ¦ https://www.ceb.lk ¦ Trajectory: NREL ATB 2024 Offshore Class 3 decline rates ¦ https://atb.nrel.gov/electricity/2024/offshore_wind ¦ Confidence: Low ¦ Node anchor: LK
PWRHDR | Hydro – Reservoir | CAPEX | USD/kW | 2500 | 2550 | 2625 | 2700 | 2775 | 2850 | 2925 | IN(base)=$1500/kW ¦ BD=N/A ¦ LK=$2500(×1.7) ¦ NP=$2761(×1.8) ¦ BT=$1200(×0.8) ¦ MV=N/A Anchor refs: CEA; Nepal NEA; Bhutan PSMP LK ×~1.5: No specific LK data [⚠ NO URL] NP ×2.0-3.0: Tanahu $3,607/kW; Upper Trishuli $2,997/kW (https://www.adb.org) BT ×0.9-1.3: Mangdechhu $938/kW; Tala $1,176/kW | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHDR | Hydro – Reservoir | Fixed O&M | USD/kW/yr | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHDR | Hydro – Reservoir | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHDR | Hydro – Reservoir | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRHDR | Hydro – Reservoir | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRHDR | Hydro – Reservoir | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: Bhutan PSMP 2040; Nepal NEA; IRENA ¦ https://www.jica.go.jp/english/overseas/bhutan/information/topics/2022/220518.html ¦ Trajectory: 1-2%/yr real escalation (best sites developed first) ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHRO | Hydro – Run-of-River | CAPEX | USD/kW | 1750 | 1785 | 1873 | 1960 | 2048 | 2135 | 2223 | IN(base)=$1300/kW ¦ BD=N/A ¦ LK=$1840(×1.4) ¦ NP=$1600(×1.2) ¦ BT=$1100(×0.85) ¦ MV=N/A Anchor refs: CEA; CEB LTGEP; PSMP; Nepal NEA LK ×~1.3: CEB LTGEP mini-hydro $1,840/kW (https://www.ceb.lk) NP ×1.3-1.7: NEA/industry ~$2,000/kW avg (https://www.adb.org/sites/default/files/publication/612641/hydropower-development-economic-growth-nepal.pdf) BT ×0.8-1.1: PSMP $785-1,339/kW; Nikachhu $1,220/kW (https://sasec.asia) | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHRO | Hydro – Run-of-River | Fixed O&M | USD/kW/yr | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHRO | Hydro – Run-of-River | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHRO | Hydro – Run-of-River | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRHRO | Hydro – Run-of-River | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRHRO | Hydro – Run-of-River | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW ¦ https://www.ceb.lk ¦ Trajectory: Same escalation logic as reservoir ¦ Confidence: Medium ¦ Node anchor: Regional
PWRHPS | Hydro – Pumped Storage | CAPEX | USD/kW | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | IN(base)=$635/kW ¦ BD=N/A ¦ LK=N/A ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP (India only) LK ×~1.5: No specific LK data [⚠ NO URL] NP ×2.0-3.0: Tanahu $3,607/kW; Upper Trishuli $2,997/kW (https://www.adb.org) BT ×0.9-1.3: Mangdechhu $938/kW; Tala $1,176/kW | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
PWRHPS | Hydro – Pumped Storage | Fixed O&M | USD/kW/yr | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
PWRHPS | Hydro – Pumped Storage | Variable O&M | USD/MWh | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
PWRHPS | Hydro – Pumped Storage | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRHPS | Hydro – Pumped Storage | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRHPS | Hydro – Pumped Storage | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW ¦ https://cea.nic.in ¦ Trajectory: Flat real cost (site-specific) ¦ https://atb.nrel.gov/electricity/2024/pumped_storage_hydropower ¦ Confidence: Medium ¦ Node anchor: IN
PWRCOASCPC | Coal – Supercritical | CAPEX | USD/kW | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | IN(base)=$1059/kW ¦ BD=$1694(×1.6) ¦ LK=$2132(×2.0) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP BD ×~1.6: Payra/Rampal cost reporting LK ×~2.0: CEB LTGEP $2,132/kW (https://www.ceb.lk) | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOASCPC | Coal – Supercritical | Fixed O&M | USD/kW/yr | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOASCPC | Coal – Supercritical | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOASCPC | Coal – Supercritical | Heat Rate | GJ/MWh | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOASCPC | Coal – Supercritical | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Coal' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRCOASCPC | Coal – Supercritical | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | CAPEX | USD/kW | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | 2250 | BD ×~1.6: Payra/Rampal cost reporting LK ×~2.0: CEB LTGEP $2,132/kW (https://www.ceb.lk) | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | Fixed O&M | USD/kW/yr | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | Heat Rate | GJ/MWh | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCOAUSC | Coal – Ultra-supercritical | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Coal' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRCOAUSC | Coal – Ultra-supercritical | Construction Time | years | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Base: Est. ~7% premium over SC; better heat rate ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: IN/LK
PWRCCG | Combined Cycle Gas Turbine | CAPEX | USD/kW | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | IN(base)=$700/kW ¦ BD=$770(×1.1) ¦ LK=$1300(×1.9) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA; IEPMP; CEB LTGEP BD ×~1.1: IEPMP ~$770/kW LK ×~1.9: CEB LTGEP $1,273-1,507/kW (https://www.ceb.lk) | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWRCCG | Combined Cycle Gas Turbine | Fixed O&M | USD/kW/yr | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWRCCG | Combined Cycle Gas Turbine | Variable O&M | USD/MWh | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 | 2.83 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWRCCG | Combined Cycle Gas Turbine | Heat Rate | GJ/MWh | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 | 6.51 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWRCCG | Combined Cycle Gas Turbine | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Natural gas' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRCCG | Combined Cycle Gas Turbine | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | CAPEX | USD/kW | 360 | 360 | 360 | 360 | 360 | 360 | 360 | IN(base)=$450/kW ¦ BD=$495(×1.1) ¦ LK=$360(×0.8) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA; CEB LTGEP BD ×~1.1: IEPMP ~$770/kW LK ×~1.9: CEB LTGEP $1,273-1,507/kW (https://www.ceb.lk) | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | Fixed O&M | USD/kW/yr | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | Variable O&M | USD/MWh | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 | 4.99 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | Heat Rate | GJ/MWh | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 | 9.65 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROCG | Open Cycle Gas Turbine | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Natural gas' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWROCG | Open Cycle Gas Turbine | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK
PWROIL | Oil/Diesel generation | CAPEX | USD/kW | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | IN(base)=$700/kW ¦ BD=$770(×1.1) ¦ LK=$1000(×1.4) ¦ NP=N/A ¦ BT=N/A ¦ MV=$700(×1.0) Anchor refs: CEB LTGEP; ADB Maldives BD ×~1.1: BPDB IPP costs LK ×~1.4: CEB LTGEP $1,000-1,124/kW (https://www.ceb.lk) NP ×~1.5: Landlocked transport premium BT ×~1.5: Landlocked transport premium MV ×~1.0: Core competency (STELCO/FENAKA) (https://www.environment.gov.mv) | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWROIL | Oil/Diesel generation | Fixed O&M | USD/kW/yr | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWROIL | Oil/Diesel generation | Variable O&M | USD/MWh | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 | 6.31 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWROIL | Oil/Diesel generation | Heat Rate | GJ/MWh | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 | 8.73 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWROIL | Oil/Diesel generation | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Crude oil (Brent)' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWROIL | Oil/Diesel generation | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: High ¦ Node anchor: LK/MV
PWRBIO | Biomass/Bagasse | CAPEX | USD/kW | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | 1782 | IN(base)=$1142/kW ¦ BD=N/A ¦ LK=$1782(×1.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: CEA NEP; CEB LTGEP | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRBIO | Biomass/Bagasse | Fixed O&M | USD/kW/yr | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRBIO | Biomass/Bagasse | Variable O&M | USD/MWh | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRBIO | Biomass/Bagasse | Heat Rate | GJ/MWh | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 | 18.83 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRBIO | Biomass/Bagasse | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Biomass residue' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRBIO | Biomass/Bagasse | Construction Time | years | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Base: CEB LTGEP $1,782/kW; FOM=4% CAPEX ¦ https://www.ceb.lk ¦ Trajectory: Flat real cost ¦ Confidence: Medium ¦ Node anchor: LK
PWRWTE | Waste-to-Energy | CAPEX | USD/kW | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | BD ×~1.1: BPDB IPP costs LK ×~1.4: CEB LTGEP $1,000-1,124/kW (https://www.ceb.lk) NP ×~1.5: Landlocked transport premium BT ×~1.5: Landlocked transport premium MV ×~1.0: Core competency (STELCO/FENAKA) (https://www.environment.gov.mv) | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRWTE | Waste-to-Energy | Fixed O&M | USD/kW/yr | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRWTE | Waste-to-Energy | Variable O&M | USD/MWh | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRWTE | Waste-to-Energy | Heat Rate | GJ/MWh | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRWTE | Waste-to-Energy | Fuel Cost | USD/GJ | [8 empty] | See OSTRAM_Consolidated_CostDB_v2 → Fuel_Costs sheet → 'Waste' row. WB CMO Oct 2025 + IEA WEO 2025 projections.
PWRWTE | Waste-to-Energy | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW ¦ Trajectory: Flat real cost ¦ Confidence: Low ¦ Node anchor: IN
PWRURN | Nuclear | CAPEX | USD/kW | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | 5103 | IN(base)=$2000/kW ¦ BD=$5200(×2.6) ¦ LK=$5103(×2.6) ¦ NP=N/A ¦ BT=N/A ¦ MV=N/A Anchor refs: India PHWR; BD Rooppur; CEB LTGEP | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Fixed O&M | USD/kW/yr | 134 | 134 | 134 | 134 | 134 | 134 | 134 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Variable O&M | USD/MWh | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 | 2.63 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Heat Rate | GJ/MWh | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 | 11.23 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Fuel Cost | USD/GJ | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRURN | Nuclear | Construction Time | years | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Base: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW ¦ https://www.ceb.lk ¦ Trajectory: ATB Nuclear Large decline rates ¦ https://atb.nrel.gov/electricity/2024/nuclear ¦ Confidence: Medium ¦ Node anchor: LK/BD
PWRGEO | Geothermal | CAPEX | USD/kW | 4589 | 4544 | 4434 | 4327 | 4222 | 4120 | 4020 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
PWRGEO | Geothermal | Fixed O&M | USD/kW/yr | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
PWRGEO | Geothermal | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
PWRGEO | Geothermal | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRGEO | Geothermal | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRGEO | Geothermal | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: IRENA global avg; ATB Hydro/Flash ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Trajectory: ATB 2024 Geothermal decline rates ¦ https://atb.nrel.gov/electricity/2024/geothermal ¦ Confidence: Low ¦ Node anchor: Intl
PWRSDS | Short-duration storage (Li-ion 4h) | CAPEX | USD/kW | [7 empty] | IN(base)=$882/kW ¦ BD=$1058(×1.2) ¦ LK=$1330(×1.5) ¦ NP=$1147(×1.3) ¦ BT=$1235(×1.4) ¦ MV=$1323(×1.5) Anchor refs: CEA NEP; CEB LTGEP; ADB BD ×~1.2: Limited BD data [⚠ NO URL] LK ×~1.5: CEB LTGEP ~$1,330/kW (https://www.ceb.lk) NP ×~1.3: No specific data [⚠ NO URL] BT ×~1.4: No specific data [⚠ NO URL] MV ×~1.5: Island logistics premium | ⚠ NO SOURCE
PWRSDS | Short-duration storage (Li-ion 4h) | Fixed O&M | USD/kW/yr | 20 | 21 | 17 | 17 | 16 | 16 | 15 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
PWRSDS | Short-duration storage (Li-ion 4h) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
PWRSDS | Short-duration storage (Li-ion 4h) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRSDS | Short-duration storage (Li-ion 4h) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRSDS | Short-duration storage (Li-ion 4h) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW ¦ https://cea.nic.in ¦ Trajectory: NREL ATB 2024 4h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: High ¦ Node anchor: IN
PWRLDS | Long-duration storage (8h+) | CAPEX | USD/kW | [7 empty] | BD ×~1.2: Limited BD data [⚠ NO URL] LK ×~1.5: CEB LTGEP ~$1,330/kW (https://www.ceb.lk) NP ×~1.3: No specific data [⚠ NO URL] BT ×~1.4: No specific data [⚠ NO URL] MV ×~1.5: Island logistics premium | ⚠ NO SOURCE
PWRLDS | Long-duration storage (8h+) | Fixed O&M | USD/kW/yr | 45 | 47 | 38 | 37 | 35 | 34 | 33 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
PWRLDS | Long-duration storage (8h+) | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
PWRLDS | Long-duration storage (8h+) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRLDS | Long-duration storage (8h+) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRLDS | Long-duration storage (8h+) | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: Generic 8h+ proxy; not single chemistry ¦ Trajectory: NREL ATB 2024 8h BESS decline rates ¦ https://atb.nrel.gov/electricity/2024/utility-scale_battery_storage ¦ Confidence: Low ¦ Node anchor: Regional
PWRFPV | Floating Solar PV | CAPEX | USD/kW | 1244 | 1190 | 1054 | 918 | 842 | 767 | 691 | BD ×1.5-2.0: ADB Muktagacha $1,215/kW; Beximco $1,500/kW (https://www.adb.org) LK ×1.9-2.5: CEB LTGEP $849/kW; Siyambalanduwa $1,400/kW (https://www.ceb.lk) NP ×2.0-2.5: No large-scale data [⚠ NO URL] BT ×2.0-2.5: No data [⚠ NO URL] MV ×3.0-9.0: ADB POISED $5,000/kW system; ASPIRE $1,600-2,000/kW (https://www.adb.org) | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
PWRFPV | Floating Solar PV | Fixed O&M | USD/kW/yr | 19 | 18 | 17 | 16 | 15 | 14 | 13 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
PWRFPV | Floating Solar PV | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
PWRFPV | Floating Solar PV | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRFPV | Floating Solar PV | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRFPV | Floating Solar PV | Construction Time | years | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Base: CEB LTGEP ($1,244/kW, 1.5% FOM) ¦ https://www.ceb.lk ¦ Trajectory: ATB 2024 utility PV decline (proxy) ¦ https://atb.nrel.gov/electricity/2024/utility-scale_pv ¦ Confidence: Medium ¦ Node anchor: LK
PWRH2G | Green Hydrogen Fuel Cell | CAPEX | USD/kW | 2200 | 2100 | 1800 | 1500 | 1300 | 1100 | 1000 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
PWRH2G | Green Hydrogen Fuel Cell | Fixed O&M | USD/kW/yr | 66 | 63 | 54 | 45 | 39 | 33 | 30 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
PWRH2G | Green Hydrogen Fuel Cell | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
PWRH2G | Green Hydrogen Fuel Cell | Heat Rate | GJ/MWh | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 | 6.55 |  | N/A — renewable/non-combustion technology
PWRH2G | Green Hydrogen Fuel Cell | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRH2G | Green Hydrogen Fuel Cell | Construction Time | years | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Base: DOE FC targets; India NGHM ¦ Trajectory: DOE targets + learning curves ¦ Confidence: Low ¦ Node anchor: Intl
PWRTDL | Tidal / Marine | CAPEX | USD/kW | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
PWRTDL | Tidal / Marine | Fixed O&M | USD/kW/yr | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
PWRTDL | Tidal / Marine | Variable O&M | USD/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
PWRTDL | Tidal / Marine | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRTDL | Tidal / Marine | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRTDL | Tidal / Marine | Construction Time | years | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Base: Marine energy literature ¦ Trajectory: Engineering estimates ¦ Confidence: Low ¦ Node anchor: Intl
PWRBCK | Backstop (penalty generator) | CAPEX | USD/kW | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
PWRBCK | Backstop (penalty generator) | Fixed O&M | USD/kW/yr | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
PWRBCK | Backstop (penalty generator) | Variable O&M | USD/MWh | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  | Base: Modeling construct ¦ Trajectory: N/A ¦ Confidence: High ¦ Node anchor: All
PWRBCK | Backstop (penalty generator) | Heat Rate | GJ/MWh | [8 empty] | N/A — renewable/non-combustion technology
PWRBCK | Backstop (penalty generator) | Fuel Cost | USD/GJ | [8 empty] | N/A — renewable/non-combustion technology
PWRBCK | Backstop (penalty generator) | Construction Time | years | [8 empty] | N/A — backstop/penalty generator
Note on E2: Source: CEA NEP Annexure-A (4.64 Cr/MW) Node default: IN
Note on E3: Source: CEA NEP Annexure-A (4.64 Cr/MW) Node default: IN
Note on E4: Source: CEA NEP Annexure-A (4.64 Cr/MW) Node default: IN
Note on E5: ⚠ MISSING: No cost data for PWRSPV / Heat Rate. Check CostDB or ATB fallback.
Note on E6: ⚠ MISSING: No cost data for PWRSPV / Fuel Cost. Check CostDB or ATB fallback.
Note on E7: Source: CEA NEP Annexure-A (4.64 Cr/MW) Node default: IN
Note on E8: Source: CERC/MNRE benchmarks; SL LTGEP $982/kW Node default: IN
Note on E9: Source: CERC/MNRE benchmarks; SL LTGEP $982/kW Node default: IN
Note on E10: Source: CERC/MNRE benchmarks; SL LTGEP $982/kW Node default: IN
Note on E11: ⚠ MISSING: No cost data for PWRSPR / Heat Rate. Check CostDB or ATB fallback.
Note on E12: ⚠ MISSING: No cost data for PWRSPR / Fuel Cost. Check CostDB or ATB fallback.
Note on E13: Source: CERC/MNRE benchmarks; SL LTGEP $982/kW Node default: IN
Note on E14: Source: NREL ATB 2024 (no SA-specific data) Node default: ATB
Note on E15: Source: NREL ATB 2024 (no SA-specific data) Node default: ATB
Note on E16: Source: NREL ATB 2024 (no SA-specific data) Node default: ATB
Note on E17: ⚠ MISSING: No cost data for PWRCSP / Heat Rate. Check CostDB or ATB fallback.
Note on E18: ⚠ MISSING: No cost data for PWRCSP / Fuel Cost. Check CostDB or ATB fallback.
Note on E19: Source: NREL ATB 2024 (no SA-specific data) Node default: ATB
Note on E20: Source: CEA NEP Annexure-A (6.32 Cr/MW) Node default: IN
Note on E21: Source: CEA NEP Annexure-A (6.32 Cr/MW) Node default: IN
Note on E22: Source: CEA NEP Annexure-A (6.32 Cr/MW) Node default: IN
Note on E23: ⚠ MISSING: No cost data for PWRWON / Heat Rate. Check CostDB or ATB fallback.
Note on E24: ⚠ MISSING: No cost data for PWRWON / Fuel Cost. Check CostDB or ATB fallback.
Note on E25: Source: CEA NEP Annexure-A (6.32 Cr/MW) Node default: IN
Note on E26: Source: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) Node default: LK
Note on E27: Source: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) Node default: LK
Note on E28: Source: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) Node default: LK
Note on E29: ⚠ MISSING: No cost data for PWRWOF / Heat Rate. Check CostDB or ATB fallback.
Note on E30: ⚠ MISSING: No cost data for PWRWOF / Fuel Cost. Check CostDB or ATB fallback.
Note on E31: Source: CEB LTGEP 2025-2044 ($3,781/kW fixed-bottom) Node default: LK
Note on E32: Source: Bhutan PSMP 2040; Nepal NEA; IRENA Node default: Regional
Note on E33: Source: Bhutan PSMP 2040; Nepal NEA; IRENA Node default: Regional
Note on E34: Source: Bhutan PSMP 2040; Nepal NEA; IRENA Node default: Regional
Note on E35: ⚠ MISSING: No cost data for PWRHDR / Heat Rate. Check CostDB or ATB fallback.
Note on E36: ⚠ MISSING: No cost data for PWRHDR / Fuel Cost. Check CostDB or ATB fallback.
Note on E37: Source: Bhutan PSMP 2040; Nepal NEA; IRENA Node default: Regional
Note on E38: Source: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW Node default: Regional
Note on E39: Source: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW Node default: Regional
Note on E40: Source: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW Node default: Regional
Note on E41: ⚠ MISSING: No cost data for PWRHRO / Heat Rate. Check CostDB or ATB fallback.
Note on E42: ⚠ MISSING: No cost data for PWRHRO / Fuel Cost. Check CostDB or ATB fallback.
Note on E43: Source: Bhutan PSMP; Nepal NEA; CEB LTGEP mini-hydro $1,840/kW Node default: Regional
Note on E44: Source: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW Node default: IN
Note on E45: Source: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW Node default: IN
Note on E46: Source: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW Node default: IN
Note on E47: ⚠ MISSING: No cost data for PWRHPS / Heat Rate. Check CostDB or ATB fallback.
Note on E48: ⚠ MISSING: No cost data for PWRHPS / Fuel Cost. Check CostDB or ATB fallback.
Note on E49: Source: CEA NEP ($635/kW=5.27 Cr/MW); ATB PSH Class1=$3,224/kW Node default: IN
Note on E50: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on E51: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on E52: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on E53: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on E54: ⚠ MISSING: No cost data for PWRCOASCPC / Fuel Cost. Check CostDB or ATB fallback.
Note on E55: Source: CEB LTGEP $2,132/kW; CEA NEP $1,059/kW (India) Node default: IN/LK
Note on E56: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on E57: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on E58: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on E59: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on E60: ⚠ MISSING: No cost data for PWRCOAUSC / Fuel Cost. Check CostDB or ATB fallback.
Note on E61: Source: Est. ~7% premium over SC; better heat rate Node default: IN/LK
Note on E62: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on E63: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on E64: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on E65: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on E66: ⚠ MISSING: No cost data for PWRCCG / Fuel Cost. Check CostDB or ATB fallback.
Note on E67: Source: CEB LTGEP $1,273-1,507/kW; FOM=1.13 $/kW-mo Node default: LK
Note on E68: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on E69: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on E70: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on E71: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on E72: ⚠ MISSING: No cost data for PWROCG / Fuel Cost. Check CostDB or ATB fallback.
Note on E73: Source: CEB LTGEP $360/kW; FOM=0.64 $/kW-mo Node default: LK
Note on E74: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on E75: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on E76: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on E77: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on E78: ⚠ MISSING: No cost data for PWROIL / Fuel Cost. Check CostDB or ATB fallback.
Note on E79: Source: CEB LTGEP FO IC $1,000-1,124/kW; FOM=3.25 $/kW-mo Node default: LK/MV
Note on E80: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on E81: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on E82: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on E83: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on E84: ⚠ MISSING: No cost data for PWRBIO / Fuel Cost. Check CostDB or ATB fallback.
Note on E85: Source: CEB LTGEP $1,782/kW; FOM=4% CAPEX Node default: LK
Note on E86: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on E87: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on E88: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on E89: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on E90: ⚠ MISSING: No cost data for PWRWTE / Fuel Cost. Check CostDB or ATB fallback.
Note on E91: Source: Indian WTE projects (Bawana, Bidadi) $2,650-3,300/kW Node default: IN
Note on E92: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on E93: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on E94: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on E95: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on E96: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on E97: Source: CEB LTGEP $5,103/kW; BD Rooppur ~$5,200/kW Node default: LK/BD
Note on E98: Source: IRENA global avg; ATB Hydro/Flash Node default: Intl
Note on E99: Source: IRENA global avg; ATB Hydro/Flash Node default: Intl
Note on E100: Source: IRENA global avg; ATB Hydro/Flash Node default: Intl
Note on E101: ⚠ MISSING: No cost data for PWRGEO / Heat Rate. Check CostDB or ATB fallback.
Note on E102: ⚠ MISSING: No cost data for PWRGEO / Fuel Cost. Check CostDB or ATB fallback.
Note on E103: Source: IRENA global avg; ATB Hydro/Flash Node default: Intl
Note on E104: ⚠ MISSING: No cost data for PWRSDS / CAPEX. Check CostDB or ATB fallback.
Note on E105: Source: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW Node default: IN
Note on E106: Source: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW Node default: IN
Note on E107: ⚠ MISSING: No cost data for PWRSDS / Heat Rate. Check CostDB or ATB fallback.
Note on E108: ⚠ MISSING: No cost data for PWRSDS / Fuel Cost. Check CostDB or ATB fallback.
Note on E109: Source: CEA NEP $882/kW (7.32 Cr/MW, 4h); SL ~$1,330/kW Node default: IN
Note on E110: ⚠ MISSING: No cost data for PWRLDS / CAPEX. Check CostDB or ATB fallback.
Note on E111: Source: Generic 8h+ proxy; not single chemistry Node default: Regional
Note on E112: Source: Generic 8h+ proxy; not single chemistry Node default: Regional
Note on E113: ⚠ MISSING: No cost data for PWRLDS / Heat Rate. Check CostDB or ATB fallback.
Note on E114: ⚠ MISSING: No cost data for PWRLDS / Fuel Cost. Check CostDB or ATB fallback.
Note on E115: Source: Generic 8h+ proxy; not single chemistry Node default: Regional
Note on E116: Source: CEB LTGEP ($1,244/kW, 1.5% FOM) Node default: LK
Note on E117: Source: CEB LTGEP ($1,244/kW, 1.5% FOM) Node default: LK
Note on E118: Source: CEB LTGEP ($1,244/kW, 1.5% FOM) Node default: LK
Note on E119: ⚠ MISSING: No cost data for PWRFPV / Heat Rate. Check CostDB or ATB fallback.
Note on E120: ⚠ MISSING: No cost data for PWRFPV / Fuel Cost. Check CostDB or ATB fallback.
Note on E121: Source: CEB LTGEP ($1,244/kW, 1.5% FOM) Node default: LK
Note on E122: Source: DOE FC targets; India NGHM Node default: Intl
Note on E123: Source: DOE FC targets; India NGHM Node default: Intl
Note on E124: Source: DOE FC targets; India NGHM Node default: Intl
Note on E125: Source: DOE FC targets; India NGHM Node default: Intl
Note on E126: ⚠ MISSING: No cost data for PWRH2G / Fuel Cost. Check CostDB or ATB fallback.
Note on E127: Source: DOE FC targets; India NGHM Node default: Intl
Note on E128: Source: Marine energy literature Node default: Intl
Note on E129: Source: Marine energy literature Node default: Intl
Note on E130: Source: Marine energy literature Node default: Intl
Note on E131: ⚠ MISSING: No cost data for PWRTDL / Heat Rate. Check CostDB or ATB fallback.
Note on E132: ⚠ MISSING: No cost data for PWRTDL / Fuel Cost. Check CostDB or ATB fallback.
Note on E133: Source: Marine energy literature Node default: Intl
Note on E134: Source: Modeling construct Node default: All
Note on E135: Source: Modeling construct Node default: All
Note on E136: Source: Modeling construct Node default: All
Note on E137: ⚠ MISSING: No cost data for PWRBCK / Heat Rate. Check CostDB or ATB fallback.
Note on E138: ⚠ MISSING: No cost data for PWRBCK / Fuel Cost. Check CostDB or ATB fallback.
Note on E139: ⚠ MISSING: No cost data for PWRBCK / Construction Time. Check CostDB or ATB fallback.

## RE_Targets_Policies
Country | Node | Policy_Name | Target_Type | Target_Value | Target_Year | Mandate_or_Aspirational | Source
India | IN_N/S/E/W/NE | National Electricity Plan 2023 | Capacity_GW | 500 | 2030 | Mandate | NEP 2023
India | IN_N/S/E/W/NE | India NDC (Updated) | RE_share | 0.5 | 2030 | Mandate | India NDC 2022
Bangladesh | BD | Mujib Climate Prosperity Plan | Capacity_GW | 40 | 2041 | Aspirational | MCPP
Bangladesh | BD | Bangladesh NDC | RE_share | 0.4 | 2041 | Aspirational | Bangladesh NDC 2021
Nepal | NP | National Energy Strategy | Capacity_GW | 15 | 2030 | Aspirational | GoN Energy Strategy
Sri Lanka | LK | Sri Lanka Energy Policy | RE_share | 0.7 | 2030 | Mandate | GoSL NDC 2021
Bhutan | BT | Bhutan NDC | Emissions | Carbon negative | 2030 | Mandate | Bhutan NDC
Maldives | MV | MCCEE Energy Roadmap 2024-2033 | RE_share | 0.33 | 2028 | Mandate | MCCEE Energy Road Map 2024-2033 (ADB, Nov 2024)
Note on H2: India 500 GW RE by 2030: CEA NEP 2023. NDC updated Aug 2022: 50% non-fossil capacity. Source: https://unfccc.int/NDCREG
Note on H3: India 50% RE share by 2030: Updated NDC Aug 2022. Source: https://pib.gov.in/PressReleasePage.aspx?PRID=1847812
Note on H4: Bangladesh 40 GW RE by 2041: Mujib Climate Prosperity Plan. ⚠ IEPMP 2023 supersedes with lower targets. Review.
Note on H5: Bangladesh 40% RE by 2041: NDC 2021. ⚠ IEPMP 2023 has more specific targets. Cross-ref BGD_DA_Final 2_Demand_Forecasts.
Note on H6: Nepal 15 GW by 2030: National Energy Strategy. ⚠ CES/LTS Study has 9.7-20.5 GW range. Source: Nepal_new_data Demand Forecasts.
Note on H7: Sri Lanka 70% RE by 2030: GoSL NDC. CEB LTGEP 2025-2044 has detailed RE roadmap. Source: SriLanka__new_data_v2.
Note on H8: Bhutan carbon negative: NDC commitment. Hydropower dominant. Source: BTN_DA_Final 8_Sources.
Note on H29: Source: Maldives_new_data Demand Forecasts sheet. 33% RE by end-2028. Also: Maldives_Energy_Infrastructure Additional Data sheet. URL: https://www.environment.gov.mv/v2/wp-content/files/publications/20241107-pub-energy-roadmap-maldives-2024-2033-.pdf

## Emissions
Tech.ID | Tech | Tech.Name | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
1 | PWRCOASCPCBDXX01 | Coal – Supercritical, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
2 | PWRCOASCPCIN_NXX01 | Coal – Supercritical, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
3 | PWRCOASCPCIN_SXX01 | Coal – Supercritical, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
4 | PWRCOASCPCIN_EXX01 | Coal – Supercritical, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
5 | PWRCOASCPCIN_WXX01 | Coal – Supercritical, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
6 | PWRCOASCPCLKXX01 | Coal – Supercritical, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600 | 94600
7 | PWRCOAUSCIN_NXX01 | Coal – Ultra-supercritical, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000
8 | PWRCOAUSCIN_SXX01 | Coal – Ultra-supercritical, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000
9 | PWRCOAUSCIN_EXX01 | Coal – Ultra-supercritical, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000
10 | PWRCOAUSCIN_WXX01 | Coal – Ultra-supercritical, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000 | 88000
11 | PWRCCGBDXX01 | Combined Cycle Gas Turbine, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
12 | PWRCCGIN_NXX01 | Combined Cycle Gas Turbine, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
13 | PWRCCGIN_SXX01 | Combined Cycle Gas Turbine, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
14 | PWRCCGIN_EXX01 | Combined Cycle Gas Turbine, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
15 | PWRCCGIN_WXX01 | Combined Cycle Gas Turbine, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
16 | PWRCCGIN_NEXX01 | Combined Cycle Gas Turbine, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
17 | PWRCCGMVXX01 | Combined Cycle Gas Turbine, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
18 | PWRCCGLKXX01 | Combined Cycle Gas Turbine, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
19 | PWROCGBDXX01 | Open Cycle Gas Turbine, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
20 | PWROCGIN_NXX01 | Open Cycle Gas Turbine, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
21 | PWROCGIN_SXX01 | Open Cycle Gas Turbine, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
22 | PWROCGIN_EXX01 | Open Cycle Gas Turbine, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
23 | PWROCGIN_WXX01 | Open Cycle Gas Turbine, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
24 | PWROCGIN_NEXX01 | Open Cycle Gas Turbine, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
25 | PWROCGMVXX01 | Open Cycle Gas Turbine, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
26 | PWROCGLKXX01 | Open Cycle Gas Turbine, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100 | 56100
27 | PWROILMVXX01 | Oil/Diesel generation, Maldives, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300
28 | PWROILBDXX01 | Oil/Diesel generation, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300
29 | PWROILLKXX01 | Oil/Diesel generation, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300 | 73300
30 | PWRWTEIN_NXX01 | Waste-to-Energy, India – North, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
31 | PWRWTEIN_SXX01 | Waste-to-Energy, India – South, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
32 | PWRWTEIN_EXX01 | Waste-to-Energy, India – East, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
33 | PWRWTEIN_WXX01 | Waste-to-Energy, India – West, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
34 | PWRWTEIN_NEXX01 | Waste-to-Energy, India – Northeast, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
35 | PWRWTEBDXX01 | Waste-to-Energy, Bangladesh, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
36 | PWRWTELKXX01 | Waste-to-Energy, Sri Lanka, region XX (investable) | 5 | EmissionActivityRatio | tCO2/PJ | User defined | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000
--- AnnualEmissionLimit (by node, fill per scenario) ---
| AEL_BD | Annual Emission Limit, Bangladesh | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_BT | Annual Emission Limit, Bhutan | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_IN_N | Annual Emission Limit, India – North | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_IN_S | Annual Emission Limit, India – South | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_IN_E | Annual Emission Limit, India – East | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_IN_W | Annual Emission Limit, India – West | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_IN_NE | Annual Emission Limit, India – Northeast | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_NP | Annual Emission Limit, Nepal | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_LK | Annual Emission Limit, Sri Lanka | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| AEL_MV | Annual Emission Limit, Maldives | 15 | AnnualEmissionLimit | MtCO2 | User defined | 0
| MPEL_Total | Model Period Emission Limit (total system) | 16 | ModelPeriodEmissionLimit | MtCO2 | User defined | 0

## Integration_Log
OSTRAM Template Integration Log
Generated: March 2026
Color key: Green=updated from source, Yellow=ambiguity/multiple options, Red=missing, Blue=Renewables.ninja
Sheet | Category | Details | Source File | Status
Capacities_CF | Solar/Wind CFs | 10 regions × 12 timeslices × solar+wind | compiled_reninja_ts.csv | 116 new, 235 ambiguities vs existing
Capacities_CF | BGD thermal CFs | Gas, Coal, Oil/HFO × 12 timeslices | BGD_DA_Final.xlsx | 36 cells from PGCB daily reports
Capacities_CF | LKA thermal+hydro CFs | Coal, Oil_CEB, Oil_IPP, Hydro, MiniHydro × 12 ts | LKA_DA_Final.xlsx | 60 cells from PUCSL 15-min dispatch
Capacities_CF | BTN hydro CFs | HDR+HRO × 12 timeslices | BTN_DA_Final.xlsx | 24 cells from BPSO quarterly reports
Capacities_CF | NPL hydro CFs | RoR+Storage × 12 timeslices | NP_DA_Final.xlsx | 36 cells (RoR: NEA/NREL; Storage: estimated)
Demand_Profiles | BGD demand fractions | 12 timeslices | BGD_DA_Final.xlsx | From 2024 PGCB hourly data
Demand_Profiles | BTN demand fractions | 12 timeslices | BTN_DA_Final.xlsx | From BPSO 2023 + BPC Table 5.20
Demand_Profiles | IND demand fractions | 5 regions × 12 timeslices | IND_DA_Final.xlsx | From Grid-India hourly 2023-2024
Demand_Profiles | LKA demand fractions | 12 timeslices | LKA_DA_Final.xlsx | From PUCSL 15-min dispatch 2023
Demand_Profiles | NPL demand fractions | 12 timeslices | NP_DA_Final.xlsx | From NEA FY2079/80 + NREL hourly
Technology_Costs | All tech CAPEX/FOM/VOM | 23 technologies × CAPEX/FOM/VOM/HeatRate | OSTRAM_Consolidated_CostDB_v2.xlsx | 693 cells, Conservative scenario
Interconnector_Params | Cross-border links | CapitalCost, FixedCost for all corridors | OSTRAM_Consolidated_CostDB_v2.xlsx | 26 cells with full source attribution
Yearsplit | Cross-validation | 12 timeslices checked vs Renewables.ninja | compiled_reninja_ts.csv | 12 discrepancies flagged (different hour assignments)
Capacities_CF | ⚠ MISSING: India thermals | PWRCSP/coal/gas for 5 India sub-regions | N/A | No DA_Final for India thermals yet
Capacities_CF | ⚠ MISSING: Maldives CFs | All MVX techs except solar/wind | Maldives_new_data.xlsx | Yearbook data available but not yet parameterized
Demand_Profiles | ⚠ MISSING: Maldives demand | ELCMVXX02 demand fractions | N/A | No DA_Final for Maldives — see README
REFERENCE AUDIT RESULTS
Category | Count | Details | Action needed
Tech costs with full sources | 99 | CAPEX, FOM, VOM, Construction Time, Operational Life for all 23 techs | None — traceable
Fuel Cost / Heat Rate for renewables | 30 | SPV, SPR, CSP, WON, WOF, HDR, HRO, HPS, FPV, GEO, H2G, TDL, SDS, LDS, BCK | N/A by design — greyed out
Fuel Cost for thermals | 6 | CCG, OCG, Coal SC, Coal USC, OIL, BIO | Cross-ref to CostDB Fuel_Costs sheet (WB CMO + IEA WEO)
⚠ Missing multiplier URLs | 11 | NP/BT solar, BT rooftop, BD wind, BD/NP/BT BESS, LK hydro storage | Need country-specific project cost references
⚠ BESS CostDB entry | 2 | PWRSDS + PWRLDS base costs missing from Technologies sheet | Add from CostDB Node_Anchors ($882/kW IN, decline per Cole et al 2025)
Yearsplit_Template | Original hours | 12 timeslices with template hour assignments | Original template | Preserved as-is
Yearsplit_ReNinja | Renewables.ninja hours | 12 timeslices with RN hour assignments | compiled_reninja_ts.csv | New sheet — separate from template
VariableCost | Fuel costs | 60 MIN* techs × 28 years | OSTRAM_Consolidated_CostDB_v2 Fuel_Costs | 1400 cells, Conservative scenario
Secondary_Techs | CapitalCost + FixedCost | 150 techs with node multipliers applied | CostDB Node_Anchors + Technologies | 7224 cells
Capacities_CF | Rooftop Solar CFs | SPR = 0.85 × SPV for all nodes | Derived from utility-scale | 1820 cells
Capacities_CF | FIX: LDS/SDS revert | Removed misplaced thermal CFs from storage tech rows | Correction | 48 rows fixed
Secondary_Techs | AvailabilityFactor | 150 techs with standard AF values | CEA/CEB/NEA/industry | 4200 cells
Secondary_Techs | Efficiency | 150 techs with input-output ratios | CostDB Heat Rate + standards | 4200 cells
Validation_ThermalDispatch | BGD+LKA dispatch | Observed timeslice CFs for model validation | BGD_DA_Final + LKA_DA_Final | Reference only — not model input
Secondary_Techs | ResidualCapacity | 36 techs with 2023 installed capacity (GW) | DA_Final + new_data + CEA/CEB/NEA/BPC/BPDB | Set from verified sources. India regional splits approximate — refine from CEA state-level data.
PROVENANCE FIXES (Batch)
Existing/Planned_Generation | India Zone→Node mapping | 1872 existing + 376 planned with correct sub-regions | India_Electricity_Infrastructure.xlsx Zone column | Fixed
Secondary_Techs | India ResidualCapacity | 22 techs from plant-level aggregation | India_Electricity_Infrastructure.xlsx (1,870 plants aggregated by zone×fuel) | Fixed
Demand_Profiles | Maldives demand fractions | 12 cells from STELCO monthly + tropical island daypart estimate | Maldives_new_data.xlsx Seasonality (Table 12.2) | Fixed
Capacities_CF | IRENA cross-validation | BTN hydro, LKA wind/hydro/solar annual CFs checked vs IRENA | Bhutan_new_data_v2, SriLanka__new_data_v2 IRENA sheets | Fixed
Demand_Projection | LKA demand reconciliation | Generation vs demand-side definition documented | LKA_DA_Final + CEB LTGEP Table E1 | Fixed
RE_Targets_Policies | Source validation + Maldives | 7 targets sourced + Maldives 33% by 2028 added | NDC submissions, IEPMP, CEB LTGEP, MCCEE Roadmap | Fixed
Interconnectors | Cross-validation | 85 entries from Infrastructure files cross-referenced | 6 Infrastructure files | Fixed
Capacities_CF | Offshore wind provenance | 6 nodes annotated with plausibility assessment | Literature cross-references noted | Fixed
FINAL FIXES
Capacities_CF | Solar/Wind → Renewables.ninja | 420 cells replaced with RN 9-year means | compiled_reninja_ts.csv | Resolves all 235 ambiguities
Secondary_Techs | ResidualCapacity assumption flag | 49 rows flagged | N/A | ⚠ ASSUMPTION: flat across years, no retirement modeled
Demand_Projection | Improvement notes + India source | 10 nodes with actionable improvement notes | Long_Term_Electricity_Demand_Forecasting_Report.pdf Table A5.2 | New Improvement_Notes column
Capacities_CF_Options | Bhutan hydro dual option | 12 rows: BPSO 2024 vs IRENA-scaled | BTN_DA_Final + IRENA Energy Profile Bhutan | Annual CF: 0.453 vs 0.52
RE_Potential_Ceilings | Resource potential reference | 19 entries for TotalAnnualMaxCapacity | MNRE/NIWE/CEA/CEB/MCCEE/NEA/PSMP | New sheet — reference for scenario design
Demand_Profiles | Daypart assumption flags | 18 cells flagged (MV all dayparts, BT S2/S4) |  | Done
ATB_Comparison | NREL ATB cost cross-check | Surfaced from CostDB — India vs US cost ratios |  | Done
Cross_Validation_Log | Consolidated xval logs | 5 countries — dataset agreement documentation |  | Done

## Yearsplit_ReNinja
Timeslices | Parameter.ID | Parameter | Unit | Projection.Mode | Projection.Parameter | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
S1D1 | 14 | YearSplit | fraction | User defined | 0 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644
S1D2 | 14 | YearSplit | fraction | User defined | 0 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329 | 0.12329
S1D3 | 14 | YearSplit | fraction | User defined | 0 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644 | 0.061644
S2D1 | 14 | YearSplit | fraction | User defined | 0 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014
S2D2 | 14 | YearSplit | fraction | User defined | 0 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603 | 0.12603
S2D3 | 14 | YearSplit | fraction | User defined | 0 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014 | 0.063014
S3D1 | 14 | YearSplit | fraction | User defined | 0 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562
S3D2 | 14 | YearSplit | fraction | User defined | 0 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712 | 0.16712
S3D3 | 14 | YearSplit | fraction | User defined | 0 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562
S4D1 | 14 | YearSplit | fraction | User defined | 0 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781
S4D2 | 14 | YearSplit | fraction | User defined | 0 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562 | 0.083562
S4D3 | 14 | YearSplit | fraction | User defined | 0 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781 | 0.041781
Note on G2: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.055556
Note on G3: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.076389
Note on G4: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.034722
Note on G5: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.111111
Note on G6: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.152778
Note on G7: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.069444
Note on G8: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.055556
Note on G9: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.076389
Note on G10: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.034722
Note on G11: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.111111
Note on G12: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.152778
Note on G13: Source: compiled_reninja_ts.csv (2014-2022 mean) Hour mapping: D1=Night(00-06), D2=Day(06-18), D3=Evening(18-24) Season mapping: S1=Winter(Dec-Feb), S2=Pre-monsoon(Mar-May), S3=SW Monsoon(Jun-Sep), S4=Post-monsoon(Oct-Nov) Template value: 0.069444

## Validation_ThermalDispatch
THERMAL DISPATCH VALIDATION DATA (not OSeMOSYS input)
These observed dispatch CFs are for validating model outputs, not constraining the optimizer.
Thermal plants are dispatchable in OSeMOSYS — the model chooses their output based on costs and constraints.
BANGLADESH — Observed Dispatch CFs
Source: BGD_DA_Final.xlsx, 1_OSTRAM_Profiles. PGCB daily reports 2023-2026 (1140 files).
Timeslice | Season | Band | Gas (11850 MW) | Coal (5417 MW) | Oil_HFO (5831 MW) | Oil_HSD (443 MW) | Hydro (230 MW)
S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.3484 | 0.4207 | 0.0271 | 0.0086 | 0.2049
S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.3592 | 0.4795 | 0.1224 | 0.0248 | 0.2088
S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.374 | 0.5303 | 0.203 | 0.0258 | 0.2124
S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.4854 | 0.5663 | 0.2079 | 0.0863 | 0.1232
S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.4785 | 0.537 | 0.2127 | 0.0871 | 0.1401
S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.4955 | 0.5999 | 0.3873 | 0.1067 | 0.145
S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.4912 | 0.68 | 0.2685 | 0.2087 | 0.7118
S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.4728 | 0.6295 | 0.222 | 0.1805 | 0.7053
S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.4862 | 0.69 | 0.4368 | 0.221 | 0.72
S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.4114 | 0.5487 | 0.1232 | 0.007 | 0.6734
S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.4096 | 0.5455 | 0.1432 | 0.015 | 0.6638
S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.4238 | 0.6105 | 0.3136 | 0.0107 | 0.6753
SRI LANKA — Observed Dispatch CFs
Source: LKA_DA_Final.xlsx, 1_OSTRAM_Profiles. PUCSL 15-min dispatch data 2023 (363 daily sheets).
Timeslice | Season | Band | Coal (900 MW) | Oil_CEB (710 MW) | Oil_IPP (420 MW) | Major_Hydro (1384 MW) | Wind (128 MW) | Solar | Mini_Hydro | Biomass
S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.5718 | 0.158 | 0.1073 | 0.3357 | 0.3363 | 0.0008 | 0.3235 | 0.1832
S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.606 | 0.2078 | 0.2099 | 0.4808 | 0.4378 | 0.1058 | 0.315 | 0.1912
S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.6074 | 0.2084 | 0.2404 | 0.507 | 0.4329 | 0 | 0.3131 | 0.1763
S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.7451 | 0.2922 | 0.3255 | 0.1692 | 0.3456 | 0 | 0.188 | 0.0949
S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.7529 | 0.3787 | 0.4583 | 0.2895 | 0.332 | 0.0806 | 0.1833 | 0.1031
S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.7646 | 0.4074 | 0.4561 | 0.3754 | 0.3913 | 0 | 0.1877 | 0.1001
S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.5281 | 0.3878 | 0.3475 | 0.1814 | 0.9552 | -0.0003 | 0.3503 | 0.1202
S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.5393 | 0.5347 | 0.5108 | 0.2702 | 0.8542 | 0.0822 | 0.3457 | 0.1045
S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.5511 | 0.5641 | 0.5537 | 0.3278 | 1.0196 | -0.0005 | 0.3542 | 0.1133
S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.3871 | 0.0338 | 0.0024 | 0.4793 | 0.2306 | 0 | 0.2778 | 0.2884
S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.4607 | 0.0781 | 0.0608 | 0.6477 | 0.2637 | 0.0895 | 0.2854 | 0.2414
S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.4692 | 0.0832 | 0.0928 | 0.6914 | 0.259 | 0 | 0.3029 | 0.2683
⚠ INDIA — No sub-annual thermal dispatch data yet. See India thermal search prompt.

## Capacities_CF_Options
Tech Code | Tech Name | Timeslice | Season | Daypart | Option A: Template (pre-integration) | Option B: Renewables.ninja (2014-2022 mean) | Option C: DA_Final (country-verified) | Difference A-B | Recommendation | Source Notes
Only shows techs where sources differ or where multiple options exist (solar, wind, hydro).
PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.248 | 0.3524 |  | -0.1044 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.324 | 0.3797 |  | -0.0557 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.299 | 0.2891 |  | 0.0099 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVBDXX01 | Solar PV (utility-scale), Bangladesh, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.36 | 0.3421 |  | 0.0179 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.16 | 0.4787 |  | -0.3187 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.18 | 0.4623 |  | -0.2823 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.145 | 0.3364 |  | -0.1914 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVBTXX01 | Solar PV (utility-scale), Bhutan, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.17 | 0.4433 |  | -0.2733 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.46 | 0.3474 |  | 0.1126 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.49 | 0.4196 |  | 0.0704 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.4 | 0.3756 |  | 0.0244 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_NXX01 | Solar PV (utility-scale), India – North, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.45 | 0.3503 |  | 0.0997 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.5 | 0.4307 |  | 0.0693 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.52 | 0.3957 |  | 0.1243 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.42 | 0.3231 |  | 0.0969 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_SXX01 | Solar PV (utility-scale), India – South, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.475 | 0.3642 |  | 0.1108 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.44 | 0.3516 |  | 0.0884 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.47 | 0.3866 |  | 0.0834 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.38 | 0.2645 |  | 0.1155 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_EXX01 | Solar PV (utility-scale), India – East, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.43 | 0.3348 |  | 0.0952 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.49 | 0.4 |  | 0.09 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.51 | 0.4284 |  | 0.0816 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.415 | 0.3235 |  | 0.0915 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_WXX01 | Solar PV (utility-scale), India – West, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.47 | 0.3588 |  | 0.1112 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.41 | 0.3603 |  | 0.0497 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.44 | 0.3829 |  | 0.0571 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.37 | 0.2896 |  | 0.0804 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVIN_NEXX01 | Solar PV (utility-scale), India – Northeast, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.405 | 0.356 |  | 0.049 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.262 | 0.422 |  | -0.16 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.262 | 0.4451 |  | -0.1831 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.262 | 0.3449 |  | -0.0829 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVNPXX01 | Solar PV (utility-scale), Nepal, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.262 | 0.4253 |  | -0.1633 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.43 | 0.3758 |  | 0.0542 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.45 | 0.3307 |  | 0.1193 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.34 | 0.3036 |  | 0.0364 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVLKXX01 | Solar PV (utility-scale), Sri Lanka, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.38 | 0.2942 |  | 0.0858 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.393 | 0.3533 |  | 0.0397 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.393 | 0.3372 |  | 0.0558 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.393 | 0.2915 |  | 0.1015 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPVMVXX01 | Solar PV (utility-scale), Maldives, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.393 | 0.3098 |  | 0.0832 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.248 | 0.2995 |  | -0.0515 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.299 | 0.2457 |  | 0.0533 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRBDXX01 | Solar PV (rooftop/distributed), Bangladesh, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.36 | 0.2908 |  | 0.0692 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.16 | 0.4069 |  | -0.2469 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.18 | 0.3929 |  | -0.2129 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.145 | 0.2859 |  | -0.1409 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRBTXX01 | Solar PV (rooftop/distributed), Bhutan, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.17 | 0.3768 |  | -0.2068 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.46 | 0.2953 |  | 0.1647 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.49 | 0.3567 |  | 0.1333 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.4 | 0.3193 |  | 0.0807 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_NXX01 | Solar PV (rooftop/distributed), India – North, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.45 | 0.2977 |  | 0.1523 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.5 | 0.3661 |  | 0.1339 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.52 | 0.3364 |  | 0.1836 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.42 | 0.2746 |  | 0.1454 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_SXX01 | Solar PV (rooftop/distributed), India – South, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.475 | 0.3095 |  | 0.1654 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.44 | 0.2989 |  | 0.1411 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.47 | 0.3286 |  | 0.1414 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.38 | 0.2248 |  | 0.1552 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_EXX01 | Solar PV (rooftop/distributed), India – East, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.43 | 0.2846 |  | 0.1454 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.49 | 0.34 |  | 0.15 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.51 | 0.3642 |  | 0.1458 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.415 | 0.275 |  | 0.14 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_WXX01 | Solar PV (rooftop/distributed), India – West, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.47 | 0.3049 |  | 0.1651 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.41 | 0.3063 |  | 0.1037 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.44 | 0.3254 |  | 0.1146 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.37 | 0.2462 |  | 0.1238 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRIN_NEXX01 | Solar PV (rooftop/distributed), India – Northeast, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.405 | 0.3026 |  | 0.1024 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.262 | 0.3587 |  | -0.0967 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.262 | 0.3784 |  | -0.1164 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.262 | 0.2931 |  | -0.0311 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRNPXX01 | Solar PV (rooftop/distributed), Nepal, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.262 | 0.3615 |  | -0.0995 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.43 | 0.3194 |  | 0.1106 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.45 | 0.2811 |  | 0.1689 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.34 | 0.2581 |  | 0.0819 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRLKXX01 | Solar PV (rooftop/distributed), Sri Lanka, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.38 | 0.2501 |  | 0.1299 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.393 | 0.3003 |  | 0.0927 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.393 | 0.2866 |  | 0.1064 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.393 | 0.2477 |  | 0.1453 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRSPRMVXX01 | Solar PV (rooftop/distributed), Maldives, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.393 | 0.2634 |  | 0.1296 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.12 | 0.1827 |  | -0.0627 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.12 | 0.073 |  | 0.047 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.12 | 0.1776 |  | -0.0576 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.18 | 0.3122 |  | -0.1322 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.18 | 0.1885 |  | -0.0085 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.18 | 0.4045 |  | -0.2245 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.36 | 0.3461 |  | 0.0139 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.36 | 0.3106 |  | 0.0494 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.36 | 0.3991 |  | -0.0391 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.14 | 0.1246 |  | 0.0154 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.14 | 0.0613 |  | 0.0787 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBDXX01 | Onshore Wind, Bangladesh, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.14 | 0.1085 |  | 0.0315 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.2 | 0.0149 |  | 0.1851 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.2 | 0.0898 |  | 0.1102 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.2 | 0.0088 |  | 0.1912 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.2 | 0.0218 |  | 0.1782 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.2 | 0.157 |  | 0.043 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.2 | 0.0376 |  | 0.1624 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.2 | 0.0505 |  | 0.1495 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.2 | 0.147 |  | 0.053 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.2 | 0.0902 |  | 0.1098 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.2 | 0.0123 |  | 0.1877 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.2 | 0.0603 |  | 0.1397 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONBTXX01 | Onshore Wind, Bhutan, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.2 | 0.0178 |  | 0.1822 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.18 | 0.3525 |  | -0.1725 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.18 | 0.193 |  | -0.013 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.18 | 0.3697 |  | -0.1897 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.25 | 0.3756 |  | -0.1256 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.25 | 0.2353 |  | 0.0147 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.25 | 0.4159 |  | -0.1659 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.32 | 0.2661 |  | 0.0539 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.32 | 0.2024 |  | 0.1176 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.32 | 0.2449 |  | 0.0751 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.22 | 0.24 |  | -0.02 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.22 | 0.1439 |  | 0.0761 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NXX01 | Onshore Wind, India – North, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.22 | 0.2523 |  | -0.0323 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.15 | 0.3006 |  | -0.1506 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.15 | 0.236 |  | -0.086 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.15 | 0.6001 |  | -0.4501 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.24 | 0.3022 |  | -0.0622 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.24 | 0.1978 |  | 0.0422 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.24 | 0.493 |  | -0.253 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.33 | 0.4714 |  | -0.1414 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.33 | 0.5809 |  | -0.2509 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.33 | 0.4876 |  | -0.1576 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.2 | 0.2601 |  | -0.0601 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.2 | 0.2646 |  | -0.0646 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_SXX01 | Onshore Wind, India – South, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.2 | 0.3699 |  | -0.1699 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.2 | 0.2451 |  | -0.0451 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.2 | 0.1191 |  | 0.0809 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.2 | 0.1672 |  | 0.0328 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.2 | 0.3444 |  | -0.1444 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.2 | 0.2689 |  | -0.0689 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.2 | 0.4717 |  | -0.2717 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.2 | 0.3355 |  | -0.1355 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.2 | 0.323 |  | -0.123 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.2 | 0.4372 |  | -0.2372 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.2 | 0.1851 |  | 0.0149 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.2 | 0.0876 |  | 0.1124 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_EXX01 | Onshore Wind, India – East, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.2 | 0.1278 |  | 0.0722 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.22 | 0.3138 |  | -0.0938 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.22 | 0.1748 |  | 0.0452 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.22 | 0.3366 |  | -0.1166 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.27 | 0.1224 |  | 0.1476 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.27 | 0.2174 |  | 0.0526 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.27 | 0.2622 |  | 0.0078 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.36 | 0.4692 |  | -0.1092 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.36 | 0.4968 |  | -0.1368 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.36 | 0.4584 |  | -0.0984 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.24 | 0.3102 |  | -0.0702 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.24 | 0.146 |  | 0.094 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_WXX01 | Onshore Wind, India – West, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.24 | 0.2168 |  | 0.0232 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.2 | 0.3117 |  | -0.1117 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.2 | 0.1437 |  | 0.0563 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.2 | 0.3179 |  | -0.1179 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.2 | 0.4255 |  | -0.2255 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.2 | 0.2802 |  | -0.0802 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.2 | 0.3998 |  | -0.1998 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.2 | 0.2242 |  | -0.0242 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.2 | 0.1719 |  | 0.0281 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.2 | 0.2299 |  | -0.0299 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.2 | 0.2287 |  | -0.0287 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.2 | 0.0961 |  | 0.1039 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONIN_NEXX01 | Onshore Wind, India – Northeast, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.2 | 0.2112 |  | -0.0112 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.2 | 0.0112 |  | 0.1888 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.2 | 0.0358 |  | 0.1642 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.2 | 0.0106 |  | 0.1894 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.2 | 0.0232 |  | 0.1768 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.2 | 0.0709 |  | 0.1291 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.2 | 0.0242 |  | 0.1759 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.2 | 0.0132 |  | 0.1868 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.2 | 0.0458 |  | 0.1542 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.2 | 0.0278 |  | 0.1722 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.2 | 0.0057 |  | 0.1943 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.2 | 0.0131 |  | 0.1869 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONNPXX01 | Onshore Wind, Nepal, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.2 | 0.0068 |  | 0.1932 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.24 | 0.3602 | 0.3363 | -0.1202 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.24 | 0.2657 | 0.4378 | -0.0257 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.24 | 0.3704 | 0.4329 | -0.1304 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.35 | 0.2454 | 0.3456 | 0.1046 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.35 | 0.2144 | 0.332 | 0.1356 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.35 | 0.2453 | 0.3913 | 0.1047 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.52 | 0.6386 | 0.9552 | -0.1186 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.52 | 0.5911 | 0.8542 | -0.0711 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.52 | 0.5925 | 1.0196 | -0.0725 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.3 | 0.2973 | 0.2306 | 0.0027 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.3 | 0.274 | 0.2637 | 0.026 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONLKXX01 | Onshore Wind, Sri Lanka, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.3 | 0.288 | 0.259 | 0.012 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.2 | 0.2197 |  | -0.0197 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.2 | 0.2336 |  | -0.0336 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.2 | 0.2403 |  | -0.0403 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.2 | 0.2355 |  | -0.0355 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.2 | 0.2354 |  | -0.0354 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.2 | 0.2346 |  | -0.0346 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.2 | 0.2358 |  | -0.0358 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.2 | 0.2306 |  | -0.0306 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.2 | 0.2291 |  | -0.0291 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.2 | 0.3093 |  | -0.1093 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.2 | 0.3146 |  | -0.1146 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWONMVXX01 | Onshore Wind, Maldives, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.2 | 0.3002 |  | -0.1002 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.195 | 0.3006 |  | -0.1056 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.195 | 0.236 |  | -0.041 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.195 | 0.6001 |  | -0.4051 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.312 | 0.3022 |  | 0.0098 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.312 | 0.1978 |  | 0.1142 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.312 | 0.493 |  | -0.181 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.429 | 0.4714 |  | -0.0424 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.429 | 0.5809 |  | -0.1519 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.429 | 0.4876 |  | -0.0586 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_SXX01 | Offshore Wind, India – South, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.26 | 0.3699 |  | -0.1099 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.275 | 0.3138 |  | -0.0388 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.275 | 0.1748 |  | 0.1002 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.275 | 0.3366 |  | -0.0616 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.3375 | 0.1224 |  | 0.2151 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.3375 | 0.2174 |  | 0.1201 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.3375 | 0.2622 |  | 0.0753 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.45 | 0.4692 |  | -0.0192 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.45 | 0.4968 |  | -0.0468 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.45 | 0.4584 |  | -0.0084 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.3 | 0.3102 |  | -0.0102 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.3 | 0.146 |  | 0.154 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_WXX01 | Offshore Wind, India – West, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.3 | 0.2168 |  | 0.0832 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.25 | 0.1191 |  | 0.1309 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.25 | 0.1672 |  | 0.0828 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.25 | 0.3444 |  | -0.0944 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.25 | 0.2689 |  | -0.0189 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.25 | 0.4717 |  | -0.2217 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.25 | 0.3355 |  | -0.0855 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.25 | 0.323 |  | -0.073 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.25 | 0.4372 |  | -0.1872 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.25 | 0.1851 |  | 0.0649 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.25 | 0.0876 |  | 0.1624 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFIN_EXX01 | Offshore Wind, India – East, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.25 | 0.1278 |  | 0.1222 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.15 | 0.1827 |  | -0.0327 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.15 | 0.073 |  | 0.077 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.15 | 0.1776 |  | -0.0276 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.225 | 0.3122 |  | -0.0872 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.225 | 0.1885 |  | 0.0365 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.225 | 0.4045 |  | -0.1795 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.45 | 0.3461 |  | 0.1039 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.45 | 0.3106 |  | 0.1394 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.45 | 0.3991 |  | 0.0509 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.175 | 0.1246 |  | 0.0504 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.175 | 0.0613 |  | 0.1137 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFBDXX01 | Offshore Wind, Bangladesh, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.175 | 0.1085 |  | 0.0664 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.288 | 0.3602 | 0.3363 | -0.0722 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.288 | 0.2657 | 0.4378 | 0.0223 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.288 | 0.3704 | 0.4329 | -0.0824 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.42 | 0.2454 | 0.3456 | 0.1746 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.42 | 0.2144 | 0.332 | 0.2056 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.42 | 0.2453 | 0.3913 | 0.1747 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.624 | 0.6386 | 0.9552 | -0.0146 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.624 | 0.5911 | 0.8542 | 0.0329 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.624 | 0.5925 | 1.0196 | 0.0315 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.36 | 0.2973 | 0.2306 | 0.0627 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.36 | 0.274 | 0.2637 | 0.086 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFLKXX01 | Offshore Wind, Sri Lanka, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.36 | 0.288 | 0.259 | 0.072 | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.24 | 0.2197 |  | 0.0203 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.24 | 0.2336 |  | 0.0064 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.24 | 0.2346 |  | 0.0054 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.24 | 0.2306 |  | 0.0094 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.24 | 0.2291 |  | 0.0109 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.24 | 0.3093 |  | -0.0693 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.24 | 0.3146 |  | -0.0746 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRWOFMVXX01 | Offshore Wind, Maldives, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.24 | 0.3002 |  | -0.0602 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.25 |  | 0.25 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.25 |  | 0.26 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.25 |  | 0.26 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.4 |  | 0.33 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.4 |  | 0.35 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.4 |  | 0.35 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.8 |  | 0.85 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.8 |  | 0.88 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.8 |  | 0.88 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.65 |  | 0.58 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.65 |  | 0.6 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRNPXX01 | Hydro – Reservoir, Nepal, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.65 |  | 0.6 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.25 |  | 0.1952 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.25 |  | 0.2096 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.25 |  | 0.2117 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.4 |  | 0.1851 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.4 |  | 0.1988 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.4 |  | 0.2007 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.8 |  | 0.8201 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.8 |  | 0.8805 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.8 |  | 0.8891 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.65 |  | 0.5986 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.65 |  | 0.6427 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRBTXX01 | Hydro – Reservoir, Bhutan, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.65 |  | 0.649 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: BTN_DA_Final BPSO Q1-Q4 2024 ex-bus
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.3 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.3 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.3 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.45 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.45 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.45 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.75 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.75 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.75 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.6 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.6 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NXX01 | Hydro – Reservoir, India – North, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.6 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.28 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.28 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.28 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.42 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.42 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.42 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.78 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.78 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.78 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.62 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.62 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_NEXX01 | Hydro – Reservoir, India – Northeast, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.62 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.3 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.3 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.3 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.4 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.4 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.4 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.7 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.7 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.7 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.55 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.55 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRIN_EXX01 | Hydro – Reservoir, India – East, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.55 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.3 |  | 0.3357 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.3 |  | 0.4808 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.3 |  | 0.507 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.3 |  | 0.1692 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.3 |  | 0.2895 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.3 |  | 0.3754 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.4 |  | 0.1814 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.4 |  | 0.2702 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.4 |  | 0.3278 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.55 |  | 0.4793 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.55 |  | 0.6477 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHDRLKXX01 | Hydro – Reservoir, Sri Lanka, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.55 |  | 0.6914 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: LKA_DA_Final PUCSL 15-min 2023
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.15 |  | 0.25 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.15 |  | 0.26 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.15 |  | 0.26 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.35 |  | 0.33 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.35 |  | 0.35 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.35 |  | 0.35 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.85 |  | 0.85 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.85 |  | 0.88 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.85 |  | 0.88 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.65 |  | 0.58 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.65 |  | 0.6 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHRONPXX01 | Hydro – Run-of-River, Nepal, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.65 |  | 0.6 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.15 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.15 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.15 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.35 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.35 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.35 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.85 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.85 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.85 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.65 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.65 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROBTXX01 | Hydro – Run-of-River, Bhutan, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.65 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.18 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.18 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.18 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.38 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.38 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.38 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.8 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.8 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.8 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.6 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.6 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NXX01 | Hydro – Run-of-River, India – North, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.6 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.2 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.2 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.2 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.4 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.4 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.4 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.82 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.82 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.82 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.62 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.62 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHROIN_NEXX01 | Hydro – Run-of-River, India – Northeast, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.62 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_SXX01 | Hydro – Pumped Storage, India – South, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_WXX01 | Hydro – Pumped Storage, India – West, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSIN_NXX01 | Hydro – Pumped Storage, India – North, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 1 |  | 0.2 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 1 |  | 0.35 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 1 |  | 0.55 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 1 |  | 0.25 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 1 |  | 0.4 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 1 |  | 0.6 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 1 |  | 0.55 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 1 |  | 0.7 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 1 |  | 0.85 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 1 |  | 0.4 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 1 |  | 0.55 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSNPXX01 | Hydro – Pumped Storage, Nepal, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 1 |  | 0.7 |  | Use Option C (country-verified dispatch data) | A: pre-integration template (source unknown) ¦ C: NP_DA_Final NEA FY2079/80 + NREL hourly
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S1D1 | Winter (Dec-Feb) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRHPSLKXX01 | Hydro – Pumped Storage, Sri Lanka, region XX (investable) | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 1 |  |  |  | Either — values agree within 5pp | A: pre-integration template (source unknown)
PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.5 | 0.4307 |  | 0.0693 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.52 | 0.3957 |  | 0.1243 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.42 | 0.3231 |  | 0.0969 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVIN_SXX01 | Floating Solar PV, India – South, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.475 | 0.3642 |  | 0.1108 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.44 | 0.3516 |  | 0.0884 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.47 | 0.3866 |  | 0.0834 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.38 | 0.2645 |  | 0.1155 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVIN_EXX01 | Floating Solar PV, India – East, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.43 | 0.3348 |  | 0.0952 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.248 | 0.3524 |  | -0.1044 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.324 | 0.3797 |  | -0.0557 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.299 | 0.2891 |  | 0.0099 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVBDXX01 | Floating Solar PV, Bangladesh, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.36 | 0.3421 |  | 0.0179 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.43 | 0.3758 |  | 0.0542 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.45 | 0.3307 |  | 0.1193 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.34 | 0.3036 |  | 0.0364 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVLKXX01 | Floating Solar PV, Sri Lanka, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.38 | 0.2942 |  | 0.0858 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.393 | 0.3533 |  | 0.0397 | Either — values agree within 5pp | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.393 | 0.3372 |  | 0.0558 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.393 | 0.2915 |  | 0.1015 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
PWRFPVMVXX01 | Floating Solar PV, Maldives, region XX (investable) | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.393 | 0.3098 |  | 0.0832 | Review — >5pp difference between A and B | A: pre-integration template (source unknown) ¦ B: compiled_reninja_ts.csv, lat/lon from file, 2014-2022 mean
BHUTAN HYDRO — DUAL OPTIONS
Option A: BPSO Q1-Q4 2024 ex-bus generation (annual CF≈0.453)
Option B: Scaled to match IRENA 2023 annual utilization (52%), factor=1.148
Difference: BPSO 2024 may reflect a below-average water year, or IRENA uses different installed capacity denominator.
Tech | Timeslice | Season | Daypart | Option A: BPSO 2024 | Option B: IRENA-scaled | Difference | Source A | Source B
PWRHDRBTXX01 / PWRHROBTXX01 | S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.1952 | 0.2241 | 0.0289 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.2096 | 0.2406 | 0.031 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.2117 | 0.243 | 0.0313 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.1851 | 0.2125 | 0.0274 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.1988 | 0.2282 | 0.0294 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.2007 | 0.2304 | 0.0297 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.8201 | 0.9414 | 0.1213 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.8805 | 1 | 0.1195 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.8891 | 1 | 0.1109 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.5986 | 0.6871 | 0.0885 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.6427 | 0.7378 | 0.0951 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025
PWRHDRBTXX01 / PWRHROBTXX01 | S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.649 | 0.745 | 0.096 | BPSO Q1-Q4 2024 ex-bus + quarterly IC | Scaled from BPSO shape × (0.52/0.453). IRENA Energy Profile Bhutan Sep 2025

## Provenance_Matrix
OSTRAM DATA PROVENANCE MATRIX
Maps every template parameter to its source file(s), processing chain, and verification status.
Green = verified/cross-validated ¦ Yellow = single source or unverified ¦ Red = missing ¦ Grey = N/A by design ¦ Blue = derived
Template Sheet | Parameter | Node/Tech | Source File(s) | Source Sheet(s) | Processing | Verification | Status | Action Needed
Capacities_CF | CapacityFactor — Solar PV | BD,BT,IN×5,LK,MV,NP | compiled_reninja_ts.csv + SOASIA_Template_v1 (original) | N/A (CSV) / Capacities_CF | 9-year mean (2014-2022) from Renewables.ninja hourly simulations | Resolved: Renewables.ninja values adopted. Previous template values documented in comments. | VERIFIED | None — resolved
Capacities_CF | CapacityFactor — Wind Onshore | BD,BT,IN×5,LK,MV,NP | compiled_reninja_ts.csv + SOASIA_Template_v1 | N/A (CSV) / Capacities_CF | 9-year mean from Renewables.ninja | Resolved: Renewables.ninja values adopted for all nodes. | VERIFIED | None — resolved
Capacities_CF | CapacityFactor — Wind Offshore | BD,IN_E,IN_S,IN_W,LK,MV | SOASIA_Template_v1 (original) | Capacities_CF | Unknown — pre-existing values (0.24-0.624) | ⚠ NO cross-validation. Renewables.ninja covers onshore only. | UNVERIFIED | Verify against literature (e.g. WB/NREL offshore wind roadmaps) or MERRA-2 reanalysis
Capacities_CF | CapacityFactor — Hydro Reservoir | IN_N,IN_NE,IN_E,LK | SOASIA_Template_v1 (original) + LKA_DA_Final | Capacities_CF / 1_OSTRAM_Profiles | LKA from PUCSL 15-min dispatch 2023. India values pre-existing (likely OSeMOSYS Global). | LKA: VERIFIED (PUCSL). India: ⚠ UNVERIFIED. | PARTIAL | India hydro: validate against CEA/CWC monthly generation data
Capacities_CF | CapacityFactor — Hydro RoR | IN_N,IN_NE,NP,BT | NP_DA_Final + BTN_DA_Final + SOASIA_Template_v1 | 1_OSTRAM_Profiles | NP: NEA FY2079/80 gen + NREL hourly. BT: BPSO Q1-Q4 2024 ex-bus. India: pre-existing. | NP: VERIFIED. BT: VERIFIED. India: ⚠ UNVERIFIED. | PARTIAL | India RoR: validate against CEA/CWC data
Capacities_CF | CapacityFactor — Hydro Pumped Storage | IN_N,IN_S,IN_W,NP,LK | NP_DA_Final + SOASIA_Template_v1 | 1_OSTRAM_Profiles | NP from Kulekhani dispatch pattern (ESTIMATED). India/LK = 1.0 (pre-existing). | NP: MEDIUM confidence (estimated). India: ⚠ UNVERIFIED. | PARTIAL | Review India HPS dispatch against pumped storage operational data
Capacities_CF | CapacityFactor — CSP | IN×5, LK | SOASIA_Template_v1 (original) | Capacities_CF | Unknown — pre-existing values (0.35-0.48) | ⚠ No source identified. Likely from DNI dataset. | UNVERIFIED | Verify against Solargis/NREL NSRDB DNI data
Capacities_CF | CapacityFactor — Tidal | IN_S, LK | SOASIA_Template_v1 (original) | Capacities_CF | Fixed 0.25 estimate — pre-existing | ⚠ No source. Minimal tidal deployment in region. | UNVERIFIED | Low priority — no significant tidal capacity planned
Capacities_CF | CapacityFactor — Rooftop Solar | All 10 nodes | Derived from PWRSPV values | N/A | SPR = 0.85 × SPV (suboptimal tilt/azimuth/shading assumption) | 0.85 factor is assumed, not measured. Literature range: 0.80-0.90. | DERIVED | Document 0.85 assumption in methodology. Consider sensitivity analysis.
Capacities_CF | CapacityFactor — Storage (LDS/SDS) | All nodes | N/A — by design | N/A | CF=1.0 (storage available all timeslices; optimizer decides charge/discharge) | Correct for OSeMOSYS. Not a physical CF — conceptual availability. | BY DESIGN | None
Demand_Profiles | SpecifiedDemandProfile | BD | BGD_DA_Final.xlsx | 1_OSTRAM_Profiles (Section B) | 2024 PGCB hourly data → timeslice aggregation | Cross-validated against 2023 & 2025 daily report profiles. Max deviation 1.1%. | VERIFIED | None
Demand_Profiles | SpecifiedDemandProfile | BT | BTN_DA_Final.xlsx | 1_OSTRAM_Profiles (Section A) | BPSO 2023 quarterly × BPC Table 5.20 hourly. S2/S4 daypart interpolated. | Cross-validated against 2024 Jan-Sep. Shape consistent despite 1.1-1.6× growth. | VERIFIED | S2/S4 dayparts are interpolated — flag as ESTIMATED
Demand_Profiles | SpecifiedDemandProfile | IN×5 | IND_DA_Final.xlsx | Demand Fractions | Raw hourly Grid-India demand 2023-2024 → timeslice fractions. No approximations. | Three-way comparison: file(IMD) vs POSOCO vs re-derived. December shape analyzed separately. | VERIFIED | None
Demand_Profiles | SpecifiedDemandProfile | LK | LKA_DA_Final.xlsx | 1_OSTRAM_Profiles (Section B) | PUCSL 15-min dispatch 2023 (363 daily sheets) → timeslice aggregation. | Total: 15,274 GWh. Cross-validated in sheet 4_Cross_Validation. | VERIFIED | None
Demand_Profiles | SpecifiedDemandProfile | NP | NP_DA_Final.xlsx | 1_OSTRAM_Profiles (Section A) | NEA FY2079/80 monthly × NREL Table 1 hourly shape. | Cross-validated against 818 NDOR daily reports (±5.5%). See 5_Cross_Validation. | VERIFIED | None
Demand_Profiles | SpecifiedDemandProfile | MV | N/A — NOT YET PARAMETERIZED | N/A | Yearbook monthly production available (STELCO Table 12.2). Daypart splits need estimation. | ⚠ NOT DONE. See Maldives_Timeslice_README.md for assessment. | MISSING | Build from STELCO monthly production + tropical island diurnal profile
Demand_Projection | SpecifiedAnnualDemand (PJ) | BD | BGD_DA_Final, Bangladesh_new_data_v2_REV | 2_Demand_Forecasts | IEPMP 2023 growth rates applied to 2023 base (86,255 GWh → 310.5 PJ) | Cross-check: 310.5 PJ matches BPDB. 2030/2040/2050 consistent with IEPMP. | VERIFIED | None
Demand_Projection | SpecifiedAnnualDemand (PJ) | LK | SriLanka__new_data_v2 | Demand Forecast | CEB LTGEP 2025-2044 Table E1 growth trajectory | ⚠ Template=53.3 PJ (14,806 GWh) vs PUCSL=15,274 GWh (55.0 PJ). ~3% gap — likely T&D losses. | REVIEW | Reconcile: is template using net demand or gross generation?
Demand_Projection | SpecifiedAnnualDemand (PJ) | IN×5 | India_new_data_v2 | 2_Demand_Forecasts, 5_Demand_Energy_State, 6_Demand_Scenarios | CEA 20th EPS demand by state, allocated to 5 OSTRAM sub-regions | ⚠ Regional allocation method not documented in template. State-to-region mapping needed. | PARTIAL | Document the state→region mapping used for India demand splits
Demand_Projection | SpecifiedAnnualDemand (PJ) | NP | Nepal_new_data, NP_DA_Final | Demand Forecasts, 2_Monthly_Demand | NEA load forecast ~8.4%/yr from 2023 base (11,548 GWh → 40.7 PJ) | Template=40.7 PJ vs NEA=41.6 PJ. ~2% gap. | CLOSE | Minor — within rounding
Technology_Costs | CAPEX/FOM/VOM/etc | Generic (23 techs) | OSTRAM_Consolidated_CostDB_v2.xlsx | Technologies, Node_Anchors, Source_Registry | India anchor costs × node multipliers. Decline trajectories from NREL ATB 2024. | Source_Registry has 27 entries with URLs. ATB_Comparison sheet provides cross-check vs US costs. | VERIFIED | Fill 11 missing multiplier URLs (NP/BT solar, BD wind, BESS)
VariableCost | Fuel costs (USD/GJ) | All 60 fuel techs | OSTRAM_Consolidated_CostDB_v2.xlsx | Fuel_Costs | Conservative scenario. Coal: WB CMO + DESNZ. Gas: WB CMO + IEA WEO. Oil: WB Brent/6.12. | Full source chain: WB CMO Oct 2025 base → IEA WEO 2025 / DESNZ trajectories. | VERIFIED | None
Secondary_Techs | CapitalCost (node-specific) | 119 of 150 techs | OSTRAM_Consolidated_CostDB_v2.xlsx | Technologies × Node_Anchors | India base × node multiplier. Interpolated 2023-2050. | 31 empty = N/A (tech not applicable in that node, e.g. offshore wind in Nepal) | VERIFIED | None
Secondary_Techs | ResidualCapacity (GW) | 36 of 150 techs | DA_Final files, new_data files, CEA/CEB/NEA/BPC | Various installed capacity sheets | Converted MW → GW. India regional splits approximate. | ⚠ India splits are approximate (not from plant-level database). 114 empty = correctly zero or not yet set. | PARTIAL | India: build proper state→region plant aggregation from India_Electricity_Infrastructure.xlsx (1,870 plants)
Secondary_Techs | AvailabilityFactor | All 150 techs | Industry standards + CEA/CEB fleet data | N/A (standard values) | Standard AF by tech type (e.g. coal SC=0.85, CCGT=0.90, hydro=0.95) | Values are reasonable but not country-specific. India coal PLF data available in IND_DA_Final. | STANDARD | Could refine with IND_DA_Final Daily PLF sheet for India-specific AFs
Secondary_Techs | Efficiency | All 150 techs | CostDB Heat Rate + industry standards | Technologies sheet | Converted Heat Rate → efficiency where available, otherwise standard values | Reasonable for OSeMOSYS. Not country-specific. | STANDARD | Could refine coal efficiency from CEA fleet Heat Rate data
Existing_Generation | Plant inventory | 2,112 plants × 6 countries | *_Infrastructure.xlsx, *_Power_Sector.xlsx | Existing Generation sheets | Copied plant name, fuel, capacity, commissioning year from 6 Infrastructure files. | ⚠ India plants all mapped to IN_N (regional disaggregation not done). | PARTIAL | India: map 1,870 plants to correct sub-regions using state column
Planned_Generation | Pipeline inventory | 554 projects × 6 countries | *_Infrastructure.xlsx | Planned Generation sheets | Copied project name, fuel, capacity, expected COD. | Same India regional issue as Existing_Generation. | PARTIAL | Same — map India projects to sub-regions
Interconnectors | Corridor inventory | 25 corridors | OSTRAM_Consolidated_CostDB_v2.xlsx + Infrastructure files | Interconnectors + Existing/Planned Interconnections | Pre-populated in template. CostDB has cost data. | Cross-checkable against Infrastructure file interconnection sheets (not yet done). | PARTIAL | Cross-validate corridor list against 6 Infrastructure files
Interconnector_Params | CapitalCost, FixedCost | 13 corridors × 2 params | OSTRAM_Consolidated_CostDB_v2.xlsx | Interconnectors sheet | Direct transfer. Full source attribution per corridor. | Sources: ADB PADs, Nepal-India ETTP, PFCCL tender, WB estimates. | VERIFIED | None
RE_Targets_Policies | NDC/RE targets | All countries | SOASIA_Template_v1 (original) | RE_Targets_Policies | Pre-existing. Not updated. | ⚠ Not cross-validated against source files. | NOT UPDATED | Validate against new_data files and national NDC submissions
Emissions | Emission factors | All techs | SOASIA_Template_v1 (original) | Emissions | Pre-existing. Not updated. | ⚠ Not cross-validated. Likely from IPCC defaults or OSeMOSYS Global. | NOT UPDATED | Validate against IPCC 2006/2019 emission factors
N/A — SOURCE FILES NOT YET INTEGRATED
(unused) | Hourly load profiles | BT | BTN_DA_Final.xlsx | 3_Hourly_Profiles | BPC PDB 2024 Table 5.20 — 24-hour verified profiles (Dec/Jun) | Used indirectly for daypart splits. Raw hourly data available for finer analysis. | AVAILABLE | Could improve daypart splits or add sub-daily resolution
(unused) | River flow data | BT | BTN_DA_Final.xlsx | 5_River_Flows | NCHM long-term monthly mean river flows (m³/s) | Available for hydrological validation of hydro CFs. | AVAILABLE | Cross-validate hydro CFs against river flow seasonality
(unused) | Daily PLF + generation | IN | IND_DA_Final.xlsx | Daily PLF, Daily Generation, Monthly Installed Cap | 3,883 daily PLF records + 3,959 daily generation records (NITI Aayog ICED) | Available for India thermal validation and country-specific AF refinement. | AVAILABLE | Use for post-hoc validation; refine India AF values
(unused) | Cost trends | IN | IND_DA_Final.xlsx | Cost Trends | Power purchase cost trends by fuel type (Rs/kWh) from NITI Aayog ICED | Available for cross-validating CostDB fuel + VOM assumptions. | AVAILABLE | Cross-check against CostDB variable costs
(unused) | IRENA country profiles | BT, LK, IN | Bhutan_new_data_v2, SriLanka__new_data_v2, India_new_data_v2 | IRENA sheets (Capacity Factors, Historical Production, Demand) | IRENA national profiles — annual CFs, generation, demand | Available as independent cross-validation source. | AVAILABLE | Cross-validate annual CFs against IRENA published values
(unused) | Installed capacity time series | BD, NP | Bangladesh_new_data_v2_REV, Nepal_new_data | 5_Installed_Capacity | Historical installed capacity by tech (MW) — multi-year series | Available for building ResidualCapacity retirement profiles. | AVAILABLE | Use to model capacity retirement (currently set flat)
(unused) | Cross-validation logs | BD, BT, IN, LK, NP | All DA_Final files | *_Cross_Validation sheets | Systematic dataset-vs-dataset comparison results | Documents agreement levels between independent sources. | AVAILABLE | Reference when resolving ambiguities

## RE_Potential_Ceilings
RENEWABLE ENERGY POTENTIAL CEILINGS
Reference data for setting TotalAnnualMaxCapacity in Secondary_Techs (currently empty — scenario-specific).
These are physical/resource limits, not policy targets (see RE_Targets_Policies for those).
Node | Technology | OSTRAM Code | Max Potential (GW) | Basis | Source | URL | Confidence | Notes
IN_N | Solar PV | PWRSPVIN_NXX01 | 150 | MNRE solar potential assessment | MNRE / CEA NEP | https://mnre.gov.in | HIGH | Rajasthan+Gujarat solar parks. Land availability primary constraint.
IN_S | Solar PV | PWRSPVIN_SXX01 | 120 | MNRE solar potential | MNRE / CEA NEP | https://mnre.gov.in | HIGH | Karnataka+Tamil Nadu+AP.
IN_E | Solar PV | PWRSPVIN_EXX01 | 30 | MNRE solar potential | MNRE / CEA NEP | https://mnre.gov.in | MEDIUM | Lower irradiation; land competition.
IN_W | Solar PV | PWRSPVIN_WXX01 | 200 | MNRE solar potential | MNRE / CEA NEP | https://mnre.gov.in | HIGH | Gujarat+Maharashtra+Rajasthan (western part).
IN_NE | Solar PV | PWRSPVIN_NEXX01 | 10 | MNRE solar potential | MNRE / CEA NEP | https://mnre.gov.in | LOW | Limited land; cloud cover.
BD | Solar PV | PWRSPVBDXX01 | 15 | WB/SREDA assessment | WB Bangladesh Energy Sector | https://www.worldbank.org | MEDIUM | Land-scarce. Rooftop + floating PV primary pathways.
NP | Solar PV | PWRSPVNPXX01 | 5 | NEA estimates | NEA / Nepal_new_data |  | LOW | Mountain terrain limits utility-scale.
LK | Solar PV | PWRSPVLKXX01 | 10 | CEB LTGEP | CEB LTGEP 2025-2044 | https://www.ceb.lk | MEDIUM
BT | Solar PV | PWRSPVBTXX01 | 0.5 | PSMP estimate | Bhutan PSMP 2040 |  | LOW | Very limited; hydro-dominant system.
MV | Solar PV | PWRSPVMVXX01 | 0.5 | MCCEE Roadmap | MCCEE Energy Roadmap 2024-2033 | https://www.environment.gov.mv | MEDIUM | Island rooftop + floating. Land severely constrained.
IN_S | Wind Onshore | PWRWONIN_SXX01 | 100 | NIWE wind atlas | NIWE / CEA NEP | https://niwe.res.in | HIGH | Tamil Nadu+Karnataka primary wind belt.
IN_W | Wind Onshore | PWRWONIN_WXX01 | 120 | NIWE wind atlas | NIWE / CEA NEP | https://niwe.res.in | HIGH | Gujarat+Maharashtra wind belt.
IN_N | Wind Onshore | PWRWONIN_NXX01 | 15 | NIWE wind atlas | NIWE / CEA NEP | https://niwe.res.in | MEDIUM | Rajasthan.
LK | Wind Onshore | PWRWONLKXX01 | 5 | CEB LTGEP | CEB LTGEP 2025-2044 | https://www.ceb.lk | MEDIUM | Mannar, Puttalam corridors.
IN_S | Offshore Wind | PWRWOFIN_SXX01 | 35 | MNRE offshore target | CEA NEP / MNRE |  | MEDIUM | Gulf of Mannar, Tamil Nadu coast.
IN_W | Offshore Wind | PWRWOFIN_WXX01 | 35 | MNRE offshore target | CEA NEP / MNRE |  | MEDIUM | Gujarat coast.
NP | Hydro RoR | PWRHRONPXX01 | 40 | NEA technical potential | ADB Hydropower Development Nepal | https://www.adb.org/sites/default/files/publication/612641/hydropower-development-economic-growth-nepal.pdf | HIGH | 83 GW total technical; ~40 GW economically viable.
BT | Hydro (all) | PWRHDRBTXX01+PWRHROBTXX01 | 24 | PSMP technical potential | Bhutan PSMP 2040 / JICA | https://www.jica.go.jp | HIGH | 24 GW potential; 2.4 GW developed as of 2024.
BT | Hydro RoR | PWRHROBTXX01 | 12 | IRENA RE resource potential | Bhutan_new_data_v2 9_IRENA_RE_Resource_Potential |  | MEDIUM | IRENA estimate for small/RoR hydro.

## ATB_Comparison
NREL ATB 2024 vs OSTRAM Cost Cross-Check
Source: OSTRAM_Consolidated_CostDB_v2.xlsx ATB_Comparison sheet. ATB = US market costs; OSTRAM uses India anchor + country multipliers.
Technology | ATB_2023 | ATB_2030_M | ATB_2050_M | OSTRAM_2023_IN | OSTRAM_2023_LK | IN_vs_ATB | LK_vs_ATB | Notes
Solar PV (Utility) | 1611 | 1194 | 683 | 560 | 849 | 0.35x | 0.53x | India 65% below ATB. SL 47% below. India world-lowest.
Onshore Wind (Class 4) | 1786 | 1408 | 1115 | 761 | 1391 | 0.43x | 0.78x | India 57% below ATB. SL closer to ATB.
Offshore Wind (Class 3) | 6136 | 4450 | 3132 | 2339 | 3781 | 0.38x | 0.62x | Both SA anchors well below US ATB.
BESS 4h Li-ion | 2080 | 1451 | 1036 | 882 | 1330 | 0.42x | 0.64x | India SECI tenders driving rapid cost decline.
BESS 8h | 3685 | 2470 | 1688 | 1800 |  | 0.49x | N/A | SA closer to ATB for longer-duration storage.
CCGT (F-Frame) | 1487 | 1403 | 1191 | 700 | 1300 | 0.47x | 0.87x | SL LTGEP may include LNG terminal costs.
OCGT (F-Frame) | 1339 | 1271 | 1075 | 450 | 360 | 0.34x | 0.27x | Both SA anchors far below US ATB.
Coal-new (SC) | 4057 | 3906 | 3268 | 1059 | 2132 | 0.26x | 0.53x | India BHEL domestic mfg = 74% below ATB.
Nuclear (Large) |  | 7616 | 5013 | 2000 | 5103 | N/A | 0.67x | India PHWR: domestic program. SL near ATB Moderate.
Biopower (Dedicated) | 5341 | 4778 | 4136 | 1142 | 1782 | 0.21x | 0.33x | US biomass costs much higher than SA.
CSP (Class 2) | 7912 | 5180 | 4455 | 7912 | 7912 | 1.00x | 1.00x | No SA-specific data; ATB used directly.
Geothermal (Hydro/Flash) | 7097 | 6482 | 5735 | 4589 |  | 0.65x | N/A | IRENA global avg anchor below ATB.
PSH (Class 1) | 3224 | 3224 | 3224 | 635 |  | 0.20x | N/A | India CEA likely optimistic. ATB flat.
INTERPRETATION
IN_vs_ATB ratios below 1.0 indicate OSTRAM India costs are lower than US ATB — expected for solar/wind where India has lower labor and land costs. Ratios above 1.0 would indicate OSTRAM costs exceed US levels — worth investigating. Country multipliers (BD ×1.5, LK ×1.5-2.5, NP ×1.6, BT ×1.8, MV ×3.0) bring non-India nodes closer to or above ATB levels, reflecting smaller markets, logistics, and import dependence.

## Cross_Validation_Log
CONSOLIDATED CROSS-VALIDATION LOG
Extracted from DA_Final files. Documents agreement between independent data sources used in OSTRAM parameterization.
BGD — 6_Cross_Validation | Source: BGD_DA_Final.xlsx
BANGLADESH — CROSS-VALIDATION LOG
Three independent datasets compared. Discrepancies documented with explanations.
A. Datasets Used
Code | Dataset | Period | Records | Resolution | Key Strength
[S] | PGCB Hourly (UCI DOI:10.24432/C59P6V) | Apr 2015–Jun 2025 | 92,650 | Hourly by fuel type | Energy-weighted CFs; sub-daily resolution; solar accuracy
[D] | BPDB Daily Report Scrape | Jan 2023–Mar 2026 | 1,140 files | Daily by fuel type | Multi-year coverage; HFO/HSD split; fleet evolution
[P] | BPDB Plant Register (Feb 2026) | Feb 2026 snapshot | 138 plants | Plant-level | CCGT/OCGT split; exact nameplate capacity; technology type
B. Key Discrepancies and Resolutions
Item | [S] 2024 hourly | [D] 2023-26 daily | Resolution | Explanation
Solar daytime CF | 0.25–0.36 | 0.41–0.50 | Use [S] hourly | Daily reports capture peak snapshots, not energy-weighted averages. Hourly data integrates full D2 band.
Gas CF level | 0.31–0.47 | 0.35–0.49 | Use [D] multi-year | Slight offset from different capacity denominators. Multi-year average is more robust.
Coal S4 CF | 0.42–0.47 | 0.55–0.61 | Use [D] multi-year | 2023 had anomalously high coal S4 (0.83-0.94); multi-year average smooths this.
Hydro S2 CF | 0.12–0.15 | 0.12–0.15 (combined) | Confirmed | Both sources agree: S2 is below RELAC threshold. Year-by-year: 2023 severe (0.04), 2024 marginal, 2025 clear.
Hydro S3 CF | 0.76–0.78 | 0.71–0.72 | Use [D] multi-year | 2025 was wetter than 2024. Multi-year average preferred.
Import CF | 0.29–0.68 | 0.61–0.91 | Use [D] with 1800 MW cap | Adani disruption in 2024 suppresses [S]. [D] corrected to 1800 MW weighted-average denominator.
Wind S2 CF | 0.14–0.22 | 0.29–0.36 | Use [D] multi-year | 62 MW fleet is tiny; year-to-year variation is high. Multi-year is more representative.
Demand fractions | S3=38%, S1=19% | S3=36%, S1=23% | Use [S] 2024 hourly | [D] combined overweights winter (3.3 winters vs 3.0 monsoons). Individual years each show ~19-20% winter.
Oil_HSD capacity | 968 MW [P] | 443 MW [D] | Document both | [P] = nameplate incl. standby; [D] = actively dispatched only. Both valid for different purposes.
BTN — 7_Cross_Validation | Source: BTN_DA_Final.xlsx
BHUTAN — CROSS-VALIDATION LOG
Compares demand shape across datasets and documents the critical series-definition finding.
A. BPSO Two-Series Problem (CRITICAL FINDING)
Month | 2024 Accounting (sold to BPC) | 2024 Actual Consumption | 2023 Accounting | 2023 Actual Consumption | Notes
Jan | 567.26 | 587.7 | 309.48 | 376.82
Feb | 519.95 | 567.14 | 247.18 | 346.67
Mar | 706.46 | 589.27 | 289.67 | 380.09
Apr | 550.82 | 588.81 | 427.12 | 427.12
May | 554.52 | 601.09 | 489.06 | 489.06
Jun | 610.81 | 580.49 | 450.29 | 450.29
Jul | 654.66 | 611.73 | 475.61 | 475.61
Aug | 653.63 | 605.81 | 517.73 | 517.73
Sep | 610.2 | 579.67 | 538.96 | 538.96
Oct | 832.92 | — | 594.98 | 576.42 | Acct series shows spike (833); actual shows normal (576 in 2023)
Nov | 604.6 | — | 516.35 | 562.79
Dec | 454.78 | — | 383.41 | 602.43 | Acct shows trough (455/383); actual shows PEAK (602 in 2023)
CONCLUSION: The 'sold to BPC' series is an accounting/billing metric that does not reflect actual grid consumption timing. For demand profiling, ALWAYS use the 'actual consumption' series (Table 3.1.2/5.2, BPSO page 4).
B. Demand Shape Validation: 2023 vs PSMP 2017
| S1 Winter | S2 Pre-monsoon | S3 Monsoon | S4 Post-monsoon | Pattern
2023 actual (this file) | 0.231 | 0.226 | 0.345 | 0.198 | S3 > S1 > S2 > S4 (by total GWh)
2023 avg MW/month | 442 | 432 | 496 | 570 | S4 > S3 > S1 > S2 (by intensity)
PSMP 2017 avg MW peak | 305 | 325 | 343 | — | Rainy > Other > Dry
2024 Jan-Sep actual | 577 | 593 | 594 | — | Flat; winter grew most since 2023
IND — Demand Comparison | Source: IND_DA_Final.xlsx
Three-Way Comparison: File (IMD) vs POSOCO Estimate vs Exact Hourly
File(IMD): from india_demand_timeslices.xlsx (IMD seasons, avg 2023-2024). POSOCO Est: POSOCO daily + file daypart blend. Exact: raw hourly data, OSeMOSYS seasons.
Region | Season | DayPart | File (IMD) | POSOCO Est | Exact
India_East | S1_Winter | D1_Night | 0.03051 | 0.04663 | 0.04448
India_East | S1_Winter | D2_Day | 0.07073 | 0.10558 | 0.10493
India_East | S1_Winter | D3_Evening | 0.03624 | 0.05478 | 0.05355
India_East | S2_PreMonsoon | D1_Night | 0.06171 | 0.06402 | 0.0608
India_East | S2_PreMonsoon | D2_Day | 0.12503 | 0.12971 | 0.12377
India_East | S2_PreMonsoon | D3_Evening | 0.0668 | 0.06931 | 0.06643
India_East | S3_SWMonsoon | D1_Night | 0.09642 | 0.09416 | 0.09683
India_East | S3_SWMonsoon | D2_Day | 0.18523 | 0.18086 | 0.18517
India_East | S3_SWMonsoon | D3_Evening | 0.10105 | 0.09868 | 0.10176
India_East | S4_PostMonsoon | D1_Night | 0.05254 | 0.03629 | 0.0389
India_East | S4_PostMonsoon | D2_Day | 0.11336 | 0.07829 | 0.07987
India_East | S4_PostMonsoon | D3_Evening | 0.06035 | 0.04168 | 0.04351
India_North | S1_Winter | D1_Night | 0.02791 | 0.0425 | 0.03999
India_North | S1_Winter | D2_Day | 0.07903 | 0.11643 | 0.11685
India_North | S1_Winter | D3_Evening | 0.03656 | 0.05415 | 0.05356
India_North | S2_PreMonsoon | D1_Night | 0.0519 | 0.05405 | 0.0519
India_North | S2_PreMonsoon | D2_Day | 0.1171 | 0.12222 | 0.12239
India_North | S2_PreMonsoon | D3_Evening | 0.05861 | 0.06106 | 0.05888
India_North | S3_SWMonsoon | D1_Night | 0.09825 | 0.09799 | 0.09746
India_North | S3_SWMonsoon | D2_Day | 0.19968 | 0.19926 | 0.20004
India_North | S3_SWMonsoon | D3_Evening | 0.10413 | 0.10386 | 0.10334
India_North | S4_PostMonsoon | D1_Night | 0.04753 | 0.03111 | 0.03431
India_North | S4_PostMonsoon | D2_Day | 0.12199 | 0.07984 | 0.08165
India_North | S4_PostMonsoon | D3_Evening | 0.05733 | 0.03752 | 0.03962
India_Northeast | S1_Winter | D1_Night | 0.02724 | 0.04279 | 0.04086
India_Northeast | S1_Winter | D2_Day | 0.07333 | 0.11239 | 0.1095
India_Northeast | S1_Winter | D3_Evening | 0.04093 | 0.06286 | 0.06025
India_Northeast | S2_PreMonsoon | D1_Night | 0.04902 | 0.04956 | 0.04992
India_Northeast | S2_PreMonsoon | D2_Day | 0.11568 | 0.1169 | 0.1163
India_Northeast | S2_PreMonsoon | D3_Evening | 0.06678 | 0.06747 | 0.06658
India_Northeast | S3_SWMonsoon | D1_Night | 0.09341 | 0.09154 | 0.09416
India_Northeast | S3_SWMonsoon | D2_Day | 0.18614 | 0.18239 | 0.18696
India_Northeast | S3_SWMonsoon | D3_Evening | 0.11391 | 0.11166 | 0.11595
India_Northeast | S4_PostMonsoon | D1_Night | 0.04754 | 0.03305 | 0.03292
India_Northeast | S4_PostMonsoon | D2_Day | 0.11912 | 0.08284 | 0.08078
India_Northeast | S4_PostMonsoon | D3_Evening | 0.06691 | 0.04653 | 0.04581
India_South | S1_Winter | D1_Night | 0.03509 | 0.05177 | 0.05288
India_South | S1_Winter | D2_Day | 0.09167 | 0.13385 | 0.13709
India_South | S1_Winter | D3_Evening | 0.03669 | 0.05511 | 0.05586
India_South | S2_PreMonsoon | D1_Night | 0.06261 | 0.0636 | 0.06484
India_South | S2_PreMonsoon | D2_Day | 0.14639 | 0.1487 | 0.15064
India_South | S2_PreMonsoon | D3_Evening | 0.0646 | 0.06562 | 0.06608
India_South | S3_SWMonsoon | D1_Night | 0.07282 | 0.07288 | 0.07159
India_South | S3_SWMonsoon | D2_Day | 0.17476 | 0.17487 | 0.16989
India_South | S3_SWMonsoon | D3_Evening | 0.07961 | 0.07968 | 0.07843
India_South | S4_PostMonsoon | D1_Night | 0.05088 | 0.03322 | 0.03319
India_South | S4_PostMonsoon | D2_Day | 0.12864 | 0.08398 | 0.08214
India_South | S4_PostMonsoon | D3_Evening | 0.05624 | 0.03673 | 0.03738
India_West | S1_Winter | D1_Night | 0.03605 | 0.05419 | 0.05402
India_West | S1_Winter | D2_Day | 0.09007 | 0.13389 | 0.13672
India_West | S1_Winter | D3_Evening | 0.03956 | 0.05937 | 0.05999
India_West | S2_PreMonsoon | D1_Night | 0.06157 | 0.06382 | 0.06323
India_West | S2_PreMonsoon | D2_Day | 0.1336 | 0.13852 | 0.13801
India_West | S2_PreMonsoon | D3_Evening | 0.06386 | 0.0662 | 0.06569
India_West | S3_SWMonsoon | D1_Night | 0.07646 | 0.07599 | 0.07555
India_West | S3_SWMonsoon | D2_Day | 0.16353 | 0.16252 | 0.16107
India_West | S3_SWMonsoon | D3_Evening | 0.08104 | 0.08055 | 0.08052
India_West | S4_PostMonsoon | D1_Night | 0.05639 | 0.03658 | 0.03732
India_West | S4_PostMonsoon | D2_Day | 0.13631 | 0.08843 | 0.08706
India_West | S4_PostMonsoon | D3_Evening | 0.06157 | 0.03994 | 0.04082
SUMMARY: POSOCO estimate was within ±6% of exact for all 60 timeslices. File (IMD) was ±50% for S1, ±35% for S4 — entirely due to December.
S2 and S3: all three sources agree within ±5%. These seasons are unaffected by the December mapping issue.
LKA — 4_Cross_Validation | Source: LKA_DA_Final.xlsx
SRI LANKA — CROSS-VALIDATION LOG
Validates PUCSL-derived profiles against CEB benchmarks and physical constraints.
A. Annual Energy vs CEB 2023 Benchmarks
Fuel Type | Script (GWh) | CEB Benchmark (GWh) | Ratio | Assessment
Coal | 4641.9 | 4800 | 0.967 | ✓ Within 5%
Oil_CEB | 1970 | 1900 | 1.037 | ✓ Within 5%
Oil_IPP | 1156.6 | 1200 | 0.964 | ✓ Within 5%
Major_Hydro | 4531.2 | 4500 | 1.007 | ✓ Within 5%
Wind | 770.6 | 800 | 0.963 | ✓ Within 5%
Solar | 813 | 900 | 0.903 | ~ Within 10%
Biomass | 126.2 | 130 | 0.971 | ✓ Within 5%
Mini_Hydro | 1262.3 | 1300 | 0.971 | ✓ Within 5%
B. Physical Constraint Checks
Check | Result | Status
Solar CF at night (D1) | Near zero (<0.001) in all seasons except via energy allocation method | ✓ Pass
Coal CF range | 0.39–0.76 across timeslices (Norochcholai 3-unit baseload) | ✓ Plausible
Wind CF max | 1.02 at S3D3 — installed capacity ~128 MW may be slightly low | ⚠ Minor
Hydro dispatch pattern | D3 (evening) peak in all 4 seasons — consistent with reservoir dispatch | ✓ Pass
Demand fractions sum | 1.000002 (rounding only) | ✓ Pass
Total demand | 15,274 GWh vs ~16,000 GWh CEB (95.5%) — 2 missing days in S2,S3,S4 | ✓ Acceptable
Gen/demand balance | 100.0% annual; per-timeslice 94–105% (T&D losses + measurement) | ✓ Pass
C. Table Layout Detection (dynamic row detection v2)
File (Month) | Total Row | Detection Result
June 2023 | 36 | 8/8 fuels, 15/15 hydro
April 2023 | 44 | 8/8 fuels, 15/15 hydro
November 2023 | 38 | 8/8 fuels, 15/15 hydro
September 2023 | 37 | 8/8 fuels, 15/15 hydro
March 2023 | 44 | 8/8 fuels, 15/15 hydro
August 2023 | 36 | 8/8 fuels, 15/15 hydro
December 2023 | 38 | 8/8 fuels, 15/15 hydro
July 2023 | 36 | 8/8 fuels, 15/15 hydro
February 2023 | 44 | 8/8 fuels, 15/15 hydro
January 2023 | 44 | 8/8 fuels, 15/15 hydro
May 2023 | 36 | 8/8 fuels, 15/15 hydro
October 2023 | 38 | 8/8 fuels, 15/15 hydro
NPL — 5_Cross_Validation | Source: NP_DA_Final.xlsx
NEPAL — CROSS-VALIDATION LOG
Compares seasonal demand shares from two independent sources. Agreement within ±5.5% confirms profile robustness.
A. SEASONAL SHARE COMPARISON
Season | NEA Yearly (FY 2079/80) | NDOR Daily (818 days) | Difference (%) | Assessment
S1 Winter (Dec-Feb) | 0.2248 | 0.2276 | +1.2% | ✓ Excellent agreement
S2 Pre-monsoon (Mar-May) | 0.2629 | 0.2525 | -3.9% | ✓ Good agreement
S3 SW Monsoon (Jun-Sep) | 0.3775 | 0.3777 | +0.0% | ✓ Near-perfect agreement
S4 Post-monsoon (Oct-Nov) | 0.1348 | 0.1422 | +5.5% | ✓ Acceptable (NDOR has more S4 days)
B. PEAK TIME VALIDATION (confirms D3 evening peak assignment)
Season | NDOR Avg Peak Time | NDOR Median Peak Time | Top 3 Peak Times | Daypart | Consistent with D3?
S1 Winter | 18:06 | 18:00 | 17:50(48x), 17:55(34x), 18:30(24x) | D3 | ✓ Yes — peak at/after 18:00
S2 Pre-monsoon | 19:00 | 19:00 | 19:00(26x), 18:50(24x), 18:45(23x) | D3 | ✓ Yes — firmly in D3
S3 SW Monsoon | 19:08 | 19:30 | 19:40(41x), 19:35(39x), 19:30(34x) | D3 | ✓ Yes — later sunset shifts peak later
S4 Post-monsoon | 18:09 | 18:10 | 18:20(29x), 17:55(21x), 17:50(21x) | D2/D3 boundary | ~ Marginal — some peaks fall in late D2
C. KEY FINDING: SEASONAL DEMAND vs SUPPLY MISMATCH
The original audit predicted winter should have HIGHEST demand intensity (1.08-1.15x average). Data shows the OPPOSITE:
Winter = 0.91x average, Monsoon = 1.13x average. Nepal does NOT have widespread electric heating.
The winter crisis is a SUPPLY-side problem (hydro at 20-30%), not demand-side. Monsoon has highest actual consumption.
Both NEA Yearly Summary AND 818 NDOR daily reports independently confirm this pattern.