## 1_OSTRAM_Profiles
BANGLADESH — RECOMMENDED OSTRAM TIMESLICE PROFILES
Final consolidated values for model parameterisation. Each cell states its source and basis.
Date produced | March 2026
Methodology | Best-source selection across 3 independent datasets (see sheet 7_Source_Selection for rationale)
Base year | 2024 (most recent complete calendar year); multi-year validation from 2023-2026
A. CAPACITY FACTORS — Recommended values for OSTRAM CapacityFactor parameter
Green = from extended daily reports (2023-2026, 1140 files). Yellow = from 2024 hourly PGCB (energy-weighted). Red = RELAC warning.
Timeslice | Season | Band | Gas (11850 MW) | Coal (5417 MW) | Oil_HFO (5831 MW) | Oil_HSD (443 MW) | Hydro (230 MW) | Solar (543 MW) | Wind (36 MW) | Import (1800 MW) | Source Key
S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.3484 | 0.4207 | 0.0271 | 0.0086 | 0.2049 | 0 | 0.2635 | 0.6113 | D=daily 23-26; S=hourly 24
S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.3592 | 0.4795 | 0.1224 | 0.0248 | 0.2088 | 0.2479 | 0.1298 | 0.7078 | D=daily 23-26; S=hourly 24
S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.374 | 0.5303 | 0.203 | 0.0258 | 0.2124 | 0 | 0.1617 | 0.7694 | D=daily 23-26; S=hourly 24
S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.4854 | 0.5663 | 0.2079 | 0.0863 | 0.1232 | 0.0022 | 0.2976 | 0.7527 | D=daily 23-26; S=hourly 24
S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.4785 | 0.537 | 0.2127 | 0.0871 | 0.1401 | 0.3244 | 0.3572 | 0.7437 | D=daily 23-26; S=hourly 24
S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.4955 | 0.5999 | 0.3873 | 0.1067 | 0.145 | 0 | 0.2882 | 0.7621 | D=daily 23-26; S=hourly 24
S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.4912 | 0.68 | 0.2685 | 0.2087 | 0.7118 | 0.0024 | 0.3325 | 0.7864 | D=daily 23-26; S=hourly 24
S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.4728 | 0.6295 | 0.222 | 0.1805 | 0.7053 | 0.299 | 0.3693 | 0.7608 | D=daily 23-26; S=hourly 24
S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.4862 | 0.69 | 0.4368 | 0.221 | 0.72 | 0 | 0.3292 | 0.7832 | D=daily 23-26; S=hourly 24
S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.4114 | 0.5487 | 0.1232 | 0.007 | 0.6734 | 0.0001 | 0.1434 | 0.8652 | D=daily 23-26; S=hourly 24
S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.4096 | 0.5455 | 0.1432 | 0.015 | 0.6638 | 0.36 | 0.1154 | 0.8558 | D=daily 23-26; S=hourly 24
S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.4238 | 0.6105 | 0.3136 | 0.0107 | 0.6753 | 0 | 0.1029 | 0.9097 | D=daily 23-26; S=hourly 24
⚠ Red: Hydro CF < 0.15. Triggered in 2 of 3 complete years (2023, 2024). Use UpperLimit not MaxCapacity.
Green cells: from extended daily report profiles (bgd_timeslice_profiles.json, 1140 files, 2023-2026). Source [D].
Yellow cells: Solar from PGCB hourly dataset (2024, 8763 records). Energy-weighted average avoids daily-snapshot bias. Source [S].
B. DEMAND FRACTIONS — Recommended values for OSTRAM SpecifiedAnnualDemand distribution
From 2024 PGCB hourly data (full balanced calendar year). Cross-validated against 2023 & 2025 daily report profiles.
Timeslice | Season | Band | YearSplit | Demand Fraction | Validation: 2023 daily | Validation: 2025 daily | Max deviation | Source
S1D1 | Winter (Dec-Feb) | Night (00-06) | 0.062151 | 0.039691 | 0.042342 | 0.043625 | 0.003934 | PGCB hourly 2024 [S]
S1D2 | Winter (Dec-Feb) | Day (06-18) | 0.12442 | 0.09911 | 0.097409 | 0.10361 | 0.004497 | PGCB hourly 2024 [S]
S1D3 | Winter (Dec-Feb) | Evening (18-24) | 0.062151 | 0.051581 | 0.05894 | 0.051628 | 0.007359 | PGCB hourly 2024 [S]
S2D1 | Pre-monsoon (Mar-May) | Night (00-06) | 0.062949 | 0.06407 | 0.058812 | 0.066989 | 0.005258 | PGCB hourly 2024 [S]
S2D2 | Pre-monsoon (Mar-May) | Day (06-18) | 0.12567 | 0.13106 | 0.12025 | 0.13294 | 0.010803 | PGCB hourly 2024 [S]
S2D3 | Pre-monsoon (Mar-May) | Evening (18-24) | 0.062835 | 0.073101 | 0.07276 | 0.068039 | 0.005062 | PGCB hourly 2024 [S]
S3D1 | SW Monsoon (Jun-Sep) | Night (00-06) | 0.083134 | 0.09481 | 0.093523 | 0.095219 | 0.001287 | PGCB hourly 2024 [S]
S3D2 | SW Monsoon (Jun-Sep) | Day (06-18) | 0.16661 | 0.18232 | 0.18183 | 0.17938 | 0.002946 | PGCB hourly 2024 [S]
S3D3 | SW Monsoon (Jun-Sep) | Evening (18-24) | 0.083248 | 0.10388 | 0.11231 | 0.09254 | 0.01134 | PGCB hourly 2024 [S]
S4D1 | Post-monsoon (Oct-Nov) | Night (00-06) | 0.041738 | 0.037289 | 0.037036 | 0.040531 | 0.003242 | PGCB hourly 2024 [S]
S4D2 | Post-monsoon (Oct-Nov) | Day (06-18) | 0.083362 | 0.079386 | 0.077419 | 0.082667 | 0.003281 | PGCB hourly 2024 [S]
S4D3 | Post-monsoon (Oct-Nov) | Evening (18-24) | 0.041738 | 0.0437 | 0.047367 | 0.042837 | 0.003667 | PGCB hourly 2024 [S]
TOTAL |  |  |  | 1.000000
C. INSTALLED CAPACITY — BPDB verified (February 2026)
From Bangladesh_Power_Sector.xlsx, "Generation Summary" sheet. Plant-level detail in "Existing Generation" sheet (138 plants).
OSTRAM Code | Technology | BPDB Installed (MW) | BPDB Derated (MW) | Daily Report Avg (MW) | CCGT/OCGT Split | Source
BGAS_CCGT | Gas combined cycle | 10694 | 10603 |  | 34 CCPP plants | BPDB plant-level [P]
BGAS_OCGT | Gas open cycle/peaking | 2344 | 2157 |  | 21 GTPP/Peaking plants | BPDB plant-level [P]
BGAS (fleet) | Gas total | 13038 | 12760 | 11850 | CCGT 82% / OCGT 18% of gen | BPDB [P] + daily reports [D]
BCOA | Coal (domestic) | 5683 | 5603 | 5417 | 7 plants excl. Adani | BPDB [P] + daily [D]
BHFO | Heavy fuel oil | 5631 | 5634 | 5831 | 54 peaking plants | BPDB [P] + daily [D]
BHSD | High speed diesel | 968 | 968 | 443 | 3 plants + 2 dual-fuel | BPDB [P] + daily [D]
BHYD | Hydro (Kaptai) | 230 | 230 | 230 | 1 plant, 5 units | BPDB [P] + daily [D]
BSOL | Solar PV | 767 | 767 | 543 | 15 plants on-grid | BPDB [P] + daily [D]
BWIN | Wind | 62 | 62 | 36 | Cox Bazar 60 + Sirajgonj 2 | BPDB [P] + daily [D]
BIMP | Import total | 2196 | 2196 | 1800 | Bheramara+Tripura+Adani+Nepal | BPDB [P]; daily avg [D]
BNUC | Nuclear (planned) | 0 | 0 | 0 | Rooppur 2×1200 MW | BPDB [P]
Daily Report Avg: time-averaged installed capacity from daily reports (lower because early 2023 had less coal/solar/import).
For OSTRAM base year: use BPDB Feb 2026 figures (Installed or Derated depending on model convention).

## 2_Demand_Forecasts
BANGLADESH — DEMAND: HISTORICAL & FORECAST
A. HISTORICAL PEAK DEMAND & INSTALLED CAPACITY (Source: BPDB Annual Reports, IEEFA, ScienceDirect)
Fiscal Year | Installed Capacity (MW) | Max Generation Obtained (MW) | Peak Demand (MW) | Net Generation (GWh) | Per Capita Consumption (kWh) | T&D Losses (%) | Source
FY 2014-15 | 11534 |  | 7817 | 52000 |  |  | BPDB Annual Report
FY 2015-16 | 12365 |  | 9036 | 57276 |  |  | BPDB Annual Report
FY 2016-17 | 15351 |  | 9479 | 62678 |  |  | BPDB Annual Report; Wikipedia
FY 2017-18 | 20000 |  | 10958 | 70533 |  |  | BPDB Annual Report; Wikipedia
FY 2018-19 | 20383 |  | 12893 | 76332 |  |  | BPDB Annual Report
FY 2019-20 | 20514 |  | 13555 | 71419 |  |  | BPDB Annual Report (COVID impact)
FY 2020-21 | 22031 |  | 14782 | 80423 |  |  | BPDB Annual Report
FY 2021-22 | 22482 | 14782 | 14782 | 85607 | 464 | 10.33 | BPDB Annual Report 2021-22; HCU Energy Scenario 2021-22
FY 2022-23 | 23482 |  | 16220 | 79270 | 464 | 10.33 | BPDB Annual Report 2022-23; IEEFA (summer peak 16.22 GW)
FY 2023-24 | 28098 |  | 17830 | 86255 |  |  | ScienceDirect (Pii/S2211467X25001920); BPDB (retail consumption 86,255 GWh)
Notes: Peak demand figures represent maximum demand recorded in each FY. COVID-19 caused a dip in FY 2019-20. Summer peak ~16.22 GW vs winter ~10.92 GW (Dec 2023).
B. DEMAND FORECASTS — IEPMP 2023 (Integrated Energy and Power Master Plan, approved Nov 2023)
Year | Peak Demand (GW) — Low | Peak Demand (GW) — High | Demand Growth Rate (%/yr) | Required Installed Capacity (GW) | Reserve Margin (%) | Notes | Source
2023 | 17.8 | 17.8 |  | 28.1 | ~57% | Base year (actual) | BPDB/IEPMP
2025 |  |  | 7.0% |  |  | IEPMP growth assumption | IEPMP 2023
2030 | 27.1 | 29.3 | 7.0% | 35.4 | 31% | IEPMP central projections; range across scenarios | IEPMP 2023; Chambers RE 2025
2035 |  |  | 5.8% |  |  | Interpolated growth period | IEPMP 2023
2040 | 50.4 | 58.6 | 5.8% |  |  | Range across PP2041 and In-Between scenarios | Chambers RE 2025
2041 | 38 |  | 5.8% | 71 |  | MGSSI/JICA estimate; ~40% clean energy target | MGSSI (Jan 2024); IEPMP 2023
2045 |  |  | 3.8% |  |  | Interpolated growth period | IEPMP 2023
2050 | 70.5 | 96.8 | 3.8% | 84.6 | 20% | Max peak demand scenario; system + 26.2 GW RE = 110.8 GW | IEPMP 2023; Chambers RE 2025
Source: IEPMP 2023 (JICA/IEEJ), approved Nov 2023 by GoB. Growth rates: 7%/yr to 2030, 5.8%/yr to 2041, 3.8%/yr to 2050. GDP scenarios: PP2041 (optimistic), IMF Extension (moderate), In-Between.
C. ALTERNATIVE DEMAND PROJECTIONS (IEEFA, Daily Star Analysis)
Source | Year | Peak Demand (GW) | Energy Demand Growth Factor | Notes | Source Reference
IEEFA (2025) | 2030 | 25.8 | 1.37x (vs IEPMP 1.68x) | Factors in energy efficiency gains & demand shift | IEEFA "Fixing Bangladesh's Power Sector", 2025
Daily Star / Academic | 2030 |  | 1.37x | Academic critique of IEPMP OLS methodology | Daily Star, "The Numbers Don't Add Up", 2024
Daily Star / Academic | 2041 |  | 1.88x (vs IEPMP 2.6x) | More tempered growth than IEPMP projects | Daily Star, "The Numbers Don't Add Up", 2024
Daily Star / Academic | 2050 |  | 2.36x (vs IEPMP 3.75x) | Critiques constant 1.27 GDP-electricity elasticity | Daily Star, "The Numbers Don't Add Up", 2024
PSMP 2016 (superseded) | 2030 | 33.7 |  | Old plan; assumed 40 GW installed capacity by 2030 | PSMP 2016 (JICA)
PSMP 2016 (superseded) | 2041 |  |  | Old plan; assumed 60 GW installed capacity by 2041 | PSMP 2016 (JICA)
Note: IEEFA and academic analyses argue IEPMP overestimates demand due to reliance on optimistic GDP growth (>7%) and constant GDP-electricity elasticity of 1.27. IEPMP uses basic OLS regression without accounting for energy efficiency, population, or price effects.
D. KEY SYSTEM INDICATORS & CONTEXT
Parameter | Value | Year/Period | Source
Installed capacity (incl. captive) | ~29,000 MW | Nov 2025 | BPDB website
Electrification rate | 100% | 2022 | BPDB / GoB
Reserve margin | ~61-66% | Dec 2024 | IEEFA (2025)
T&D losses | ~10.3% | FY 2023-24 | IEEFA / BPDB
Electricity import from India | 1,160 MW | Since Dec 2018 | BPDB (500+100+560 MW)
RE share of installed capacity | ~2.8% | Jun 2023 | BPDB Annual Report 2022-23
NDC RE target | 4.1 GW by 2030 | 2021 NDC | GoB Updated NDC
IEPMP clean energy target | 25% by 2030; 40% by 2041 | 2023 | IEPMP 2023 (note: includes nuclear & gas)
COP-26 RE target | 40% RE by 2041 | 2021 | GoB announcement at COP-26
Summer peak demand | ~16.2 GW | Summer 2023 | BPDB daily generation archive
Winter peak demand | ~10.9 GW | Dec 2023 | BPDB daily generation archive
Retail electricity consumption | 86,255 GWh | FY 2023-24 | ScienceDirect (S2211467X25001920)
Rooppur Nuclear Plant | 2.4 GWe (2 x 1.2 GW) | Under construction | GoB / Rosatom
E. SOURCE CITATIONS
1. IEPMP 2023 — Government of Bangladesh, 'Integrated Energy and Power Master Plan 2023', JICA/IEEJ, approved Nov 2023. URL: powerdivision.portal.gov.bd
2. BPDB Annual Reports (2021-22, 2022-23, 2023-24) — Bangladesh Power Development Board. URL: bpdb.portal.gov.bd
3. IEEFA — Shafiqul Alam, 'Streamlining Bangladesh's Power Sector' (Feb 2024) & 'Fixing Bangladesh's Power Sector' (2025). URL: ieefa.org
4. MGSSI — Mitsui & Co. Global Strategic Studies Institute, Monthly Report Jan 2024. URL: mitsui.com/mgssi
5. Chambers & Partners — 'Renewable Energy 2025: Bangladesh'. URL: practiceguides.chambers.com
6. Daily Star — '2023 Integrated Energy & Power Master Plan: The Numbers Don't Add Up'. URL: thedailystar.net
7. ScienceDirect — 'Power sector transformation in Bangladesh' (S2211467X25001920, Aug 2025).
8. HCU — Hydrocarbon Unit, 'Energy Scenario of Bangladesh 2021-22'. URL: hcu.org.bd
9. PSMP 2016 — GoB/JICA, 'Power System Master Plan 2016'. URL: powerdivision.portal.gov.bd

## 3_Year_by_Year
BANGLADESH — CAPACITY FACTORS BY YEAR (2023, 2024, 2025, 2026 partial)
Source | bgd_timeslice_profiles_by_year.csv — from BPDB daily generation report scraping pipeline
Pipeline | Python scraper → BPDB daily PDFs → tabular extraction → timeslice aggregation
Files | 1,140 daily reports covering 2022-12-31 to 2026-03-09
Repository | github.com/codebyrama/Bangladesh-Power-Data-Pipeline (original scraper reference)
2023 (n_days per timeslice shown)
timeslice | n_days | Gas_CF | Coal_CF | Oil_HFO_CF | Oil_HSD_CF | Hydro_CF | Solar_CF | Wind_CF | Import_CF | demand_fraction
S1D1 | 90 | 0.3884 | 0.4734 | 0.0627 | 0.0144 | 0.2144 | 0 | 0 | 0.4291 | 0.042342
S1D2 | 90 | 0.3947 | 0.5024 | 0.173 | 0.0405 | 0.2138 | 0.4846 | 0 | 0.4838 | 0.097409
S1D3 | 90 | 0.408 | 0.557 | 0.2932 | 0.0423 | 0.2228 | 0 | 0 | 0.5078 | 0.05894
S2D1 | 88 | 0.517 | 0.5412 | 0.2469 | 0.1157 | 0.0376 | 0.0011 | 0 | 0.5456 | 0.058812
S2D2 | 88 | 0.5051 | 0.5239 | 0.2807 | 0.1188 | 0.0794 | 0.6574 | 0 | 0.546 | 0.12025
S2D3 | 88 | 0.523 | 0.5594 | 0.466 | 0.1447 | 0.0862 | 0.0033 | 0 | 0.5351 | 0.07276
S3D1 | 121 | 0.5656 | 0.7427 | 0.2532 | 0.2714 | 0.4994 | 0.0012 | 0 | 0.5708 | 0.093523
S3D2 | 121 | 0.538 | 0.7176 | 0.2422 | 0.2249 | 0.4942 | 0.5416 | 0 | 0.5766 | 0.18183
S3D3 | 121 | 0.5552 | 0.7584 | 0.4826 | 0.2813 | 0.516 | 0.006 | 0 | 0.5503 | 0.11231
S4D1 | 60 | 0.4428 | 0.829 | 0.0852 | 0.0095 | 0.6518 | 0 | 0 | 0.5135 | 0.037036
S4D2 | 60 | 0.4436 | 0.8206 | 0.1271 | 0.0192 | 0.6422 | 0.5946 | 0 | 0.5216 | 0.077419
S4D3 | 60 | 0.461 | 0.9435 | 0.2731 | 0.0088 | 0.6548 | 0 | 0 | 0.5039 | 0.047367
2024 (n_days per timeslice shown)
timeslice | n_days | Gas_CF | Coal_CF | Oil_HFO_CF | Oil_HSD_CF | Hydro_CF | Solar_CF | Wind_CF | Import_CF | demand_fraction
S1D1 | 90 | 0.3496 | 0.3651 | 0.013 | 0 | 0.2232 | 0 | 0.3017 | 0.4493 | 0.041061
S1D2 | 90 | 0.3664 | 0.4159 | 0.1146 | 0.0008 | 0.2313 | 0.3678 | 0.1407 | 0.5471 | 0.098214
S1D3 | 90 | 0.3828 | 0.4503 | 0.1684 | 0.0006 | 0.2328 | 0 | 0.2162 | 0.5924 | 0.057193
S2D1 | 86 | 0.5199 | 0.5466 | 0.1879 | 0.0187 | 0.1279 | 0.0008 | 0.2233 | 0.5128 | 0.061998
S2D2 | 86 | 0.5095 | 0.5146 | 0.1814 | 0.0128 | 0.1377 | 0.4884 | 0.3036 | 0.5372 | 0.12328
S2D3 | 86 | 0.5323 | 0.5756 | 0.3576 | 0.0172 | 0.1451 | 0.0022 | 0.1997 | 0.4877 | 0.07459
S3D1 | 118 | 0.4602 | 0.6517 | 0.2966 | 0.0002 | 0.7696 | 0.0011 | 0.3799 | 0.6472 | 0.092496
S3D2 | 118 | 0.4443 | 0.5959 | 0.2368 | 0.0002 | 0.7631 | 0.4369 | 0.4089 | 0.6533 | 0.17531
S3D3 | 118 | 0.4543 | 0.6541 | 0.4448 | 0.0006 | 0.7744 | 0.0041 | 0.3787 | 0.6418 | 0.10661
S4D1 | 62 | 0.4295 | 0.3721 | 0.1574 | 0.0005 | 0.6765 | 0 | 0.1361 | 0.9716 | 0.039232
S4D2 | 62 | 0.4243 | 0.3746 | 0.173 | 0.0044 | 0.6678 | 0.5372 | 0.1088 | 0.9727 | 0.080837
S4D3 | 62 | 0.4404 | 0.4091 | 0.3522 | 0.01 | 0.6845 | 0 | 0.0983 | 1.0211 | 0.049167
2025 (n_days per timeslice shown)
timeslice | n_days | Gas_CF | Coal_CF | Oil_HFO_CF | Oil_HSD_CF | Hydro_CF | Solar_CF | Wind_CF | Import_CF | demand_fraction
S1D1 | 90 | 0.326 | 0.401 | 0.0143 | 0 | 0.1708 | 0.0001 | 0.1685 | 0.7887 | 0.043625
S1D2 | 90 | 0.3341 | 0.4775 | 0.0966 | 0.0059 | 0.1753 | 0.3611 | 0.0901 | 0.9117 | 0.10361
S1D3 | 90 | 0.349 | 0.5401 | 0.1606 | 0.0016 | 0.1735 | 0 | 0.104 | 1.0061 | 0.051628
S2D1 | 90 | 0.4422 | 0.5959 | 0.2021 | 0 | 0.1802 | 0.0007 | 0.1228 | 1.1337 | 0.066989
S2D2 | 90 | 0.4414 | 0.5589 | 0.1841 | 0.0003 | 0.1811 | 0.4375 | 0.1696 | 1.0892 | 0.13294
S2D3 | 90 | 0.4536 | 0.6388 | 0.3508 | 0.0052 | 0.1822 | 0.0024 | 0.1134 | 1.1863 | 0.068039
S3D1 | 116 | 0.4593 | 0.6883 | 0.2534 | 0.1126 | 0.875 | 0.0016 | 0.2329 | 1.1529 | 0.095219
S3D2 | 116 | 0.4467 | 0.6268 | 0.182 | 0.2484 | 0.8671 | 0.4054 | 0.2672 | 1.0623 | 0.17938
S3D3 | 116 | 0.46 | 0.7034 | 0.3743 | 0.2112 | 0.8781 | 0.0044 | 0.226 | 1.17 | 0.09254
S4D1 | 61 | 0.3722 | 0.5821 | 0.1258 | 0 | 0.6917 | 0.0002 | 0.1048 | 1.1031 | 0.040531
S4D2 | 61 | 0.3714 | 0.5758 | 0.1273 | 0.0009 | 0.6811 | 0.4524 | 0.0806 | 1.0657 | 0.082667
S4D3 | 61 | 0.3811 | 0.641 | 0.3129 | 0.0384 | 0.6862 | 0 | 0.0676 | 1.1957 | 0.042837
2026 (n_days per timeslice shown)
timeslice | n_days | Gas_CF | Coal_CF | Oil_HFO_CF | Oil_HSD_CF | Hydro_CF | Solar_CF | Wind_CF | Import_CF | demand_fraction
S1D1 | 58 | 0.3065 | 0.4704 | 0.0111 | 0 | 0.2146 | 0 | 0.2442 | 0.8741 | 0.1854
S1D2 | 58 | 0.3186 | 0.5388 | 0.0932 | 0.0008 | 0.2185 | 0.4 | 0.1202 | 0.9933 | 0.43848
S1D3 | 58 | 0.3322 | 0.5922 | 0.1783 | 0.0001 | 0.2251 | 0 | 0.1144 | 1.0862 | 0.21776
S2D1 | 9 | 0.3589 | 0.6495 | 0.0592 | 0 | 0.3454 | 0 | 0.0043 | 1.2596 | 0.038045
S2D2 | 9 | 0.364 | 0.655 | 0.1032 | 0 | 0.3478 | 0.4298 | 0.0629 | 1.1934 | 0.079909
S2D3 | 9 | 0.3721 | 0.7303 | 0.2257 | 0 | 0.3478 | 0.0001 | 0.0128 | 1.3602 | 0.040411
COMBINED (n_days per timeslice shown)
timeslice | n_days | Gas_CF | Coal_CF | Oil_HFO_CF | Oil_HSD_CF | Hydro_CF | Solar_CF | Wind_CF | Import_CF | demand_fraction
S1D1 | 329 | 0.3484 | 0.4207 | 0.0271 | 0.0086 | 0.2049 | 0 | 0.2635 | 0.6113 | 0.049871
S1D2 | 329 | 0.3592 | 0.4795 | 0.1224 | 0.0248 | 0.2088 | 0.4117 | 0.1298 | 0.7078 | 0.11761
S1D3 | 329 | 0.374 | 0.5303 | 0.203 | 0.0258 | 0.2124 | 0 | 0.1617 | 0.7694 | 0.064392
S2D1 | 273 | 0.4854 | 0.5663 | 0.2079 | 0.0863 | 0.1232 | 0.0008 | 0.2976 | 0.7527 | 0.061379
S2D2 | 273 | 0.4785 | 0.537 | 0.2127 | 0.0871 | 0.1401 | 0.493 | 0.3572 | 0.7437 | 0.12319
S2D3 | 273 | 0.4955 | 0.5999 | 0.3873 | 0.1067 | 0.145 | 0.0024 | 0.2882 | 0.7621 | 0.070082
S3D1 | 355 | 0.4912 | 0.68 | 0.2685 | 0.2087 | 0.7118 | 0.0013 | 0.3325 | 0.7864 | 0.088841
S3D2 | 355 | 0.4728 | 0.6295 | 0.222 | 0.1805 | 0.7053 | 0.432 | 0.3693 | 0.7608 | 0.16941
S3D3 | 355 | 0.4862 | 0.69 | 0.4368 | 0.221 | 0.72 | 0.0045 | 0.3292 | 0.7832 | 0.098157
S4D1 | 183 | 0.4114 | 0.5487 | 0.1232 | 0.007 | 0.6734 | 0.0001 | 0.1434 | 0.8652 | 0.036931
S4D2 | 183 | 0.4096 | 0.5455 | 0.1432 | 0.015 | 0.6638 | 0.4987 | 0.1154 | 0.8558 | 0.076155
S4D3 | 183 | 0.4238 | 0.6105 | 0.3136 | 0.0107 | 0.6753 | 0 | 0.1029 | 0.9097 | 0.043978
Source: BPDB daily generation reports scraped via Python pipeline. Capacity denominators are time-averaged from daily report headers.
⚠ Red: Hydro CF < 0.15 (RELAC infeasibility risk). Triggered: 2023 (severe), 2024 (marginal), 2025 (clear).

## 4_Hydro_RELAC
BANGLADESH — HYDRO (KAPTAI) SEASONAL ANALYSIS & RELAC FLAG
Purpose | Document the hydro infeasibility risk for OSTRAM parameterisation
RELAC lesson | MaxCapacity + low seasonal CF → per-timeslice bottleneck → model infeasibility
Recommendation | Use TotalTechnologyAnnualActivityUpperLimit (annual PJ cap) instead of MaxCapacity (GW cap)
A. S2 (Pre-monsoon) Hydro CF by Year — The critical timeslices
Year | S2D1 (Night) | S2D2 (Day) | S2D3 (Evening) | Min CF | Status | Avg MW | Source
2023 | 0.0376 | 0.0794 | 0.0862 | 0.0376 | ⚠ BELOW 0.15 | 15.6 | Daily reports [D]
2024 | 0.1279 | 0.1377 | 0.1451 | 0.1279 | ⚠ BELOW 0.15 | 31.5 | Daily reports [D]
2025 | 0.1802 | 0.1811 | 0.1822 | 0.1802 | ✅ Above 0.15 | 41.5 | Daily reports [D]
2026 | 0.3454 | 0.3478 | 0.3478 | 0.3454 | ✅ Above 0.15 | 79.8 | Daily reports [D]
combined | 0.1232 | 0.1401 | 0.145 | 0.1232 | ⚠ BELOW 0.15 | 31.3 | Daily reports [D]
B. Full Seasonal Hydro Profile (combined 2023-2026)
Timeslice | Season | Hydro CF | Avg MW | Status | Source
S1D1 | Winter (Dec-Feb) | 0.2049 | 47.1 |  | Daily combined [D]
S1D2 | Winter (Dec-Feb) | 0.2088 | 48 |  | Daily combined [D]
S1D3 | Winter (Dec-Feb) | 0.2124 | 48.8 |  | Daily combined [D]
S2D1 | Pre-monsoon (Mar-May) | 0.1232 | 28.3 | ⚠ <0.15 | Daily combined [D]
S2D2 | Pre-monsoon (Mar-May) | 0.1401 | 32.2 | ⚠ <0.15 | Daily combined [D]
S2D3 | Pre-monsoon (Mar-May) | 0.145 | 33.3 | ⚠ <0.15 | Daily combined [D]
S3D1 | SW Monsoon (Jun-Sep) | 0.7118 | 163.6 |  | Daily combined [D]
S3D2 | SW Monsoon (Jun-Sep) | 0.7053 | 162.1 |  | Daily combined [D]
S3D3 | SW Monsoon (Jun-Sep) | 0.72 | 165.5 |  | Daily combined [D]
S4D1 | Post-monsoon (Oct-Nov) | 0.6734 | 154.7 |  | Daily combined [D]
S4D2 | Post-monsoon (Oct-Nov) | 0.6638 | 152.5 |  | Daily combined [D]
S4D3 | Post-monsoon (Oct-Nov) | 0.6753 | 155.2 |  | Daily combined [D]
Conclusion: S2 hydro CF drops below 0.15 in 2 of 3 complete years. This is a structural dry-season pattern, not an anomaly.
For OSTRAM: constrain hydro via TotalTechnologyAnnualActivityUpperLimit (in PJ), NOT MaxCapacity (in GW).
This allows the optimizer to shift hydro generation to wet-season timeslices without hitting per-timeslice bottlenecks.

## 5_Installed_Capacity
BANGLADESH — INSTALLED GENERATION CAPACITY (MW)
Source file | Bangladesh_Power_Sector.xlsx (uploaded)
Original source | BPDB Daily Generation Report (18-Feb-2026) & BPDB Power Generation Units (Feb 2026)
Sheets used | "Generation Summary" → fuel totals; "Existing Generation" → 138 plants with technology column
A. By Fuel Type — BPDB February 2026
Fuel Type | Installed (MW) | Derated (MW) | Share (%) | Source Row in Generation Summary
Gas | 12512 | 12204 | 44.1 | Row 4
HFO | 5641 | 5634 | 19.9 | Row 5
Coal | 7179 | 7039 | 25.3 | Row 6
Solar PV | 767 | 767 | 2.7 | Row 7
HSD | 768 | 768 | 2.7 | Row 8
Imported Power | 1160 | 1160 | 4.1 | Row 9
Hydro | 230 | 230 | 0.8 | Row 10
Wind | 62 | 62 | 0.2 | Row 11
Other | 40 | 40 | 0.1 | Row 12
TOTAL | 28359 | 27904 | 100 | Row 13
B. OSTRAM Technology Mapping — CCGT vs OCGT & HFO vs HSD
From Bangladesh_Power_Sector.xlsx → "Existing Generation" sheet, grouped by Technology column.
OSTRAM Code | Description | Plants | Installed (MW) | Derated (MW) | Mapping Rule
BGAS_CCGT | Gas combined cycle | 34 CCPP | 10694 | 10603 | Technology = CCPP or CCPP/GT
BGAS_OCGT | Gas open cycle/peaking | 21 plants | 2344 | 2157 | Technology = GTPP, Peaking, Thermal, Small PP
BHFO | Heavy fuel oil | 54 HFO plants | 5631 | 5634 | Fuel Type = HFO
BHSD | High speed diesel | 3 HSD + 2 dual | 968 | 968 | Fuel Type = HSD or Gas/HSD
BCOA | Coal | 7 plants | 5683 | 5603 | Fuel Type = Coal
BHYD | Hydro | 1 plant | 230 | 230 | Fuel Type = Hydro
BSOL | Solar PV | 15 plants | 767 | 767 | Fuel Type = Solar
BWIN | Wind | 2 plants | 62 | 62 | Fuel Type = Wind
BIMP_HVDC | Bheramara HVDC | 1 B2B station | 1000 | 1000 | Existing Interconnections sheet; 2×500 MW
BIMP_TRIP | Tripura AC | 1 line | 160 | 160 | Existing Interconnections sheet
BIMP_ADNI | Adani Godda | 1 HVDC | 1496 | 1496 | Existing Interconnections sheet; PPA 1496 MW
BIMP_NEPL | Nepal trial | trial | 40 | 40 | Existing Interconnections sheet
C. Data Gaps — Remaining
Gap | Status | Notes | Needed From
Variable costs by technology | ⏳ IN PROGRESS | Luis cross-country cost query | IRENA, IEA WEO, BPDB tariff
Capital costs for new build | ⏳ IN PROGRESS | Luis cross-country cost query | IRENA, IEA WEO, IEPMP
LNG infrastructure & costs | ⏳ OPEN | Constrains gas dispatch | Petrobangla, RPGCL
Domestic gas production projections | ⏳ OPEN | Key supply constraint for gas fleet | Petrobangla
Emission factors by fuel | ⏳ OPEN | IPCC defaults available as fallback | IPCC 2006 GL; UNFCCC NIR
RE resource potential (solar/wind) | ⏳ OPEN | For future scenario expansion | IRENA Global Atlas, ESMAP

## 6_Cross_Validation
BANGLADESH — CROSS-VALIDATION LOG
Three independent datasets compared. Discrepancies documented with explanations.
A. Datasets Used
Code | Dataset | Period | Records | Resolution | Key Strength
[S] | PGCB Hourly (UCI DOI:10.24432/C59P6V) | Apr 2015–Jun 2025 | 92,650 | Hourly by fuel type | Energy-weighted CFs; sub-daily resolution; solar accuracy
[D] | BPDB Daily Report Scrape | Jan 2023–Mar 2026 | 1,140 files | Daily by fuel type | Multi-year coverage; HFO/HSD split; fleet evolution
[P] | BPDB Plant Register (Feb 2026) | Feb 2026 snapshot | 138 plants | Plant-level | CCGT/OCGT split; exact nameplate capacity; technology type
B. Key Discrepancies and Resolutions
Item | [S] 2024 hourly | [D] 2023-26 daily | Resolution | Explanation
Solar daytime CF | 0.25–0.36 | 0.41–0.50 | Use [S] hourly | Daily reports capture peak snapshots, not energy-weighted averages. Hourly data integrates full D2 band.
Gas CF level | 0.31–0.47 | 0.35–0.49 | Use [D] multi-year | Slight offset from different capacity denominators. Multi-year average is more robust.
Coal S4 CF | 0.42–0.47 | 0.55–0.61 | Use [D] multi-year | 2023 had anomalously high coal S4 (0.83-0.94); multi-year average smooths this.
Hydro S2 CF | 0.12–0.15 | 0.12–0.15 (combined) | Confirmed | Both sources agree: S2 is below RELAC threshold. Year-by-year: 2023 severe (0.04), 2024 marginal, 2025 clear.
Hydro S3 CF | 0.76–0.78 | 0.71–0.72 | Use [D] multi-year | 2025 was wetter than 2024. Multi-year average preferred.
Import CF | 0.29–0.68 | 0.61–0.91 | Use [D] with 1800 MW cap | Adani disruption in 2024 suppresses [S]. [D] corrected to 1800 MW weighted-average denominator.
Wind S2 CF | 0.14–0.22 | 0.29–0.36 | Use [D] multi-year | 62 MW fleet is tiny; year-to-year variation is high. Multi-year is more representative.
Demand fractions | S3=38%, S1=19% | S3=36%, S1=23% | Use [S] 2024 hourly | [D] combined overweights winter (3.3 winters vs 3.0 monsoons). Individual years each show ~19-20% winter.
Oil_HSD capacity | 968 MW [P] | 443 MW [D] | Document both | [P] = nameplate incl. standby; [D] = actively dispatched only. Both valid for different purposes.

## 7_Source_Selection
BANGLADESH — SOURCE SELECTION RATIONALE
Documents WHY each recommended value uses a particular source. Prevents "which number do I trust?" ambiguity.
Parameter | Recommended Source | Source Code | Reason | Alternative Considered | Why Not Used
Gas CF (12 timeslices) | Extended daily 2023-2026 | [D] | Multi-year average smooths inter-annual variation; 1140 files | 2024 hourly [S] | Single year; Adani disruption distorts import-vs-gas dispatch
Coal CF (12 timeslices) | Extended daily 2023-2026 | [D] | Captures fleet expansion (Matarbari, SS Power); 3 monsoon cycles | 2024 hourly [S] | Coal S4 anomalously low in 2024 vs multi-year pattern
Oil_HFO CF (12 timeslices) | Extended daily 2023-2026 | [D] | Multi-year average; strong correlation (r=0.97) across sources | 2024 hourly [S] | Consistent with [S]; [D] preferred for multi-year robustness
Oil_HSD CF (12 timeslices) | Extended daily 2023-2026 | [D] | Only source that splits HFO/HSD (PGCB hourly lumps them) | 2024 hourly [S] | [S] cannot separate HFO from HSD
Hydro CF (12 timeslices) | Extended daily 2023-2026 | [D] | Multi-year captures wet/dry monsoon variation; confirms RELAC flag | 2024 hourly [S] | Single year; 2024 was moderate; 2023 was drier
Solar CF (12 timeslices) | 2024 PGCB hourly | [S] | Energy-weighted hourly average; avoids daily-snapshot bias | Extended daily [D] | Daily reports show 0.41-0.50 daytime CF vs 0.25-0.36 hourly — snapshot artifact
Wind CF (12 timeslices) | Extended daily 2023-2026 | [D] | 62 MW fleet has high year-to-year variability; multi-year smooths | 2024 hourly [S] | Single year less representative for tiny fleet
Import CF (12 timeslices) | Extended daily 2023-2026 | [D] | Corrected to 1800 MW weighted denominator; includes Adani normalization | 2024 hourly [S] | 2024 had Adani payment disruption; distorts import profile
Demand fractions (12 ts) | 2024 PGCB hourly | [S] | Full balanced calendar year; hourly resolution captures true energy split | Extended daily [D] | [D] combined overweights winter due to incomplete year bookends
Installed capacity | BPDB plant register Feb 2026 | [P] | Official government source; plant-level granularity; most current | Daily report averages [D] | [D] averages across years with different fleet sizes
CCGT vs OCGT split | BPDB plant register Feb 2026 | [P] | Only source with Technology column (CCPP vs GTPP) | None available | PGCB hourly has single "gas" column; daily reports also aggregate
HFO vs HSD split (capacity) | BPDB plant register Feb 2026 | [P] | 138 plants with Fuel Type column | Daily reports [D] | [D] shows lower HSD (actively dispatched only vs nameplate)

## 8_Sources
BANGLADESH — COMPLETE SOURCE INDEX
Every data point in this workbook traces to one of the sources below.
Code | Source | Publisher | Identifier | License | Sheets Used | What It Provides
[S] | PGCB Hourly Generation Dataset | UCI ML Repository | DOI: 10.24432/C59P6V | CC BY 4.0 | 1,6 | 92,650 hourly records (2015-2025). Generation by fuel, demand, imports. File: PGCB_date_power_demand.xlsx
[S-paper] | Islam, Turja & Habib (2025) | Springer | DOI: 10.1007/s42488-025-00140-9 | Open Access | — | Describes PGCB dataset methodology, validates quality. J. Data Information Management 7:1-19.
[D] | BPDB Daily Report Scrape (extended) | BPDB via Python pipeline | 1,140 daily PDFs, 2023-01 to 2026-03 | Public (BPDB) | 1,3,4,6 | Daily generation by fuel type. Processed to bgd_timeslice_profiles.json/csv. Pipeline ref: github.com/codebyrama/Bangladesh-Power-Data-Pipeline
[D-prev] | BPDB Daily Report Scrape (initial) | BPDB via Python pipeline | 423 daily PDFs, 2025-01 to 2026-03 | Public (BPDB) | 6 (validation) | First batch. Superseded by extended [D] but used for cross-validation.
[P] | Bangladesh_Power_Sector.xlsx | BPDB (compiled Feb 2026) | Daily Gen Report 18-Feb-2026; Power Gen Units Feb 2026 | Public (BPDB) | 1,5,6 | 138 plants with technology/fuel/owner/zone. Interconnections. Transmission. Planned generation.
[P-bpdb] | BPDB Installed Capacity webpage | bpdb.gov.bd | As of 30 Nov 2025 | Public | 5 (cross-check) | Capacity by ownership entity. Cross-check against [P].
[F] | Bangladesh_new_data.xlsx (demand forecasts) | Compiled from multiple sources | See Section E in sheet | Mixed | 2 | IEPMP 2023, IEEFA, BPDB Annual Reports. Per-row citations in sheet.
[F-iepmp] | IEPMP 2023 | JICA/IEEJ; GoB | Approved Nov 2023 | GoB | 2 | Official demand forecasts to 2050. Growth: 7%/yr→5.8%→3.8%.
[F-ieefa] | IEEFA 2025 | ieefa.org | Fixing Bangladeshs Power Sector | Public | 2 | Alternative demand projections; overcapacity critique.
[C] | BGD_Context_Review.docx | CLG / OSTRAM project | March 2026 | Internal | 6 (validation) | Structured review of 3 papers + 2 datasets. Cross-validated against all sheets.
[G-gem] | GEM Wiki: Adani Godda | gem.wiki | Updated Jan 2026 | Public | 1,4 | Adani payment dispute timeline; supply resumption Mar 2025.
[G-hdfc] | HDFC SKY report | hdfcsky.com | Nov 2025 | Public | 1 | Bangladesh $437M payment to clear Adani arrears.
[G-irena] | IRENA Energy Profile Bangladesh | irena.org | Updated 22 Sep 2025 | Public | 5 (cross-check) | RE capacity, utilisation rates.
[G-bnef] | BNEF 2023 | Bloomberg NEF | Bangladesh Power Sector Crossroads, Oct 2023 | Restricted | 5 (superseded by [P]) | Generation mix snapshot end-2022. Superseded by [P] Feb 2026.