## Existing Generation
NEPAL — Existing Power Generation
Source: NEA Generation Directorate 2076 (Aug 2019); NEA Annual Report FY 2024/2025; NEA Annual Report FY 2075/76
Plant Name | Zone/Location | Fuel Type | Owner Type | Owner | Installed Capacity (MW) | Derated Capacity (MW) | Technology | Status | Notes
Kaligandaki 'A' (KGA) | Beltari, Syangja / Gandaki | Hydro | Public | NEA | 144 |  | Run-of-River (6-hr peaking) | Operational | 3 units × 48 MW; Commissioned 2002; Annual design: 982 GWh; Rehabilitation under ADB financing
Middle Marsyangdi (MMHPS) | Gandaki Province | Hydro | Public | NEA | 70 |  | Run-of-River | Operational | Annual design generation: 398 GWh; Commissioned 2008
Marsyangdi (MHPS) | Lamjung | Hydro | Public | NEA | 69 |  | Run-of-River (peaking) | Operational | 3 units × 23 MW; Commissioned 1989; Cumulative gen: 12,407,451.9 MWh
Kulekhani I | Dhorsing, Makwanpur | Hydro | Public | NEA | 60 |  | Storage/Reservoir | Operational | 2 units × 30 MW; Only reservoir-type project in Nepal; Cumulative gen reached 92 MW full capacity
Upper Trishuli 3A HEP | Rasuwa & Nuwakot, Bagmati | Hydro | Public | NEA | 60 | 43.75 | Run-of-River | Operational | 2 × 30 MW; Commercial operation Aug 2019; Funded by China Exim Bank (125.775 M USD); China Gezhouba Group contractor; 44.7 km 220 kV DC TL to Matatirtha
Kulekhani II | Bhimphedi, Makwanpur | Hydro | Public | NEA | 32 | 16.5 | Storage (cascade of KL-I) | Operational | Cascade of Kulekhani I; Annual design: 104.6 GWh; Commissioned ~1986
Chameliya | Darchula | Hydro | Public | NEA | 30 |  | Daily pondage Run-of-River | Operational | 2 × 15 MW; Francis turbines; Commissioned 2018; Joint funding
Trishuli | Trishuli Bazar, Nuwakot | Hydro | Public | NEA | 24 |  | Run-of-River (peaking) | Operational | Originally 21 MW (7×3 MW, commissioned 1967 with GoI assistance); Rehabilitated 1995 to 24 MW (6×3.5 MW + 1×3 MW); Annual design: 163 GWh
Gandak | Pratappur Gaunpalika-7, Nawalparasi | Hydro | Public | NEA | 15 |  | Run-of-River | Operational | 15 MW; Shared project with India
Devighat | Battar, Nuwakot | Hydro | Public | NEA | 14.1 |  | Run-of-River (cascade of Trishuli) | Operational | Cascade of Trishuli HPS; Commissioned 1984 with GoI & GoN assistance; Annual design: 114 GWh
Modikhola | Kaski | Hydro | Public | NEA | 14.8 |  | Run-of-River | Operational | 2 units × 7.4 MW; Annual design: 92.5 GWh; Commissioned 2000
Kulekhani III HEP | Sanutar/Bhaise, Makwanpur | Hydro | Public | NEA | 14 |  | Run-of-River (cascade of KL-II) | Operational | Headworks near tailrace of KL-II; Powerhouse 4.5 km north of Hetauda; Completed ~2019/20
Sunkoshi | Sindhupalchowk | Hydro | Public | NEA | 10.05 |  | Run-of-River (daily pondage) | Operational | 3 × 3.35 MW; Commissioned Jan 1972 with PRC cooperation; Cost ~NRs 109.4 M; Cumulative gen: 2,378 GWh
Puwa Khola (Ilam) | Golakharka, Ilam | Hydro | Public | NEA | 6.2 |  | Run-of-River | Operational | 2 × 3.1 MW; Commissioned 1999; Annual design: 48 GWh
Chatara | Chatara, Sunsari | Hydro | Public | NEA | 3.2 |  | Canal drop | Operational | Annual avg energy: 6 GWh; Max head: 5.38 m
Panauti | Panauti, Kavrepalanchok | Hydro | Public | NEA | 2.4 |  | Run-of-River | Operational | Annual design: 6.97 GWh
Tatopani | Tatopani | Hydro | Public | NEA | 2 |  | Run-of-River | Operational | 2,000 kW
Seti (Pokhara) | Nadipur, Pokhara | Hydro | Public | NEA | 1.5 |  | Run-of-River | Operational | 3 × 0.5 MW; Annual design: 9.8 GWh; Commissioned ~1967
Tinau | Palpa | Hydro | Public | NEA | 1.024 |  | Run-of-River | Operational | 1,024 kW; Part of Tinau-Sundarijal Rehabilitation Project
Fewa | Pokhara | Hydro | Public | NEA | 1 |  | Run-of-River | Operational | 4 × 0.25 MW; Annual design: 6.5 GWh
Sundarijal | Sindhupalchowk (~15 km NE of Kathmandu) | Hydro | Public | NEA | 0.97 | 0.64 | Run-of-River | Operational | Originally 640 kW, upgraded to 970 kW; Annual design: 4.77 GWh; Rehabilitation under ADB financing
Pharping | Kathmandu | Hydro | Public | NEA | 0.5 |  | Run-of-River | Operational | Commissioned 1911 (oldest HPS in Nepal); Rated capacity 500 kW (2 × 250 kW)
Gamgad | Gamgad | Hydro | Public | NEA | 0.4 |  | Run-of-River | Operational | 400 kW
Khandbari | Khandbari | Hydro | Public | NEA | 0.25 |  | Run-of-River | Operational | 250 kW; Isolated grid
Jomsom | Mustang | Hydro | Public | NEA | 0.24 |  | Run-of-River | Operational | 240 kW; Isolated
Phidim | Panchthar | Hydro | Public | NEA | 0.24 |  | Run-of-River | Operational | 240 kW; Isolated
Baglung | Baglung | Hydro | Public | NEA | 0.2 |  | Run-of-River | Operational | 200 kW
Surnaiyagad | Surnaiyagad | Hydro | Public | NEA | 0.2 |  | Run-of-River | Operational | 200 kW
Doti | Doti | Hydro | Public | NEA | 0.2 |  | Run-of-River | Operational | 200 kW
Ramechhap | Ramechhap | Hydro | Public | NEA | 0.15 |  | Run-of-River | Operational | 150 kW
Terhathum | Terhathum | Hydro | Public | NEA | 0.1 |  | Run-of-River | Operational | 100 kW; Isolated
Multifuel Power Plant (Duhabi) | Bansbari, Morang | Thermal (Multi-fuel) | Public | NEA | 39 |  | Diesel/Gas (Wartsila DG sets) | Operational | 6 × 6.5 MW Wartsila DG sets; Commissioned 1990/91; Major overhauling completed; Run mainly for testing in recent years
Hetauda Diesel Power Plant | Hetauda W.N.-1, Makwanpur | Thermal (Diesel) | Public | NEA | 14.41 |  | Diesel (HSD) | Operational | 4 × 2.5 MW + 3 × 1.47 MW; Commissioned 1963 & 1980 (British/Nepal support); Run mainly for testing; Cumulative gen: 155.53 GWh
Chilime HEP | Rasuwa | Hydro | Public (Subsidiary) | Chilime Hydro Power Company Ltd. (NEA sub.) | 22.1 |  | Run-of-River | Operational | PPA: 2054.03.11; COD: 2060.05.08 (2003 AD)
Upper Tamakoshi HEP | Dolkha | Hydro | Public (Subsidiary) | Upper Tamakoshi Hydropower Ltd. (NEA sub.) | 456 |  | Run-of-River | Operational | PPA: 2067.09.14; COD: 2078.05.04 (2021 AD); Largest HPS in Nepal
Upper Sanjen HEP | Rasuwa | Hydro | Public (Subsidiary) | Sanjen Hydropower Co. Ltd. (NEA sub.) | 14.8 |  | Run-of-River | Operational | PPA: 2068.06.23; COD: 2080.06.21 (2023 AD); Part of Sanjen complex
Sanjen HEP | Rasuwa | Hydro | Public (Subsidiary) | Sanjen Hydropower Company Ltd. (NEA sub.) | 42.5 |  | Run-of-River | Operational | PPA: 2068.08.19; COD: 2081.09.01 (2024 AD)
Rasuwagadhi HEP | Rasuwa | Hydro | Public (Subsidiary) | Rasuwagadhi Hydropower Company Ltd. (NEA sub.) | 111 |  | Run-of-River | Operational | PPA: 2068.07.28; COD: 2081.09.16 (2024 AD)
Khimti Khola HEP | Dolakha | Hydro | Private | Himal Power Ltd. | 60 |  | Run-of-River | Operational | PPA: 2052.10.01; COD: 2057.03.27 (2000 AD)
Upper Bhotekoshi HEP | Sindhupalchowk | Hydro | Private | Bhotekoshi Power Company Ltd. | 45 |  | Run-of-River | Operational | PPA: 2053.04.06; COD: 2057.10.11
Indrawati III HEP | Sindhupalchowk | Hydro | Private | National Hydro Power Company Ltd. | 7.5 |  | Run-of-River | Operational | PPA: 2054.09.15; COD: 2059.06.21
Jhimruk Khola HEP | Pyuthan | Hydro | Private | Butwal Power Company Ltd. | 12 |  | Run-of-River | Operational | PPA: 2058.03.29; COD: 2051.05.01
Andhi Khola HEP | Syangja | Hydro | Private | Butwal Power Company Ltd. | 9.4 |  | Run-of-River | Operational | PPA: 2058.03.29; COD: 2071.12.22
Mardi Khola HEP | Kaski | Hydro | Private | Gandaki Hydro Power Co. Pvt. Ltd. | 4.8 |  | Run-of-River | Operational | PPA: 2060.07.07; COD: 2066.10.08
Lower Modi 1 HEP | Parbat | Hydro | Private | United Modi Hydropower Pvt. Ltd. | 10 |  | Run-of-River | Operational | PPA: 2065.10.20; COD: 2069.08.10
Sipring Khola HEP | Dolakha | Hydro | Private | Synergy Power Development (P.) Ltd. | 9.658 |  | Run-of-River | Operational | PPA: 2065.10.20; COD: 2069.10.03

## Generation Summary
NEPAL — Generation Summary & Demand Statistics
Source: NEA Annual Report FY 2024/2025; NEA Generation Directorate 2076 (Aug 2019); JICA Data Collection Survey on T&D (Jul 2019)
Category | Fuel Type / Description | Count | Installed Capacity (MW) | % of Total | Notes | Fiscal Year | Source
NEA-Owned Generation | Hydro (major & small, grid-connected) | 20+ | ~627 MW | ~17% | Includes KGA, Upper Tamakoshi subsidiary, Chameliya, Kulekhani I/II/III, etc.; NEA generation total incl. subsidiaries | FY 2024/25 | NEA Annual Report 2024/25
NEA Subsidiary Companies | Hydro | 5 | 646.4 MW | ~18% | Chilime 22.1MW, Upper Tamakoshi 456MW, Upper Sanjen 14.8MW, Sanjen 42.5MW, Rasuwagadhi 111MW | FY 2024/25 | NEA Annual Report 2024/25
IPPs (Private) | Hydro, Solar | 204 projects | 2,929.7 MW | ~82% | Total operational IPP capacity as of FY 2081/82 (2024/25); 55% of total energy supply | FY 2024/25 | NEA Annual Report 2024/25
TOTAL INSTALLED CAPACITY | All sources | — | 3,591 MW | 100% | 434 MW added in FY 2024/25 alone | FY 2024/25 | NEA Annual Report 2024/25
Solar Plants (commissioned FY 2024/25) | Solar PV | 8 | 170 MW | ~5% | Part of 960 MW competitive tariff bidding program; PPAs signed for 63 projects | FY 2024/25 | NEA Annual Report 2024/25
Under-construction capacity | Hydro+Solar | 148+ IPPs | 4,303 MW after fin. closure; 4,203 MW at various stages | — | Includes Middle Bhotekoshi 102MW, Tanahun 140MW, Tamakoshi-V 94.8MW, Upper Modi 42+18.2MW, Upper Trishuli 3B 37MW | FY 2024/25 | NEA Annual Report 2024/25
System Peak Demand | — | — | 2,901 MW (system); 2,409 MW (national) | — | System peak: 2,901 MW (2901 MW includes export); National peak demand: 2,409 MW on 10 Jun 2025 | FY 2024/25 | NEA Annual Report 2024/25
Total Energy Available | — | — | 15,641 GWh | 100% | NEA 34%, IPPs 55%, Import from India 11% | FY 2024/25 | NEA Annual Report 2024/25
Domestic Consumption | — | — | 11,343 GWh | 72% |  | FY 2024/25 | NEA Annual Report 2024/25
Exports to India | — | — | 2,380 GWh | — | 22.3% increase vs. previous year; Revenue: NRs 17,471 million | FY 2024/25 | NEA Annual Report 2024/25
Imports from India | — | — | 1,681 GWh | — | Net exporter: Net export = 699 GWh | FY 2024/25 | NEA Annual Report 2024/25
System Loss | — | — | 12.26% | — | Reduced from 12.73% previous year | FY 2024/25 | NEA Annual Report 2024/25
Export capacity contracted | — | 936.72 MW | 936.72 MW | — | + additional 200 MW of new plants contracted for exports to India | FY 2024/25 | NEA Annual Report 2024/25
NEA Generation Directorate - Hydro Plants | Hydro | 18+ stations | 559.29 MW | — | As of Aug 2019 (FY 2075/76); Total generation FY 2075/76: 2,541.116 GWh | FY 2018/19 | NEA Gen Directorate 2076
NEA Generation Directorate - Thermal | Thermal | 2 plants | 53.41 MW | — | Multifuel 39 MW + Hetauda Diesel 14.41 MW; Run mainly for testing in FY 2075/76 | FY 2018/19 | NEA Gen Directorate 2076
Under construction (as of 2019) | Hydro | 2 | 74 MW | — | Upper Trishuli 3A (60 MW) - trial ops; Kulekhani III (14 MW) - near completion | FY 2018/19 | NEA Gen Directorate 2076
Total installed capacity | All | — | 1,069 MW | — | Power generation capacity as of July 2018 | FY 2017/18 | JICA DCS Jul 2019
Peak demand | — | — | ~1,509 MW | — | About 440 MW shortage made up by imports from India | FY 2017/18 | JICA DCS Jul 2019
System loss rate | — | — | 20.45% | — | Higher than neighboring countries in 2018 | FY 2017/18 | JICA DCS Jul 2019
Theoretical hydro potential | Hydro | — | 83,000 MW (theoretical); 42,000 MW (economically developable) | — | Only ~2.5% developed as of 2016 | 2016 | JICA DCS Jul 2019
Annual demand growth | — | — | 7-8% per year | — | Historical average; expected to continue | 2011-2018 | JICA DCS Jul 2019
Installed capacity growth | — | — | 3.9% per year | — | 2011 (706 MW) to 2016 (856 MW) | 2011-2016 | JICA DCS Jul 2019

## Existing Interconnections
NEPAL — Existing Cross-Border Interconnections
Source: NEA Transmission/PMD Directorate Year Book FY 2075/76 (2018/19); NEA Annual Report FY 2024/2025
Project | From Country | To Country | From Point | To Point | Capacity (MW) | Voltage Level | DC/AC | Technology | Directionality | Operational Date | Status | Notes
Dhalkebar – Muzzaffarpur 400 kV Cross-Border Line | Nepal | India | Dhalkebar (Dhanusha) | Muzzaffarpur (Bihar, India) | 1,000 | 400 kV | AC | XLPE / Overhead (Quad Moose) | Bidirectional | Aug 2018 (220 kV); Full 400 kV operational | Operational (220 kV level in 2018; 400 kV ongoing) | Part of NIETTP (World Bank funded); Nepal portion 78 km DC; Dhalkebar-Inaruwa 306 km total backbone; Started importing power from India Aug 2018
Raxaul – Parwanipur (Cross Border) | India | Nepal | Raxaul (Bihar, India) | Parwanipur (Parsa, Nepal) | ~150 | 132 kV | AC | Overhead (BEAR conductor) | Bidirectional | Pre-2018 | Operational | Nepal portion ~32 km DC; Provides import from Indian grid; Existing 132 kV cross-border
Kataiya – Kushaha (Cross Border) | India | Nepal | Kataiya (Bihar, India) | Kushaha (Sunsari, Nepal) | ~150 | 132 kV | AC | Overhead (BEAR conductor) | Bidirectional | Pre-2018 | Operational | Nepal portion ~26 km DC; Provides import from Indian grid; Existing 132 kV cross-border
Mainohiya – Sampatiya (Cross Border) | India | Nepal | Gorakhpur area (India) | Sampatiya (Rupandehi, Nepal) | ~150 | 132 kV | AC | Overhead (BEAR conductor) | Bidirectional | Post-2019 | Operational | Nepal portion ~56 km DC; Cross-border link

## Planned Interconnections
NEPAL — Planned Cross-Border Interconnections
Source: NEA Transmission/PMD Directorate Year Book FY 2075/76 (2018/19); NEA Annual Report FY 2024/2025
Project | From Country | To Country | From Point | To Point | Voltage Level | Function | Capacity (MW) | DC/AC | Background/Rationale | Expected COD | Status | Source
Butwal – Gorakhpur 400 kV Cross-Border Line | Nepal | India | New Butwal (Rupandehi) | Gorakhpur (UP, India) | 400 kV | Export / Import | ~1,000 | AC | Financial modalities in final stage as of 2019; Enables large-scale electricity trade; Part of GoN 15,000 MW export target | ~2026/27 | In progress / under development | NEA Grid 2076; NEA Annual 2024/25
Inaruwa – Purniya 400 kV Cross-Border Line | Nepal | India | Inaruwa (Sunsari) | Purniya (Bihar, India) | 400 kV | Export / Import | ~1,000 | AC | Detail design in preparation as of 2019; Part of eastern grid integration | TBD | Planning | NEA Grid 2076
New Lumki (Dododhara) – Bareli 400 kV Cross-Border Line | Nepal | India | New Lumki / Dododhara (Kanchanpur) | Bareli (India) | 400 kV | Export / Import | ~1,000 | AC | Detail design in preparation as of 2019; Western cross-border link | TBD | Planning | NEA Grid 2076
Nepalgunj – Nanpara 132 kV Cross-Border Line | Nepal | India | Nepalgunj (Banke) | Nanpara (UP, India) | 132 kV | Import / Export | ~150 | AC | Under construction as of FY 2024/25; Expected completion 2025/26 | 2025/26 | Under Construction | NEA Annual 2024/25
Dhalkebar – Loharpatti (Expansion) | Nepal | India | Dhalkebar (Dhanusha) | Loharpatti (Bihar) | 132 kV | Export | — | AC | Existing cross-border corridor expansion; 38 km Cardinal conductor line | 2025 | Operational/Expansion | NEA Annual 2024/25

## Existing Transmission
NEPAL — Existing High-Voltage Transmission Lines & Substations
Source: NEA Annual Report FY 2024/2025; NEA Transmission/PMD Directorate Year Book FY 2075/76 (2018/19)
# | Line Description | Circuit Type | Length (Circuit km) | Conductor Type | Nominal Al. Cross-Section (sq.mm) | Voltage Level | Notes
1 | Anarmani-Duhabi | Single | 75.76 | BEAR | 250 | 132 kV
2 | Kushaha (Nepal)-Kataiya (India) | Single | 15.00 | BEAR | 250 | 132 kV | Cross-border
3 | Duhabi-Inaruwa-Kushaha | Double | 56.00 | ACCC Cordoba | 250 | 132 kV
4 | Kushaha-Rupani-Lahan-Mirchaiya-Dhalkebar | Double | 276.00 | BEAR | 250 | 132 kV
5 | Parwanipur-Pathalaiya-Chapur-Nawalpur-Dhalkebar | Double | 200.00 | BEAR | 250 | 132 kV
6 | Pathalaiya-Kamane-Hetauda | Double | 76.00 | ACCC Cordoba | 250 | 132 kV
7 | Bharatpur-Marsyangdi P/S | Single | 25.00 | DUCK | 300 | 132 kV
8 | Hetauda-Bharatpur | Single | 70.00 | PANTHER | 200 | 132 kV
9 | Marsyangdi P/S-Suichatar | Single | 84.00 | DUCK | 300 | 132 kV
10 | Matatirtha-KL2 P/S-Hetauda | Double | 80.00 | BEAR | 250 | 132 kV
11 | Suichatar-Matatirtha | Double | 8.00 | ACCC Cordoba | 250 | 132 kV
12 | Suichatar-Balaju | Single | 5.00 | ACCC Amsterdam | 250 | 132 kV
13 | Balaju-Chapali-New Bhaktapur | Double | 36.00 | BEAR | 250 | 132 kV
14 | New Bhaktapur-Lamosangu | Double | 96.00 | BEAR | 250 | 132 kV
15 | Lamosangu-New Khimti | Single | 46.00 | ACCC Cordoba | 250 | 132 kV
16 | Lamosangu-Bhotekoshi P/S | Single | 31.00 | BEAR | 250 | 132 kV
17 | Bharatpur-Damauli | Single | 39.00 | ACCC Copenhagen | 150 | 132 kV
18 | Bharatpur-Kawasoti-Bardghat | Single | 70.00 | PANTHER | 200 | 132 kV
19 | Bardghat-Gandak P/S | Double | 28.00 | PANTHER | 200 | 132 kV
20 | Bardghat-Butwal | Double | 32.00 | BEAR | 250 | 132 kV
21 | New Butwal-Sunwal-Butwal | Double | 54.00 | ACCC Cordoba | — | 132 kV
22 | Butwal-KGA P/S | Double | 116.00 | DUCK | 300 | 132 kV
23 | KGA P/S-Lekhnath | Double | 96.00 | DUCK | 300 | 132 kV
24 | Lekhnath-Damauli | Single | 45.00 | WOLF | 150 | 132 kV
25 | Lekhnath-Pokhara | Single | 7.00 | ACCC Copenhagen | 150 | 132 kV
26 | Pokhara-Modikhola P/S | Single | 37.00 | BEAR | 250 | 132 kV
27 | Butwal-Shivapur-Lamahi-Kohalpur | Double | 430.00 | BEAR | 250 | 132 kV
28 | Lamahi-Jhimruk P/S | Single | 50.00 | DOG | 100 | 132 kV
29 | Kohalpur-Bhurigaun-Lumki | Double | 176.66 | BEAR | 250 | 132 kV
30 | Lamki-Pahalwanpur-Attariya-Mahendranagar (Lalpur) | Double | 203.12 | BEAR | 250 | 132 kV
31 | Mahendranagar-Gaddachauki | Single | 12.00 | BEAR | 250 | 132 kV
32 | Marsyangdi-M. Marsyangdi | Double | 80.00 | CARDINAL | 420 | 132 kV
33 | Damak-Godak | Double | 70.00 | BEAR | 250 | 132 kV
34 | Kusum-Hapure | Single | 22.00 | BEAR | 250 | 132 kV | Completed FY 2018/19
35 | Bhulbhule-Middle Marsyangdi P/S | Single | 22.00 | BEAR | 250 | 132 kV
36 | Chameliya-Syaule-Attaria | Double | 262.00 | BEAR | 250 | 132 kV
37 | Raxual-Parwanipur (Cross Border-Nepal Portion) | Double | 32.00 | BEAR | 250 | 132 kV | Cross-border
38 | Kushaha-Kataiya (Cross Border-Nepal Portion) | Double | 26.00 | BEAR | 250 | 132 kV | Cross-border
39 | Dumre-Damauli | Double | 46.00 | BEAR | 250 | 132 kV | Completed FY 2018/19
40 | Lamahi-Ghorahi | Double | 25.00 | BEAR | 250 | 132 kV | Completed FY 2018/19
41 | Kushma-Lower Modi | Single | 6.20 | BEAR | 250 | 132 kV
42 | Godak-Phidim-Amarpur (Kabeli II & III) | Double | 113.13 | BEAR | 250 | 132 kV | Kabeli corridor
43 | Trishuli 3A-Trishuli 3B Hub | Double | 6.00 | BISON | 350 | 132 kV
44 | Samundratar-Trishuli 3B Hub | Double | 52.00 | AAAC Upas | 300 | 132 kV
45 | Singati-Lamosangu | Single | 40.00 | BEAR | 250 | 132 kV
46 | Solu Corridor (Tingla-Mirchaiya) | Double | 180.00 | CARDINAL | 420 | 132 kV
47 | New Modi-Lahachwok-Lekhnath | Double | 84.00 | BEAR | 250 | 132 kV
48 | Motipur-Sandhikharka-Tamghas | Double | 104.00 | BEAR | 250 | 132 kV
49 | Butwal-Lumbini | Double | 36.00 | BEAR / XLPE | 250/500 | 132 kV | Includes 4 km UG
50 | Dordi (Kirtipur-Udipur) | Double | 20.00 | CARDINAL | 420 | 132 kV
51 | Ramechhap-Garjyang-Khimti | Double | 62.00 | BEAR | 250 | 132 kV
52 | Mainohiya-Sampatiya (Cross Border-Nepal Portion) | Double | 56.00 | BEAR | 250 | 132 kV | Cross-border
53 | Bardaghat-Sardi | Double | 40.00 | BEAR | 250 | 132 kV
54 | New Hetauda-Old Hetauda | Double | 8.00 | BEAR | 250 | 132 kV
55 | Dhalkebar-Loharpatti | Double | 38.00 | CARDINAL | 420 | 132 kV | Cross-border expansion
| TOTAL 132 kV |  | 4,005.87
1 | Khimti-Dhalkebar | Double | 150.00 | BISON | 350 | 220 kV | First 220 kV line; originally charged at 132 kV
2 | Trishuli 3B Hub-Matatirtha | Double | 98.00 | BISON | 350 | 220 kV | Upper Trishuli 3A evacuation
3 | Marsyangdi (Markichowk)-Matatirtha | Double | 164.00 | MOOSE | 500 | 220 kV
4 | Matatirtha-Matatirtha Substation (UG) | Double UG | 5.00 | XLPE Cu Cable | 1200/1600 | 220 kV | Underground segment
5 | Dana-Kushma | Double | 79.60 | MOOSE | 500 | 220 kV
6 | Koshi Corridor (Inaruwa-Basantapur-Baneshwor-Tumlingtar) | Single | 106.00 | MOOSE | 500 | 220 kV
7 | Koshi Corridor (Basantapur-Dhungesanghu) | Double | 70.00 | MOOSE | 500 | 220 kV
8 | Kushma-New Butwal | Double | 176.00 | ACCC Drake | 519.7 | 220 kV | Kaligandaki corridor
9 | Bharatpur-Bardghat | Double | 148.00 | BISON | 350 | 220 kV
10 | New Bharatpur-New Hetauda | Double | 143.40 | BISON | 350 | 220 kV
11 | Chilime-Trishuli | Double | 72.00 | BISON | 350 | 220 kV | Completed FY 2024/25; enables evacuation of Trishuli basin power
12 | New Butwal-Bardaghat | Double | 42.00 | BISON | 350 | 220 kV
| TOTAL 220 kV |  | 1,254.00
1 | Dhalkebar-Muzzaffarpur (Nepal Portion) | Double | 78.00 | MOOSE | 500 | 400 kV | Cross-border; Part of NIETTP; Charged 2018
2 | Dhalkebar-Inaruwa | Double | 306.00 | MOOSE | 500 | 400 kV | Part of NIETTP backbone
| TOTAL 400 kV |  | 384.00
1 | Chilime P/S-Trishuli P/S | Single | 39.00 | WOLF | 150 | 66 kV
2 | Trishuli P/S-Balaju | Double | 58.00 | DOG | 100 | 66 kV
3 | Trishuli P/S-Devighat P/S | Single | 4.56 | WOLF | 150 | 66 kV
4 | Devighat P/S-Okhaltar | Double | 53.00 | DOG | 100 | 66 kV
5 | Okhaltar-Chapali | Double | 5.60 | XLPE Cable | 500 | 66 kV
6 | Chapali-New Chabel | Double | 10.00 | ACCC Silvasa | 100 | 66 kV
7 | New Chabel-Lainchaur | Single | 7.00 | XLPE Cable | 500 | 66 kV
8 | Balaju-Lainchor | Single | 2.00 | PANTHER | 200 | 66 kV
9 | Balaju-Siuchatar-KL1 P/S | Double | 72.00 | WOLF | 150 | 66 kV
10 | KL1 P/S-Hetauda-Simara | Double | 104.00 | WOLF | 150 | 66 kV
11 | Simara-Parwanipur-Birgunj | Double | 40.00 | HTLS INVAR | 150 | 66 kV
12 | Suichatar-Teku | Double | 8.20 | BEAR | 250 | 66 kV
13 | Suichatar-New Patan | Double | 13.00 | ACCC Copenhagen | 150 | 66 kV
14 | Teku-K3 (underground) | Double SC | 5.60 | XLPE Cable | 400/500 | 66 kV
15 | Bhaktapur-Baneshwor-Patan | Single | 16.50 | ACCC Silvasa | 123 | 66 kV
16 | Bhaktapur-Banepa-Panchkhal-Sunkoshi P/S | Single | 48.00 | LGJ 120 | 120 | 66 kV
17 | Indrawati-Panchkhal | Single | 28.00 | PANTHER | 200 | 66 kV
| TOTAL 66 kV |  | 514.46
EXISTING GRID SUBSTATIONS (as of FY 2018/19)
# | Substation Name | Voltage Level | Location/Notes
1 | Amarpur (Kabeli) | 132/33 kV
2 | Phidim | 132/33 kV
3 | Godak | 132/33 kV
4 | Damak | 132/33 kV
5 | Anarmani | 132/33 kV
6 | Duhabi | 132/33 kV
7 | Kushaha | 132 kV Switching Station
8 | Rupani | 132/33 kV | Completed FY 2018/19; 63 MVA
9 | Lahan | 132/33 kV
10 | Mirchaiya | 132/33 kV
11 | Dhalkebar | 220/132 kV | 2×160 MVA transformers; NIETTP hub; Cross-border 400 kV pulling station; Commissioned Jul 2018
12 | Chandranigahapur | 132/33 kV
13 | Pathlaiya | 132/11 kV
14 | New Parwanipur | 132/66 kV
15 | Birgunj | 66/33 kV
16 | Simra | 66/11 kV
17 | Amlekhgunj | 66/11 kV
18 | Kamane | 132/33 kV
19 | Hetauda | 132/66 kV
20 | Bharatpur | 132/33 kV
21 | Balaju | 132/66 kV
22 | Chapali | 132/66 kV
23 | Siuchatar | 132/66 kV
24 | New Chabel | 66/11 kV
25 | Lainchour | 66/11 kV
26 | New Patan | 66/11 kV
27 | Teku | 66/11 kV
28 | K3 | 66/11 kV
29 | Baneswor | 66/11 kV
30 | Bhaktapur | 132/66 kV
31 | Banepa | 66/11 kV
32 | Panchkhal | 66/11 kV
33 | Lamosanghu | 132/33 kV
34 | Matatirtha | 132/33 kV
35 | Indrawati | 66/11 kV
36 | Damauli | 132/33 kV
37 | Pokhara | 132/11 kV
38 | Lekhnath | 132/33 kV
39 | Markichowk | 132/33 kV | Completed Apr 2019; 30 MVA
40 | Syangja | 132/33 kV
41 | Butwal | 132/33 kV
42 | Bardghat | 132/11 kV
43 | Gandak | 132 kV Switching Station
44 | Chanauta | 132/33 kV
45 | Lamahi | 132/33 kV
46 | Ghorahi | 132/33 kV | Completed FY 2018/19
47 | Kawasoti | 132/33 kV
48 | Kusum | 132/11 kV
49 | Hapure | 132/33 kV | Panchakule 30 MVA; Completed 2018/19
50 | Attaria | 132/33 kV
51 | Kohalpur | 132/33 kV
52 | Lamki | 132/33 kV
53 | Mahendranagar | 132/33 kV
54 | Bhurigaon | 132/33 kV
55 | Pahalmanpur | 132/33 kV
56 | Syaule | 132/33 kV

## Planned Transmission
NEPAL — Planned & Under-Construction Transmission Lines & Substations
Source: NEA Transmission/PMD Directorate Year Book FY 2075/76 (2018/19); NEA Annual Report FY 2024/2025
Project | From | To | Voltage Level | Function/Notes | Length (km) | Expected COD | Status | Financing | Source
Singati-Lamosangu 2nd Circuit TL | Singati | Lamosangu | 132 kV | N-1 reliability; Balefi corridor power evacuation | 40 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Burtibang-Paudi Amarai-Tamghas TL | Burtibang | Tamghas | 132 kV | Distribution network upgrade in Baglung area | 66 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Kushaha-Biratnagar TL | Kushaha | Biratnagar | 132 kV | Industrial area supply | 46 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Kohalpur-Surkhet-Dailekh TL | Kohalpur | Dailekh | 132 kV | Far-west region power supply | 168 | 2026/27 | Under Construction | — | NEA Annual 2024/25
Balefi Corridor TL | Balefi | Barhabise | 132 kV | IPP power evacuation in Balefi corridor | 40 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Dhalkebar-Balganga TL | Dhalkebar | Balganga | 132 kV | Grid reinforcement in Terai | 48 | 2025/26 | Under Construction | CARDINAL | NEA Annual 2024/25
Kaligandaki-Ridi TL | Kaligandaki area | Ridi | 132 kV | Western region power distribution | 44 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Nawalpur (Lalbandi)-Salimpur TL | Nawalpur | Salimpur | 132 kV | Distribution reinforcement | 40 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Bhumahi-Hakui TL | Bhumahi | Hakui | 132 kV | Local grid | 32 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Kabeli (Amarpur)-Dhungesangu TL | Amarpur | Dhungesangu | 132 kV | Eastern corridor extension | 40 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Godak-Soyak TL | Godak | Soyak | 132 kV | Eastern grid extension | 16 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Kushma-Lower Modi-Modi TL | Kushma | Modi | 132 kV | Modi Khola area distribution | 30 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Birgunj-Parsauni Underground TL | Birgunj | Parsauni | 132 kV | Urban underground cable | 5.6 | 2025/26 | Under Construction | XLPE Cu Cable | NEA Annual 2024/25
Barhabise-Lamosangu 2nd Circuit (Sunkoshi 132 kV SS) | Barhabise | Lamosangu | 132 kV | Second circuit for N-1 redundancy | 12 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Nepalgunj-Nanpara Cross-Border TL | Nepalgunj | Nanpara (India) | 132 kV | Cross-border import/export | 33 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Bafikot-Madichaur (Khungri) TL | Bafikot | Madichaur | 132 kV | Karnali area distribution | 150 | 2025/26 | Under Construction | — | NEA Annual 2024/25
Khimti-Dhalkebar 2nd Circuit TL | Khimti | Dhalkebar | 220 kV | Upper Tamakoshi power evacuation; N-1 reliability | 75 | ~2020 | Under Construction (2019) | World Bank, GoN, NEA | NEA Grid 2076
Tumlingtar-Sitalpati TL | Tumlingtar | Sitalpati (Sankhuwasabha) | 220 kV | IPP power evacuation in Arun/Tamor area; New 220/132/33 kV 200 MVA substation at Sitalpati | 15 | TBD | Planned | GoN; US$ 2.8M | NEA Grid 2076
Borang-Ratmate (Naubise) TL | Borang | Ratmate/Naubise | 220 kV | Aankhu Khola corridor IPP power evacuation | — | TBD | Planned | — | NEA Grid 2076
Hetauda-Dhalkebar-Inaruwa 400 kV (NIETTP backbone) | Hetauda | Inaruwa via Dhalkebar | 400 kV | National grid backbone; 1,000 MW cross-border capacity with India; 288 km DC Quad Moose | 288 | 2020-2022 | Under Construction / Partially Operational | World Bank | NEA Grid 2076
New Butwal-Lamahi 400 kV DC TL (CP-1) | New Butwal | Lamahi | 400 kV | National 400 kV backbone | 150 | TBD | Planned | NIETTP / GoN | NEA Grid 2076
Lamahi-New Kohalpur 400 kV DC TL (CP-1) | Lamahi | New Kohalpur | 400 kV | National 400 kV backbone | 90 | TBD | Planned | NIETTP / GoN | NEA Grid 2076
New Kohalpur-Dododhara 400 kV DC TL (CP-1) | New Kohalpur | Dododhara (New Lumki) | 400 kV | Western 400 kV backbone to cross-border | 95 | TBD | Planned | NIETTP / GoN | NEA Grid 2076
Dododhara-New Attariya 400 kV DC TL (CP-1) | Dododhara | New Attariya | 400 kV | Far-west 400 kV backbone | — | TBD | Planned | NIETTP / GoN | NEA Grid 2076
Tingla Hub-Likhu Hub-New Khimti 400 kV DC TL (CP-1) | Tingla Hub | New Khimti | 400 kV | Central eastern 400 kV corridor | ~55 | TBD | Planned | NIETTP / GoN | NEA Grid 2076
New Khimti-Tamakoshi 3-Sunkoshi Hub-Dhalkebar 400 kV (CP-1) | New Khimti | Dhalkebar via Sunkoshi Hub | 400 kV | Eastern 400 kV backbone | ~110 | TBD | Planned | NIETTP / GoN | NEA Grid 2076
Budhigandaki Corridor 400 kV (Philim-Gumda-Ratamate) CP-2 | Philim | Ratamate | 400 kV | Budhigandaki HEP power evacuation | ~95 | TBD | Planned | NIETTP / GoN | NEA Grid 2076
Lapsephedi & Changunarayan Substations | Lapsephedi | Changunarayan | 132/33 kV | Valley distribution reinforcement; Target Dec 2019 | — | Dec 2019 | Near completion (2019) | GoN | NEA Grid 2076
New Butwal-Bardaghat 220 kV 2nd segment | New Butwal | Bardaghat | 220 kV | Kaligandaki corridor completion; 21 km from New Butwal to Bardaghat | 21 | 2020 | Under Construction/Planning (2019) | GoN | NEA Grid 2076
Under Construction Total (FY 2024/25): 132 kV | — | — | 132 kV | Transmission Directorate + PMD | 1,154 | Various | Under Construction | Various | NEA Annual 2024/25
Under Construction Total (FY 2024/25): 220 kV | — | — | 220 kV | Transmission Directorate + PMD | 434 | Various | Under Construction | Various | NEA Annual 2024/25
Under Construction Total (FY 2024/25): 400 kV | — | — | 400 kV | Transmission Directorate + PMD | 446 | Various | Under Construction | Various | NEA Annual 2024/25
Planned & Proposed Total (FY 2024/25): 132 kV | — | — | 132 kV | Transmission Directorate + PMD | 2,034 | TBD | Planned | Various | NEA Annual 2024/25
Planned & Proposed Total (FY 2024/25): 220 kV | — | — | 220 kV | Transmission Directorate + PMD | 1,108 | TBD | Planned | Various | NEA Annual 2024/25
Planned & Proposed Total (FY 2024/25): 400 kV | — | — | 400 kV | Transmission Directorate + PMD | 1,894 | TBD | Planned | Various | NEA Annual 2024/25
Under Construction Substation Capacity (FY 2024/25) | — | — | All levels | TD + PMD total | 6,338.5 MVA | Various | Under Construction | Various | NEA Annual 2024/25
Planned Substation Capacity (FY 2024/25) | — | — | All levels | TD + PMD total | 16,177.5 MVA | TBD | Planned | Various | NEA Annual 2024/25

## Planned Generation
NEPAL — Planned & Under-Construction Generation Projects
Source: NEA Annual Report FY 2024/2025; NEA Generation Directorate 2076 (Aug 2019); JICA Data Collection Survey Jul 2019
Project/Plant | Zone/Location | Fuel Type | Capacity (MW) | Technology | Developer | Status | Expected COD | Notes/Source
Middle Bhotekoshi HEP | Sindhupalchowk | Hydro | 102 | Run-of-River | Middle Bhotekoshi Jalbidhyut Company Ltd. (NEA sub.) | Under Construction / Ready for operation | 2025 | PPA: 2068.07.28; Ready for operation as of FY 2024/25
Upper Trishuli 3B HEP | Rasuwa | Hydro | 37 | Run-of-River | Trishuli Jal Vidhyut Company Ltd. (NEA sub.) | Under Construction | 2025/26 | PPA: 2074.05.06
Tanahun HEP | Tanahun | Hydro | 140 | Run-of-River (storage) | Tanahun Hydropower Ltd. (NEA sub.) | Under Construction | 2025/26 | PPA: 2075.03.15; Has already crossed 2025; Commissioned partially
Rahughat HEP | Myagdi | Hydro | 40 | Run-of-River | Raghuganga Hydropower Ltd. (NEA sub.) | Under Construction | 2025 | PPA: 2075.12.18; Partially commissioned FY 2024/25
Tamakoshi-V HEP | Dolakha | Hydro | 94.8 | Run-of-River | Tamakoshi Jalvidyut Company Ltd. (NEA sub.) | Under Construction | 2025/26 | PPA: 2079.08.14; Annual energy: ~502.58 GWh
Upper Modi 'A' HEP | Kaski | Hydro | 42 | Run-of-River | Modi Jalvidhyut Company Ltd. (NEA sub.) | Under Construction | 2026 | PPA: 2080.03.11
Upper Modi HEP | Kaski | Hydro | 18.2 | Run-of-River | Modi Jalvidhyut Company Ltd. (NEA sub.) | Under Construction | 2026 | PPA: 2080.10.18
Kulekhani III HEP | Makwanpur (near Hetauda) | Hydro | 14 | Run-of-River (cascade) | NEA | Operational (completed ~2020) | 2020 | Cascade of KL-II; Near completion as of Gen 2076 report; Now operational
Upper Trishuli 3A HEP | Rasuwa & Nuwakot | Hydro | 60 | Run-of-River | NEA | Operational | Aug 2019 | Funded by China Exim Bank; Contractor: China Gezhouba Group
Budi Gandaki HEP | Gorkha/Dhading | Hydro | 1 | 200 | Storage (dam) | NEA / GoN | Pre-construction | 2030+ | 600 MW main powerhouse + 70 MW dam-toe; Total 670 MW dam storage; Annual energy: 3,377 GWh; Strategic national project
Chainpur HEP | Eastern Nepal | Hydro | 210 | Run-of-River | CSJVCL (Chilime subsidiary) | Under development | TBD | Annual energy: 1,206.674 GWh incl. 181.743 GWh dry season (5-hr peaking)
Rolwaling HEP | Dolakha | Hydro | 22 | Run-of-River | IPP | Under Construction | 2025/26 | Mentioned in Annual 2024/25 as in different stages
Tamakoshi V HEP (Tamkoshi Khola) | Dolakha | Hydro | 99.8 | Run-of-River | Tamakoshi Jal Vidhyut Company Ltd. (TJVCL) | Under Construction | 2025 | Annual energy: ~502.58 GWh; Dry season: focusing on peak hours
Upper Modi (UMAHEP) | Kaski | Hydro | 42 | Run-of-River | NEA subsidiary | Under Construction | 2026 | Annual energy mentioned in 2024/25 report
Upper Modi (UMHEP) | Kaski | Hydro | 18.2 | Run-of-River | NEA subsidiary | Under Construction | 2026 | Different unit from Upper Modi A
Solar Plants (63 projects via competitive bidding) | Various districts | Solar PV | 960 | Solar PV | Various IPPs | Awarded/Under development | 2025-2028 | Competitive tariff-based bidding; NEA Annual 2024/25; PPA signed for 960 MW total; 8 plants (170 MW) commissioned FY 2024/25
Rahughat HEP | Myagdi | Hydro | 40 | Run-of-River | NEA/Subsidiary | Under Construction | 2024/25 | Mentioned in JICA 2019 as planned
Upper Trishuli 3A | Rasuwa/Nuwakot | Hydro | 60 | Run-of-River | NEA | Under Construction (2019) → Operational | Aug 2019 | 60 MW; JICA 2019; Operational as of 2019
Khani Khola-1 HEP | Dolakha | Hydro | 40 | Run-of-River | Greenlife Energy Pvt. Ltd. | Under Construction | TBD | PPA: 2067.06.24
Baleph A HEP | Sindhupalchowk | Hydro | 22.14 | Run-of-River | Moonlight Hydropower Pvt. Ltd. | Under Construction | TBD | PPA: 2069.07.14
Khani Khola (Dolakha) HEP | Dolakha | Hydro | 30 | Run-of-River | Sasha Engineering Hydropower (P) Ltd. | Under Construction | TBD | PPA: 2069.03.25
Lower Irkhuwa HEP | Bhojpur | Hydro | 13.04 | Run-of-River | Lower Irkhuwa Hydropower Co. Pvt. Ltd. | Under Construction | TBD | PPA: 2075.02.16
Badi Gad HEP | Baglung | Hydro | 6.6 | Run-of-River | Water and Energy Nepal Pvt. Ltd. | Under Construction | TBD | PPA: 2068.08.13
Rawa Khola HEP | Khotang | Hydro | 6.5 | Run-of-River | Dudhkoshi Power Company Pvt. Ltd. | Under Construction | TBD | PPA: 2069.09.26
Phalankhu Khola HEP | Rasuwa | Hydro | 13.7 | Run-of-River | Betrawoti Hydropower Company (P) Ltd. | Under Construction | TBD | PPA: 2069.12.06
Upper Tadi HEP | Nuwakot | Hydro | 11 | Run-of-River | Suryakunda Hydroelectric Pvt. Ltd. | Under Construction | TBD | PPA: 2068.12.03
Upper Mailung A HEP | Rasuwa | Hydro | 6.42 | Run-of-River | Energy Engineering Pvt. Ltd. | Under Construction | TBD | PPA: 2067.03.25
Tadi Khola HEP | Nuwakot | Hydro | 5 | Run-of-River | Hira Ratna Hydropower P. Ltd. | Under Construction | TBD | PPA: 2067.01.09
Middle Midim HEP | Lamjung | Hydro | 4.8 | Run-of-River | Madhya Midim Jalbidhyut Company P. Ltd. | Under Construction | TBD | PPA: 2069.10.23
Khorounga Khola HEP | Terhathum | Hydro | 4.8 | Run-of-River | Reliable Hydropower Co. Pvt. Ltd. | Under Construction | TBD | PPA: 2069.08.26

## Additional Data
NEPAL — Additional Electricity Sector Data
Source: NEA Annual Report FY 2024/2025; NEA Generation Directorate 2076 (Aug 2019); NEA Transmission/PMD Year Book FY 2075/76; NEA DCS Directorate Year Book FY 2075/76; JICA Data Collection Survey Jul 2019
Category | Sub-category | Description / Data | Value / Details | Fiscal Year / Date | Source
Financial | Revenue | Revenue from power exports | NRs 17,471 million (NRs 17.47 billion) | FY 2024/25 | NEA Annual 2024/25
Financial | Cost | Expenditure on electricity import | Decreased in FY 2024/25 vs prior year | FY 2024/25 | NEA Annual 2024/25
Financial | Losses | Foreign exchange losses | Significant losses due to forex rate increase | FY 2024/25 | NEA Annual 2024/25
Financial | Profitability | NEA profit/loss status | Surplus since 2017; Income has increased | 2017-2018 | JICA DCS Jul 2019
Financial | Balance Sheet | Current ratio | Increased from ~30% (2016) to ~46% (2017-18) | 2018 | JICA DCS Jul 2019
Financial | Balance Sheet | Capital adequacy ratio | Increased from ~10% to 23-28% since 2017 | 2017-2018 | JICA DCS Jul 2019
Tariff | EV Charging | Charging station operator surcharge | Max 20% additional charge on base tariff for EV charging service | FY 2024/25 | NEA Annual 2024/25
Tariff | Regulation | Regulatory body | Nepal Electricity Regulatory Commission (NERC) | — | JICA DCS Jul 2019
Tariff | Community Wholesale | Community wholesale consumer category | Minimum charge specified in regulation | FY 2024/25 | NEA Annual 2024/25
Distribution | Consumer Services | Number of provinces covered | 7 Provincial Offices + 2 Division Offices under DCSD | FY 2024/25 | NEA Annual 2024/25
Distribution | Electrification | National electrification rate | ~99% urban; lower rural; GoN target: 99% by 2030 | 2018 | JICA DCS Jul 2019
Distribution | Loss Reduction | System loss rate history | 20.45% (FY 2017/18) → 12.73% (FY 2023/24) → 12.26% (FY 2024/25) | 2018-2025 | Multiple NEA reports
Distribution | Substation Capacity | New substation capacity added | 140 MVA new capacity added in FY 2024/25 | FY 2024/25 | NEA Annual 2024/25
Distribution | Network | Distribution network length | 9,336 ckt-km of 33, 11 kV lines | FY 2024/25 | NEA Annual 2024/25
Distribution | Transformer Network | 11/0.4 kV transformers | Large network with total significant capacity | FY 2024/25 | NEA Annual 2024/25
Distribution | Regional Offices | Biratnagar Regional Office | Covers eastern Nepal; details in DCS Yearbook 2075/76 | FY 2018/19 | NEA DCS Yearbook 2075/76
Distribution | Regional Offices | Janakpur Regional Office | Covers central-south Nepal | FY 2018/19 | NEA DCS Yearbook 2075/76
Distribution | Regional Offices | Hetauda Regional Office | Covers central hill/Terai | FY 2018/19 | NEA DCS Yearbook 2075/76
Distribution | Regional Offices | Pokhara Regional Office | Covers western hills | FY 2018/19 | NEA DCS Yearbook 2075/76
Distribution | Regional Offices | Kathmandu Regional Office | Covers Kathmandu Valley | FY 2018/19 | NEA DCS Yearbook 2075/76
Distribution | Regional Offices | Butwal Regional Office | Covers western Terai | FY 2018/19 | NEA DCS Yearbook 2075/76
Distribution | Regional Offices | Nepalgunj Regional Office | Covers mid-west Nepal | FY 2018/19 | NEA DCS Yearbook 2075/76
Distribution | Regional Offices | Attariya Regional Office | Covers far-west Nepal | FY 2018/19 | NEA DCS Yearbook 2075/76
Transmission | Loss | Transmission loss rate | 4.35% (all-time low) | FY 2018/19 | NEA Grid 2076
Transmission | Capacity Added | Transmission line added in FY 2018/19 | 606 circuit km | FY 2018/19 | NEA Grid 2076
Transmission | Capacity Added | Substation capacity added in FY 2018/19 | 738 MVA | FY 2018/19 | NEA Grid 2076
Transmission | Capacitor Banks | Capacitor banks installed (FY 2018/19) | 3 locations; total 42.5 MVAr; voltage profile improvement | FY 2018/19 | NEA Grid 2076
Transmission | Projects | Projects under construction (2019) | 40 projects at different stages | FY 2018/19 | NEA Grid 2076
Transmission | Projects | Projects planned (2019) | 30 projects for next FY | FY 2018/19 | NEA Grid 2076
Transmission | Emergency | ERS (Emergency Restoration Systems) | Used at 3 locations in FY 2018/19 to minimize outages | FY 2018/19 | NEA Grid 2076
Transmission | LDC | Load Dispatch Centre upgrade | LDC upgradation in progress; Regional LDCs at Butwal and Dhalkebar planned | FY 2018/19 | NEA Grid 2076
Transmission | INPS Mode | Grid operation mode | Synchronous with Indian Grid | FY 2018/19 | NEA Grid 2076
Policy | Sector Organization | Main utility | Nepal Electricity Authority (NEA); established 1985 under Electricity Authority Act 1984 | 1985 | JICA DCS Jul 2019
Policy | Sector Organization | Transmission company | Rastriya Prasaran Grid Company Ltd. (RPGCL); established 2015 | 2015 | JICA DCS Jul 2019
Policy | Sector Organization | Regulatory body | Nepal Electricity Regulatory Commission (NERC); Water and Energy Commission | 2018 | JICA DCS Jul 2019
Policy | Legislation | Primary energy law | Electricity Act 1992; allows private (IPP) participation in wholesale power | 1992 | JICA DCS Jul 2019
Policy | Planning | T&D Master Plan | Transmission System Master Plan (TSMP) 2015; sets 2035 and 2040 network targets | 2015 | JICA DCS Jul 2019
Policy | Planning | Generation target | GoN target: 15,000 MW in 10 years; 10,000 MW import capacity | 2024/25 | NEA Annual 2024/25
Policy | Planning | Load shedding | Nepal declared end of load shedding (all consumer categories) from May 2018 | May 2018 | JICA DCS Jul 2019
Policy | IPPs | Total IPP PPAs | 494 PPAs with IPPs; combined capacity 11,436 MW | FY 2024/25 | NEA Annual 2024/25
Policy | IPPs | Operational IPP projects | 204 operational projects; 2,929.7 MW | FY 2024/25 | NEA Annual 2024/25
Generation History | Annual Generation | NEA hydropower total generation FY 2075/76 | 2,541.116 GWh (vs target 2,536.840 GWh; +0.17%); FY 2074/75 was 2,296.220 GWh | FY 2018/19 | NEA Gen Directorate 2076
Generation History | Cumulative Generation | Marsyangdi HPS cumulative generation | 12,407,451.90 MWh (as of FY 2075/76) | FY 2018/19 | NEA Gen Directorate 2076
Generation History | Cumulative Generation | Kulekhani-II cumulative generation | 44,676.10 MWh in FY 2075/76 | FY 2018/19 | NEA Gen Directorate 2076
Generation History | Cumulative Generation | Sunkoshi HPS cumulative generation | 2,378.431 GWh (as of FY 2075/76) | FY 2018/19 | NEA Gen Directorate 2076
Generation History | Cumulative Generation | Trishuli HPS cumulative generation | 5,306.66 GWh (as of FY 2075/76) | FY 2018/19 | NEA Gen Directorate 2076
Generation History | Cumulative Generation | Upper Trishuli 3A (trial gen) | 16,185.60 MWh generated till Ashad 2076 (before commercial operation) | 2019 | NEA Gen Directorate 2076
Generation History | Maintenance | Multifuel Power Plant status | Run only for testing in FY 2075/76; Major overhauling of Wartsila DG sets completed | FY 2018/19 | NEA Gen Directorate 2076
Smart Metering | AMI System | AMI meters installed in HPS (FY 2075/76) | Kulekhani I: 5, Marsyangdi: counted, Devighat: 12, Gandak: 3, Seti-Fewa: 4, Chameliya: 1, others ongoing | FY 2018/19 | NEA Gen Directorate 2076
Smart Metering | AMI System | 33 CT operated energy meters | AMI system in 33 CT operated meters in different HPS | FY 2018/19 | NEA Gen Directorate 2076
JICA Study | Scope | Study purpose | Data Collection Survey on T&D Network Development in Nepal; Funded by JICA (NEWJEC Inc., Kansai Electric) | July 2019 | JICA DCS Jul 2019
JICA Study | Focus Cities | Target areas studied | Pokhara (Kaski) and Nepalgunj (Banke) | July 2019 | JICA DCS Jul 2019
JICA Study | Battery Storage | Large-scale battery storage study | Feasibility study for large-scale battery storage in Pokhara and Nepalgunj conducted | July 2019 | JICA DCS Jul 2019
JICA Study | Distribution | Pokhara distribution network | 132 kV/33 kV/11 kV distribution network; specific upgrade scenarios analyzed | July 2019 | JICA DCS Jul 2019
JICA Study | Distribution | Nepalgunj distribution network | 132 kV/33 kV/11 kV; Specific improvement packages proposed | July 2019 | JICA DCS Jul 2019
Generation Statistics | NEA Annual 2024/25 | KGA and KL3 cumulative generation | KGA + KL3 reached 279.8 GWh in FY 2024/25 | FY 2024/25 | NEA Annual 2024/25
Generation Statistics | NEA Annual 2024/25 | Upper Tamakoshi HEP generation | Average annual energy: 2,281 GWh; Commissioned 2021 | FY 2024/25 | NEA Annual 2024/25
Generation Statistics | NEA Annual 2024/25 | Hetauda Diesel generation | 6.6 GWh in FY 2024/25 (105% of target; 138% of design); Cumulative: 155.53 GWh | FY 2024/25 | NEA Annual 2024/25
Generation Statistics | NEA Annual 2024/25 | Multifuel Power Plant (Duhabi) cumulative | Commissioned 1990/91; 39 MW; Run mainly for testing | FY 2024/25 | NEA Annual 2024/25